## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-190_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-190_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-190_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-190_0_2_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1631-190_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1631-190_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1631-190_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1631-190_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1631-190_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1631-190_0_2_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_1631-190_0_2_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_1631-190_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1631-190_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1631-190_0_2_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_1631-190_0_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1631-190_0_2_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1631-190_0_2_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_1631-190_0_2_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1631-190_0_2_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_1631-190_0_2_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1631-190_0_2_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1631-190_0_2_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1631-190_0_2_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1631-190_0_2_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1631-190_0_2_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1631-190_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1631-190_0_2_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1631-190_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1631-190_0_2_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1631-190_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1631-190_0_2_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1631-190_0_2_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1631-190_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_1631-190_0_2_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_1631-190_0_2_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1631-190_0_2_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1631-190_0_2_node_23 | 0.4 | n |  | TRUE
37 | bus_MV_145_0_node_151 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-190_0_2_load_0 | 0 | 0.0052701 | 0.0013208 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-190_0_2_load_2 | 2 | 0.0066522 | 0.0016672 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-190_0_2_load_7 | 3 | 0.0056881 | 0.0014256 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-190_0_2_load_3 | 5 | 0.0064178 | 0.0016084 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-190_0_2_load_4 | 6 | 0.0049773 | 0.0012474 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-190_0_2_load_8 | 8 | 0.0075598 | 0.0018947 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-190_0_2_load_39 | 9 | 0.0046532 | 0.0011662 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-190_0_2_load_28 | 10 | 0.0044704 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-190_0_2_load_36 | 13 | 0.0048727 | 0.0012212 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-190_0_2_load_33 | 15 | 0.0073013 | 0.0018299 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-190_0_2_load_38 | 16 | 0.0062198 | 0.0015588 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-190_0_2_load_29 | 17 | 0.0070645 | 0.0017705 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-190_0_2_load_35 | 18 | 0.0049287 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-190_0_2_load_11 | 19 | 0.048238 | 0.01209 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-190_0_2_load_34 | 20 | 0.0099583 | 0.0024958 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-190_0_2_load_14 | 21 | 0.0069081 | 0.0017313 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-190_0_2_load_15 | 22 | 0.0024344 | 0.00061011 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-190_0_2_load_16 | 23 | 0.0037154 | 0.00093116 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-190_0_2_load_17 | 25 | 0.01079 | 0.0027043 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-190_0_2_load_21 | 27 | 0.0021839 | 0.00054734 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-190_0_2_load_31 | 28 | 0.0045217 | 0.0011332 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-190_0_2_load_30 | 31 | 0.0077428 | 0.0019405 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-190_0_2_load_25 | 32 | 0.005236 | 0.0013123 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-190_0_2_load_40 | 33 | 0.0023004 | 0.00057654 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-190_0_2_load_24 | 34 | 0.0038822 | 0.00097298 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-190_0_2_load_22 | 35 | 0.0060771 | 0.0015231 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-190_0_2_load_23 | 36 | 0.0063499 | 0.0015914 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-190_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-190_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.011625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-190_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0088752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-190_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.007436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-190_0_2_line_4 | NAYY 4x150 SE | 4 | 8 | 0.0091449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-190_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.019297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-190_0_2_line_6 | NAYY 4x150 SE | 6 | 7 | 0.007262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-190_0_2_line_7 | NAYY 4x150 SE | 7 | 9 | 0.013411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-190_0_2_line_8 | NAYY 4x150 SE | 8 | 10 | 0.0011131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-190_0_2_line_9 | NAYY 4x150 SE | 9 | 16 | 0.0081165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-190_0_2_line_10 | NAYY 4x150 SE | 10 | 17 | 0.0095305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-190_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.044884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-190_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.037223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1631-190_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.059434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-190_0_2_line_14 | NAYY 4x150 SE | 12 | 15 | 0.029335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-190_0_2_line_15 | NAYY 4x150 SE | 13 | 18 | 0.0051881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1631-190_0_2_line_16 | NAYY 4x150 SE | 14 | 19 | 0.086398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-190_0_2_line_17 | NAYY 4x150 SE | 15 | 20 | 0.010987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-190_0_2_line_18 | NAYY 4x150 SE | 16 | 30 | 0.0078265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-190_0_2_line_19 | NAYY 4x150 SE | 17 | 31 | 0.00022197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-190_0_2_line_20 | NAYY 4x150 SE | 18 | 29 | 0.0149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1631-190_0_2_line_21 | NAYY 4x150 SE | 21 | 22 | 0.012811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1631-190_0_2_line_22 | NAYY 4x150 SE | 21 | 23 | 0.0056643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1631-190_0_2_line_23 | NAYY 4x150 SE | 23 | 24 | 0.010238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1631-190_0_2_line_24 | NAYY 4x150 SE | 24 | 27 | 0.002659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1631-190_0_2_line_25 | NAYY 4x150 SE | 25 | 26 | 0.0029977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-190_0_2_line_26 | NAYY 4x150 SE | 26 | 28 | 0.0081043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-190_0_2_line_27 | NAYY 4x150 SE | 26 | 29 | 0.029132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-190_0_2_line_28 | NAYY 4x150 SE | 27 | 30 | 0.016656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1631-190_0_2_line_29 | NAYY 4x150 SE | 29 | 31 | 0.0078907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-190_0_2_line_30 | NAYY 4x150 SE | 29 | 32 | 0.014908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1631-190_0_2_line_31 | NAYY 4x150 SE | 30 | 33 | 0.0076974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-190_0_2_line_32 | NAYY 4x150 SE | 30 | 34 | 0.010954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1631-190_0_2_line_33 | NAYY 4x150 SE | 32 | 36 | 0.005489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1631-190_0_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.0043678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1631-190_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.013351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-190_0_2_trafo_15 | 0.25 MVA 20/0.4 kV | 37 | 22 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2724150.8512 | 1206065.6091 | 2724130.3158 | 1206051.7958
1 | 2724150.8512 | 1206065.6091 | 2724157.5048 | 1206056.077
2 | 2724157.5048 | 1206056.077 | 2724162.5847 | 1206048.7994
3 | 2724166.8409 | 1206042.7019 | 2724162.5847 | 1206048.7994
4 | 2724166.8409 | 1206042.7019 | 2724171.4983 | 1206034.8318
5 | 2724146.9711 | 1206031.5449 | 2724143.746 | 1206029.7341 | 2724135.47 | 1206026.3594 | 2724129.6973 | 1206023.0369
6 | 2724123.4033 | 1206019.4144 | 2724129.6973 | 1206023.0369
7 | 2724123.4033 | 1206019.4144 | 2724130.3026 | 1206007.9141
8 | 2724172.0652 | 1206033.8739 | 2724171.4983 | 1206034.8318
9 | 2724134.4781 | 1206000.9539 | 2724130.3026 | 1206007.9141
10 | 2724176.919 | 1206025.672 | 2724172.0652 | 1206033.8739
11 | 2724230.7466 | 1206047.2347 | 2724240.7296 | 1206030.7409 | 2724253.5545 | 1206008.5798
12 | 2724230.7466 | 1206047.2347 | 2724198.4694 | 1206028.6953
13 | 2724253.5545 | 1206008.5798 | 2724266.1841 | 1205988.1271 | 2724269.6702 | 1205982.5732 | 2724284.8798 | 1205958.0711
14 | 2724253.5545 | 1206008.5798 | 2724249.3452 | 1206006.1126 | 2724228.2233 | 1205993.7846
15 | 2724198.4694 | 1206028.6953 | 2724193.9706 | 1206026.1113
16 | 2724284.8798 | 1205958.0711 | 2724218.6255 | 1205929.6264 | 2724206.039 | 1205922.8481
17 | 2724228.2233 | 1205993.7846 | 2724218.7345 | 1205988.2464
18 | 2724138.5044 | 1205994.2425 | 2724134.4781 | 1206000.9539
19 | 2724177.032 | 1206025.481 | 2724176.919 | 1206025.672
20 | 2724181.0506 | 1206018.6903 | 2724193.9706 | 1206026.1113
21 | 2724162.1137 | 1205985.8052 | 2724173.1266 | 1205992.35
22 | 2724162.1137 | 1205985.8052 | 2724157.2443 | 1205982.9115
23 | 2724148.443 | 1205977.681 | 2724157.2443 | 1205982.9115
24 | 2724148.443 | 1205977.681 | 2724147.0748 | 1205979.961
25 | 2724204.4996 | 1206010.9944 | 2724201.9226 | 1206009.463
26 | 2724204.4996 | 1206010.9944 | 2724211.4677 | 1206015.1326
27 | 2724181.0506 | 1206018.6903 | 2724183.4373 | 1206017.3389 | 2724185.0566 | 1206018.1287 | 2724196.0421 | 1206020.7259 | 2724199.8201 | 1206018.6918 | 2724204.4996 | 1206010.9944
28 | 2724138.5044 | 1205994.2425 | 2724147.0748 | 1205979.961
29 | 2724181.0506 | 1206018.6903 | 2724177.032 | 1206025.481
30 | 2724181.0506 | 1206018.6903 | 2724168.1245 | 1206011.2627
31 | 2724138.5044 | 1205994.2425 | 2724131.8299 | 1205990.4085
32 | 2724138.5044 | 1205994.2425 | 2724148.0018 | 1205999.6999
33 | 2724168.1245 | 1206011.2627 | 2724163.3653 | 1206008.528
34 | 2724148.0018 | 1205999.6999 | 2724151.7889 | 1206001.876
35 | 2724151.7889 | 1206001.876 | 2724163.3653 | 1206008.528

## bus_geodata
| x | y | coords
0 | 2724130.3158 | 1206051.7958
1 | 2724150.8512 | 1206065.6091
2 | 2724157.5048 | 1206056.077
3 | 2724162.5847 | 1206048.7994
4 | 2724166.8409 | 1206042.7019
5 | 2724146.9711 | 1206031.5449
6 | 2724129.6973 | 1206023.0369
7 | 2724123.4033 | 1206019.4144
8 | 2724171.4983 | 1206034.8318
9 | 2724130.3026 | 1206007.9141
10 | 2724172.0652 | 1206033.8739
11 | 2724230.7466 | 1206047.2347
12 | 2724253.5545 | 1206008.5798
13 | 2724198.4694 | 1206028.6953
14 | 2724284.8798 | 1205958.0711
15 | 2724228.2233 | 1205993.7846
16 | 2724134.4781 | 1206000.9539
17 | 2724176.919 | 1206025.672
18 | 2724193.9706 | 1206026.1113
19 | 2724206.039 | 1205922.8481
20 | 2724218.7345 | 1205988.2464
21 | 2724162.1137 | 1205985.8052
22 | 2724173.1266 | 1205992.35
23 | 2724157.2443 | 1205982.9115
24 | 2724148.443 | 1205977.681
25 | 2724201.9226 | 1206009.463
26 | 2724204.4996 | 1206010.9944
27 | 2724147.0748 | 1205979.961
28 | 2724211.4677 | 1206015.1326
29 | 2724181.0506 | 1206018.6903
30 | 2724138.5044 | 1205994.2425
31 | 2724177.032 | 1206025.481
32 | 2724168.1245 | 1206011.2627
33 | 2724131.8299 | 1205990.4085
34 | 2724148.0018 | 1205999.6999
35 | 2724151.7889 | 1206001.876
36 | 2724163.3653 | 1206008.528
37 | 2724148.443 | 1205977.681

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98654 | -0.093956 | 0.0052701 | 0.0013208
1 | 0.98673 | -0.092618 | 0 | 0
2 | 0.98682 | -0.09199 | 0.0066522 | 0.0016672
3 | 0.98697 | -0.090905 | 0.0056881 | 0.0014256
4 | 0.98716 | -0.089564 | 0 | 0
5 | 0.99258 | -0.051574 | 0.0064178 | 0.0016084
6 | 0.99276 | -0.050319 | 0.0049773 | 0.0012474
7 | 0.99288 | -0.049481 | 0 | 0
8 | 0.98739 | -0.087914 | 0.0075598 | 0.0018947
9 | 0.99309 | -0.047934 | 0.0046532 | 0.0011662
10 | 0.98743 | -0.087627 | 0.0044704 | 0.0011204
11 | 0.98548 | -0.10118 | 0 | 0
12 | 0.98118 | -0.13154 | 0 | 0
13 | 0.98727 | -0.088675 | 0.0048727 | 0.0012212
14 | 0.97697 | -0.16139 | 0 | 0
15 | 0.98044 | -0.13679 | 0.0073013 | 0.0018299
16 | 0.99328 | -0.046616 | 0.0062198 | 0.0015588
17 | 0.98784 | -0.084736 | 0.0070645 | 0.0017705
18 | 0.98754 | -0.086806 | 0.0049287 | 0.0012352
19 | 0.97085 | -0.20525 | 0.048238 | 0.01209
20 | 0.98028 | -0.13793 | 0.0099583 | 0.0024958
21 | 0.9982 | -0.012427 | 0.0069081 | 0.0017313
22 | 1 | 0 | -0.19777 | -0.049756
23 | 0.99743 | -0.01774 | 0.0037154 | 0.00093116
24 | 0.99607 | -0.027172 | 0 | 0
25 | 0.98767 | -0.085959 | 0.01079 | 0.0027043
26 | 0.98771 | -0.085628 | 0 | 0
27 | 0.99572 | -0.029626 | 0.0021839 | 0.00054734
28 | 0.98766 | -0.086003 | 0.0045217 | 0.0011332
29 | 0.98836 | -0.081067 | 0 | 0
30 | 0.99353 | -0.044853 | 0 | 0
31 | 0.98785 | -0.084653 | 0.0077428 | 0.0019405
32 | 0.98982 | -0.070793 | 0.005236 | 0.0013123
33 | 0.99351 | -0.045032 | 0.0023004 | 0.00057654
34 | 0.99229 | -0.053538 | 0.0038822 | 0.00097298
35 | 0.9918 | -0.056922 | 0.0060771 | 0.0015231
36 | 0.99038 | -0.066872 | 0.0063499 | 0.0015914
37 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0052701 | -0.0013208 | 0.0052711 | 0.0013209 | 9.7579e-07 | 5.9237e-08 | 0.007949 | 0.0079489 | 0.007949 | 0.98654 | -0.093956 | 0.98673 | -0.092618 | 2.9441
1 | -0.0052711 | -0.0013209 | 0.0052715 | 0.0013209 | 4.5832e-07 | 2.7779e-08 | 0.0079489 | 0.0079488 | 0.0079489 | 0.98673 | -0.092618 | 0.98682 | -0.09199 | 2.944
2 | -0.011924 | -0.0029881 | 0.011926 | 0.0029887 | 1.7903e-06 | 5.7517e-07 | 0.01798 | 0.01798 | 0.01798 | 0.98682 | -0.09199 | 0.98697 | -0.090905 | 6.6591
3 | -0.017614 | -0.0044142 | 0.017617 | 0.0044154 | 3.2721e-06 | 1.1635e-06 | 0.026555 | 0.026555 | 0.026555 | 0.98697 | -0.090905 | 0.98716 | -0.089564 | 9.8353
4 | -0.017617 | -0.0044154 | 0.017621 | 0.0044168 | 4.0241e-06 | 1.4308e-06 | 0.026555 | 0.026555 | 0.026555 | 0.98716 | -0.089564 | 0.98739 | -0.087914 | 9.8353
5 | -0.0064178 | -0.0016084 | 0.0064189 | 0.0016086 | 1.1146e-06 | 1.7923e-07 | 0.0096212 | 0.0096211 | 0.0096212 | 0.99258 | -0.051574 | 0.99276 | -0.050319 | 3.5634
6 | -0.011396 | -0.0028561 | 0.011398 | 0.0028565 | 1.3222e-06 | 4.1462e-07 | 0.017081 | 0.017081 | 0.017081 | 0.99276 | -0.050319 | 0.99288 | -0.049481 | 6.3265
7 | -0.011398 | -0.0028565 | 0.0114 | 0.0028572 | 2.4417e-06 | 7.6564e-07 | 0.017081 | 0.017081 | 0.017081 | 0.99288 | -0.049481 | 0.99309 | -0.047934 | 6.3264
8 | -0.025181 | -0.0063115 | 0.025182 | 0.0063119 | 1.0002e-06 | 3.7045e-07 | 0.037948 | 0.037948 | 0.037948 | 0.98739 | -0.087914 | 0.98743 | -0.087627 | 14.0548
9 | -0.016053 | -0.0040234 | 0.016056 | 0.0040245 | 2.9303e-06 | 1.022e-06 | 0.024054 | 0.024053 | 0.024054 | 0.99309 | -0.047934 | 0.99328 | -0.046616 | 8.9087
10 | -0.029652 | -0.0074323 | 0.029664 | 0.0074367 | 1.1875e-05 | 4.4452e-06 | 0.044685 | 0.044685 | 0.044685 | 0.98743 | -0.087627 | 0.98784 | -0.084736 | 16.5499
11 | 0.06629 | 0.016717 | -0.066009 | -0.01661 | 0.00028081 | 0.00010743 | 0.10013 | 0.10013 | 0.10013 | 0.98548 | -0.10118 | 0.98118 | -0.13154 | 37.0854
12 | -0.06629 | -0.016717 | 0.066406 | 0.016761 | 0.00011644 | 4.3833e-05 | 0.10013 | 0.10013 | 0.10013 | 0.98548 | -0.10118 | 0.98727 | -0.088675 | 18.5427
13 | 0.048735 | 0.012279 | -0.048533 | -0.012202 | 0.00020272 | 7.7223e-05 | 0.073933 | 0.073934 | 0.073934 | 0.98118 | -0.13154 | 0.97697 | -0.16139 | 27.3828
14 | 0.017274 | 0.0043306 | -0.017261 | -0.0043261 | 1.2563e-05 | 4.4616e-06 | 0.026197 | 0.026197 | 0.026197 | 0.98118 | -0.13154 | 0.98044 | -0.13679 | 9.7027
15 | -0.071279 | -0.017982 | 0.071298 | 0.017989 | 1.8697e-05 | 7.0584e-06 | 0.10747 | 0.10747 | 0.10747 | 0.98727 | -0.088675 | 0.98754 | -0.086806 | 19.9026
16 | 0.048533 | 0.012202 | -0.048238 | -0.01209 | 0.0002947 | 0.00011227 | 0.073934 | 0.073934 | 0.073934 | 0.97697 | -0.16139 | 0.97085 | -0.20525 | 27.383
17 | 0.0099599 | 0.0024963 | -0.0099583 | -0.0024958 | 1.5665e-06 | 4.6397e-07 | 0.015116 | 0.015116 | 0.015116 | 0.98044 | -0.13679 | 0.98028 | -0.13793 | 5.5986
18 | -0.022276 | -0.0055833 | 0.022281 | 0.0055853 | 5.4387e-06 | 1.9905e-06 | 0.033371 | 0.033371 | 0.033371 | 0.99328 | -0.046616 | 0.99353 | -0.044853 | 12.3597
19 | -0.036728 | -0.0092072 | 0.036729 | 0.0092074 | 4.2398e-07 | 1.6023e-07 | 0.055326 | 0.055326 | 0.055326 | 0.98784 | -0.084736 | 0.98785 | -0.084653 | 20.4911
20 | -0.076227 | -0.019224 | 0.076288 | 0.019248 | 6.1372e-05 | 2.3223e-05 | 0.1149 | 0.1149 | 0.1149 | 0.98754 | -0.086806 | 0.98836 | -0.081067 | 21.2779
21 | -0.19662 | -0.049624 | 0.19697 | 0.049756 | 0.00034367 | 0.00013185 | 0.29323 | 0.29323 | 0.29323 | 0.9982 | -0.012427 | 1 | 0 | 54.3018
22 | 0.18972 | 0.047893 | -0.18957 | -0.047839 | 0.00014147 | 5.4263e-05 | 0.28293 | 0.28293 | 0.28293 | 0.9982 | -0.012427 | 0.99743 | -0.01774 | 52.3948
23 | 0.18586 | 0.046907 | -0.18561 | -0.046813 | 0.00024579 | 9.4266e-05 | 0.27739 | 0.27739 | 0.27739 | 0.99743 | -0.01774 | 0.99607 | -0.027172 | 51.3684
24 | 0.18561 | 0.046813 | -0.18555 | -0.046789 | 6.3834e-05 | 2.4482e-05 | 0.27739 | 0.27739 | 0.27739 | 0.99607 | -0.027172 | 0.99572 | -0.029626 | 51.3684
25 | -0.01079 | -0.0027043 | 0.010791 | 0.0027045 | 4.9434e-07 | 1.5177e-07 | 0.016257 | 0.016257 | 0.016257 | 0.98767 | -0.085959 | 0.98771 | -0.085628 | 6.021
26 | 0.0045219 | 0.0011332 | -0.0045217 | -0.0011332 | 2.3469e-07 | -1.3455e-08 | 0.0068123 | 0.0068124 | 0.0068124 | 0.98771 | -0.085628 | 0.98766 | -0.086003 | 2.5231
27 | -0.015313 | -0.0038377 | 0.015322 | 0.003841 | 9.6739e-06 | 3.3476e-06 | 0.023069 | 0.023069 | 0.023069 | 0.98771 | -0.085628 | 0.98836 | -0.081067 | 8.5441
28 | 0.18337 | 0.046241 | -0.18298 | -0.046092 | 0.0003905 | 0.00014976 | 0.27413 | 0.27413 | 0.27413 | 0.99572 | -0.029626 | 0.99353 | -0.044853 | 50.764
29 | 0.044494 | 0.011156 | -0.044472 | -0.011148 | 2.2096e-05 | 8.3973e-06 | 0.066989 | 0.066989 | 0.066989 | 0.98836 | -0.081067 | 0.98785 | -0.084653 | 24.8108
30 | -0.1361 | -0.034245 | 0.1363 | 0.03432 | 0.00019539 | 7.4768e-05 | 0.20496 | 0.20496 | 0.20496 | 0.98836 | -0.081067 | 0.98982 | -0.070793 | 37.9553
31 | 0.0023005 | 0.00057646 | -0.0023004 | -0.00057654 | 5.7018e-08 | -7.7749e-08 | 0.0034454 | 0.0034454 | 0.0034454 | 0.99353 | -0.044853 | 0.99351 | -0.045032 | 1.2761
32 | 0.15839 | 0.03993 | -0.1582 | -0.039856 | 0.00019246 | 7.374e-05 | 0.23731 | 0.23731 | 0.23731 | 0.99353 | -0.044853 | 0.99229 | -0.053538 | 43.9461
33 | -0.14154 | -0.035632 | 0.14161 | 0.035662 | 7.7573e-05 | 2.9695e-05 | 0.21283 | 0.21283 | 0.21283 | 0.98982 | -0.070793 | 0.99038 | -0.066872 | 39.4129
34 | 0.15432 | 0.038883 | -0.15425 | -0.038855 | 7.3026e-05 | 2.7974e-05 | 0.23149 | 0.23149 | 0.23149 | 0.99229 | -0.053538 | 0.9918 | -0.056922 | 42.8681
35 | 0.14817 | 0.037332 | -0.14796 | -0.037253 | 0.00020598 | 7.8881e-05 | 0.22237 | 0.22237 | 0.22237 | 0.9918 | -0.056922 | 0.99038 | -0.066872 | 41.1796

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2002 | 0.050366

## res_load
| p_mw | q_mvar
0 | 0.0052701 | 0.0013208
1 | 0.0066522 | 0.0016672
2 | 0.0056881 | 0.0014256
3 | 0.0064178 | 0.0016084
4 | 0.0049773 | 0.0012474
5 | 0.0075598 | 0.0018947
6 | 0.0046532 | 0.0011662
7 | 0.0044704 | 0.0011204
8 | 0.0048727 | 0.0012212
9 | 0.0073013 | 0.0018299
10 | 0.0062198 | 0.0015588
11 | 0.0070645 | 0.0017705
12 | 0.0049287 | 0.0012352
13 | 0.048238 | 0.01209
14 | 0.0099583 | 0.0024958
15 | 0.0069081 | 0.0017313
16 | 0.0024344 | 0.00061011
17 | 0.0037154 | 0.00093116
18 | 0.01079 | 0.0027043
19 | 0.0021839 | 0.00054734
20 | 0.0045217 | 0.0011332
21 | 0.0077428 | 0.0019405
22 | 0.005236 | 0.0013123
23 | 0.0023004 | 0.00057654
24 | 0.0038822 | 0.00097298
25 | 0.0060771 | 0.0015231
26 | 0.0063499 | 0.0015914

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1