## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-195_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-195_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-195_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1631-195_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1631-195_0_3_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_1631-195_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-195_0_3_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1631-195_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1631-195_0_3_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_1631-195_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1631-195_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1631-195_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1631-195_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1631-195_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-195_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1631-195_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1631-195_0_3_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1631-195_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1631-195_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1631-195_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1631-195_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1631-195_0_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1631-195_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1631-195_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1631-195_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1631-195_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1631-195_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1631-195_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1631-195_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1631-195_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1631-195_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_MV_145_0_node_159 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-195_0_3_load_0 | 0 | 0.011897 | 0.0029816 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-195_0_3_load_1 | 1 | 0.0063759 | 0.001598 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-195_0_3_load_20 | 4 | 0.0093604 | 0.0023459 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-195_0_3_load_17 | 7 | 0.0076612 | 0.0019201 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-195_0_3_load_32 | 8 | 0.0084462 | 0.0021168 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-195_0_3_load_18 | 9 | 0.005323 | 0.0013341 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-195_0_3_load_6 | 10 | 0.039297 | 0.0098488 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-195_0_3_load_9 | 13 | 0.011204 | 0.0028079 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-195_0_3_load_10 | 14 | 0.0060809 | 0.001524 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-195_0_3_load_11 | 15 | 0.0052361 | 0.0013123 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-195_0_3_load_33 | 16 | 0.0058801 | 0.0014737 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-195_0_3_load_13 | 18 | 0.006198 | 0.0015534 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-195_0_3_load_15 | 20 | 0.0055631 | 0.0013943 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-195_0_3_load_30 | 21 | 0.0044528 | 0.001116 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-195_0_3_load_21 | 22 | 0.0049544 | 0.0012417 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-195_0_3_load_22 | 23 | 0.0061198 | 0.0015338 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-195_0_3_load_23 | 24 | 0.012375 | 0.0031014 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-195_0_3_load_24 | 25 | 0.0057818 | 0.0014491 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-195_0_3_load_26 | 26 | 0.0080109 | 0.0020077 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-195_0_3_load_27 | 27 | 0.0044179 | 0.0011072 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-195_0_3_load_28 | 28 | 0.0047147 | 0.0011816 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-195_0_3_load_29 | 29 | 0.0084317 | 0.0021132 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-195_0_3_load_31 | 30 | 0.0081106 | 0.0020327 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-195_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0076518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-195_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0017794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-195_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.082285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-195_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.011202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-195_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0062846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-195_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.04905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-195_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0085032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-195_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.01641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-195_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0068009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1631-195_0_3_line_9 | NAYY 4x150 SE | 8 | 21 | 0.012226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-195_0_3_line_10 | NAYY 4x150 SE | 9 | 20 | 0.00099037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1631-195_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.022275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-195_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.003344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-195_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.018838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-195_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0093221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1631-195_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.001342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1631-195_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.005385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1631-195_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0087814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1631-195_0_3_line_18 | NAYY 4x150 SE | 17 | 19 | 0.003011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1631-195_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.0055002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-195_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0072347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1631-195_0_3_line_21 | NAYY 4x150 SE | 21 | 30 | 0.0018065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-195_0_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.011217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-195_0_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.0084658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-195_0_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.006536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-195_0_3_line_25 | NAYY 4x150 SE | 25 | 26 | 0.0082279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-195_0_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.0044182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-195_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.0073758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-195_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.0012034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-195_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0056668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-195_0_3_trafo_9 | 0.25 MVA 20/0.4 kV | 31 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2724418.6817 | 1206070.213 | 2724423.2544 | 1206072.8738 | 2724425.232 | 1206074.1642
1 | 2724426.7222 | 1206075.1366 | 2724425.232 | 1206074.1642
2 | 2724426.7222 | 1206075.1366 | 2724434.0913 | 1206080.7612 | 2724442.281 | 1206088.6267 | 2724451.7112 | 1206099.754 | 2724460.4046 | 1206093.3192 | 2724464.6082 | 1206089.8486 | 2724472.7687 | 1206078.688 | 2724475.1573 | 1206075.4242 | 2724478.2208 | 1206074.454 | 2724477.749 | 1206070.0852 | 2724479.5955 | 1206065.0866
3 | 2724479.5955 | 1206065.0866 | 2724483.8908 | 1206054.7406
4 | 2724486.3006 | 1206048.9363 | 2724483.8908 | 1206054.7406
5 | 2724486.3006 | 1206048.9363 | 2724489.358 | 1206036.2237 | 2724492.0262 | 1206014.8186 | 2724494.1948 | 1206000.5863
6 | 2724486.3006 | 1206048.9363 | 2724479.3023 | 1206046.3218 | 2724478.3054 | 1206046.053
7 | 2724494.1948 | 1206000.5863 | 2724486.2382 | 1205997.229 | 2724478.6173 | 1205995.6923
8 | 2724471.6366 | 1206044.8052 | 2724475.4136 | 1206045.2732 | 2724478.3054 | 1206046.053
9 | 2724466.6666 | 1205993.1232 | 2724470.1838 | 1205993.9918 | 2724478.6173 | 1205995.6923
10 | 2724470.6538 | 1206044.6834 | 2724471.6366 | 1206044.8052
11 | 2724423.9724 | 1206042.8214 | 2724418.1162 | 1206040.5309 | 2724403.0554 | 1206035.17
12 | 2724427.0488 | 1206044.1532 | 2724423.9724 | 1206042.8214
13 | 2724427.0488 | 1206044.1532 | 2724431.5157 | 1206032.8043 | 2724437.8202 | 1206034.8942
14 | 2724446.3538 | 1206038.5664 | 2724443.8157 | 1206037.6643 | 2724440.1068 | 1206035.6522 | 2724437.8202 | 1206034.8942
15 | 2724447.6183 | 1206039.0158 | 2724446.3538 | 1206038.5664
16 | 2724447.6183 | 1206039.0158 | 2724452.6924 | 1206040.8191
17 | 2724460.9667 | 1206043.7598 | 2724452.6924 | 1206040.8191
18 | 2724460.9667 | 1206043.7598 | 2724463.8141 | 1206044.7644
19 | 2724463.8141 | 1206044.7644 | 2724462.3147 | 1206050.0562
20 | 2724463.8141 | 1206044.7644 | 2724464.6226 | 1206043.9361 | 2724470.6538 | 1206044.6834
21 | 2724466.6666 | 1205993.1232 | 2724464.9128 | 1205992.6901
22 | 2724432.4598 | 1205984.6754 | 2724421.5696 | 1205981.9859
23 | 2724413.3508 | 1205979.9562 | 2724421.5696 | 1205981.9859
24 | 2724432.4598 | 1205984.6754 | 2724438.8052 | 1205986.2424
25 | 2724446.7931 | 1205988.2152 | 2724438.8052 | 1205986.2424
26 | 2724451.0824 | 1205989.2745 | 2724446.7931 | 1205988.2152
27 | 2724451.0824 | 1205989.2745 | 2724458.243 | 1205991.0429
28 | 2724459.4113 | 1205991.3314 | 2724458.243 | 1205991.0429
29 | 2724464.9128 | 1205992.6901 | 2724459.4113 | 1205991.3314

## bus_geodata
| x | y | coords
0 | 2724418.6817 | 1206070.213
1 | 2724425.232 | 1206074.1642
2 | 2724426.7222 | 1206075.1366
3 | 2724479.5955 | 1206065.0866
4 | 2724483.8908 | 1206054.7406
5 | 2724486.3006 | 1206048.9363
6 | 2724494.1948 | 1206000.5863
7 | 2724478.3054 | 1206046.053
8 | 2724478.6173 | 1205995.6923
9 | 2724471.6366 | 1206044.8052
10 | 2724403.0554 | 1206035.17
11 | 2724423.9724 | 1206042.8214
12 | 2724427.0488 | 1206044.1532
13 | 2724437.8202 | 1206034.8942
14 | 2724446.3538 | 1206038.5664
15 | 2724447.6183 | 1206039.0158
16 | 2724452.6924 | 1206040.8191
17 | 2724460.9667 | 1206043.7598
18 | 2724462.3147 | 1206050.0562
19 | 2724463.8141 | 1206044.7644
20 | 2724470.6538 | 1206044.6834
21 | 2724466.6666 | 1205993.1232
22 | 2724421.5696 | 1205981.9859
23 | 2724432.4598 | 1205984.6754
24 | 2724413.3508 | 1205979.9562
25 | 2724438.8052 | 1205986.2424
26 | 2724446.7931 | 1205988.2152
27 | 2724451.0824 | 1205989.2745
28 | 2724458.243 | 1205991.0429
29 | 2724459.4113 | 1205991.3314
30 | 2724464.9128 | 1205992.6901
31 | 2724427.0488 | 1206044.1532

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99186 | -0.056864 | 0.011897 | 0.0029816
1 | 0.992 | -0.055941 | 0.0063759 | 0.001598
2 | 0.99204 | -0.055611 | 0 | 0
3 | 0.9942 | -0.040393 | 0 | 0
4 | 0.9945 | -0.038325 | 0.0093604 | 0.0023459
5 | 0.99475 | -0.036573 | 0 | 0
6 | 0.98937 | -0.074289 | 0 | 0
7 | 0.99602 | -0.02771 | 0.0076612 | 0.0019201
8 | 0.98757 | -0.086999 | 0.0084462 | 0.0021168
9 | 0.99656 | -0.02391 | 0.005323 | 0.0013341
10 | 0.9975 | -0.017481 | 0.039297 | 0.0098488
11 | 0.99875 | -0.0087114 | 0 | 0
12 | 0.99894 | -0.0073968 | 0 | 0
13 | 1 | 0 | -0.18697 | -0.046854
14 | 0.99902 | -0.0067715 | 0.0060809 | 0.001524
15 | 0.99889 | -0.0077066 | 0.0052361 | 0.0013123
16 | 0.99837 | -0.01132 | 0.0058801 | 0.0014737
17 | 0.99756 | -0.016962 | 0 | 0
18 | 0.99723 | -0.019241 | 0.006198 | 0.0015534
19 | 0.99728 | -0.018898 | 0 | 0
20 | 0.99664 | -0.023331 | 0.0055631 | 0.0013943
21 | 0.98637 | -0.095439 | 0.0044528 | 0.001116
22 | 0.98414 | -0.11127 | 0.0049544 | 0.0012417
23 | 0.98443 | -0.10927 | 0.0061198 | 0.0015338
24 | 0.98399 | -0.11235 | 0.012375 | 0.0031014
25 | 0.98465 | -0.10769 | 0.0057818 | 0.0014491
26 | 0.985 | -0.10522 | 0.0080109 | 0.0020077
27 | 0.98523 | -0.10352 | 0.0044179 | 0.0011072
28 | 0.98568 | -0.10037 | 0.0047147 | 0.0011816
29 | 0.98576 | -0.099794 | 0.0084317 | 0.0021132
30 | 0.98621 | -0.096605 | 0.0081106 | 0.0020327
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011897 | -0.0029816 | 0.011898 | 0.002982 | 1.5209e-06 | 4.8619e-07 | 0.017847 | 0.017847 | 0.017847 | 0.99186 | -0.056864 | 0.992 | -0.055941 | 6.6102
1 | -0.018274 | -0.00458 | 0.018275 | 0.0045803 | 8.3432e-07 | 2.9792e-07 | 0.027411 | 0.027411 | 0.027411 | 0.992 | -0.055941 | 0.99204 | -0.055611 | 10.1524
2 | -0.018275 | -0.0045803 | 0.018313 | 0.0045941 | 3.858e-05 | 1.3774e-05 | 0.027411 | 0.027411 | 0.027411 | 0.99204 | -0.055611 | 0.9942 | -0.040393 | 10.1524
3 | -0.018313 | -0.0045941 | 0.018319 | 0.0045959 | 5.2522e-06 | 1.8748e-06 | 0.027411 | 0.027411 | 0.027411 | 0.9942 | -0.040393 | 0.9945 | -0.038325 | 10.1522
4 | -0.027679 | -0.0069419 | 0.027686 | 0.0069444 | 6.7269e-06 | 2.5057e-06 | 0.041417 | 0.041417 | 0.041417 | 0.9945 | -0.038325 | 0.99475 | -0.036573 | 15.3395
5 | 0.076517 | 0.019269 | -0.076116 | -0.019116 | 0.00040122 | 0.00015368 | 0.11449 | 0.11449 | 0.11449 | 0.99475 | -0.036573 | 0.98937 | -0.074289 | 42.4048
6 | -0.1042 | -0.026214 | 0.10433 | 0.026263 | 0.00012898 | 4.9496e-05 | 0.15591 | 0.15591 | 0.15591 | 0.99475 | -0.036573 | 0.99602 | -0.02771 | 57.7442
7 | 0.076116 | 0.019116 | -0.075982 | -0.019064 | 0.00013423 | 5.1418e-05 | 0.11449 | 0.11449 | 0.11449 | 0.98937 | -0.074289 | 0.98757 | -0.086999 | 42.4048
8 | -0.11199 | -0.028183 | 0.11205 | 0.028206 | 5.9429e-05 | 2.268e-05 | 0.16735 | 0.16735 | 0.16735 | 0.99602 | -0.02771 | 0.99656 | -0.02391 | 30.9916
9 | 0.067536 | 0.016947 | -0.067456 | -0.016917 | 7.901e-05 | 3.0232e-05 | 0.10177 | 0.10177 | 0.10177 | 0.98757 | -0.086999 | 0.98637 | -0.095439 | 37.6914
10 | -0.11738 | -0.02954 | 0.11739 | 0.029544 | 9.4958e-06 | 3.6264e-06 | 0.1753 | 0.1753 | 0.1753 | 0.99656 | -0.02391 | 0.99664 | -0.023331 | 32.4635
11 | -0.039297 | -0.0098488 | 0.039345 | 0.0098669 | 4.7764e-05 | 1.808e-05 | 0.058621 | 0.058621 | 0.058621 | 0.9975 | -0.017481 | 0.99875 | -0.0087114 | 21.7116
12 | -0.039345 | -0.0098669 | 0.039352 | 0.0098696 | 7.1707e-06 | 2.7142e-06 | 0.058621 | 0.058621 | 0.058621 | 0.99875 | -0.0087114 | 0.99894 | -0.0073968 | 21.7115
13 | -0.039352 | -0.0098696 | 0.039393 | 0.0098849 | 4.0395e-05 | 1.529e-05 | 0.058621 | 0.058621 | 0.058621 | 0.99894 | -0.0073968 | 1 | 0 | 21.7115
14 | 0.14678 | 0.036969 | -0.14664 | -0.036916 | 0.00013883 | 5.3152e-05 | 0.21848 | 0.21848 | 0.21848 | 1 | 0 | 0.99902 | -0.0067715 | 40.4589
15 | 0.14056 | 0.035392 | -0.14054 | -0.035385 | 1.8363e-05 | 7.0276e-06 | 0.20942 | 0.20942 | 0.20942 | 0.99902 | -0.0067715 | 0.99889 | -0.0077066 | 38.7816
16 | 0.13531 | 0.034072 | -0.13524 | -0.034046 | 6.8299e-05 | 2.6128e-05 | 0.20162 | 0.20162 | 0.20162 | 0.99889 | -0.0077066 | 0.99837 | -0.01132 | 37.3372
17 | 0.12936 | 0.032573 | -0.12926 | -0.032534 | 0.0001019 | 3.8964e-05 | 0.19286 | 0.19286 | 0.19286 | 0.99837 | -0.01132 | 0.99756 | -0.016962 | 35.7142
18 | 0.12926 | 0.032534 | -0.12922 | -0.03252 | 3.4941e-05 | 1.336e-05 | 0.19286 | 0.19286 | 0.19286 | 0.99756 | -0.016962 | 0.99728 | -0.018898 | 35.7142
19 | -0.006198 | -0.0015534 | 0.0061982 | 0.0015534 | 2.9355e-07 | 4.114e-08 | 0.0092483 | 0.0092482 | 0.0092483 | 0.99723 | -0.019241 | 0.99728 | -0.018898 | 3.4253
20 | 0.12302 | 0.030967 | -0.12295 | -0.030938 | 7.6096e-05 | 2.9079e-05 | 0.18361 | 0.18361 | 0.18361 | 0.99728 | -0.018898 | 0.99664 | -0.023331 | 34.0016
21 | 0.063004 | 0.015801 | -0.062994 | -0.015797 | 1.0184e-05 | 3.8938e-06 | 0.095049 | 0.095049 | 0.095049 | 0.98637 | -0.095439 | 0.98621 | -0.096605 | 35.2035
22 | -0.017331 | -0.0043437 | 0.017336 | 0.0043454 | 4.8064e-06 | 1.706e-06 | 0.026204 | 0.026204 | 0.026204 | 0.98414 | -0.11127 | 0.98443 | -0.10927 | 9.7053
23 | 0.012377 | 0.003102 | -0.012375 | -0.0031014 | 1.8499e-06 | 6.0395e-07 | 0.018713 | 0.018713 | 0.018713 | 0.98414 | -0.11127 | 0.98399 | -0.11235 | 6.9309
24 | -0.023456 | -0.0058792 | 0.023461 | 0.0058811 | 5.1268e-06 | 1.8887e-06 | 0.035455 | 0.035455 | 0.035455 | 0.98443 | -0.10927 | 0.98465 | -0.10769 | 13.1314
25 | -0.029243 | -0.0073301 | 0.029253 | 0.0073339 | 1.0027e-05 | 3.7518e-06 | 0.044192 | 0.044192 | 0.044192 | 0.98465 | -0.10769 | 0.985 | -0.10522 | 16.3675
26 | -0.037264 | -0.0093416 | 0.037272 | 0.0093449 | 8.7369e-06 | 3.3041e-06 | 0.056294 | 0.056294 | 0.056294 | 0.985 | -0.10522 | 0.98523 | -0.10352 | 20.8497
27 | -0.04169 | -0.010452 | 0.041709 | 0.010459 | 1.8248e-05 | 6.9245e-06 | 0.062967 | 0.062967 | 0.062967 | 0.98523 | -0.10352 | 0.98568 | -0.10037 | 23.321
28 | -0.046423 | -0.011641 | 0.046427 | 0.011642 | 3.6884e-06 | 1.4033e-06 | 0.070084 | 0.070084 | 0.070084 | 0.98568 | -0.10037 | 0.98576 | -0.099794 | 25.9571
29 | -0.054859 | -0.013755 | 0.054883 | 0.013765 | 2.425e-05 | 9.2546e-06 | 0.082812 | 0.082812 | 0.082812 | 0.98576 | -0.099794 | 0.98621 | -0.096605 | 30.6711

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19818 | 0.049662

## res_load
| p_mw | q_mvar
0 | 0.011897 | 0.0029816
1 | 0.0063759 | 0.001598
2 | 0.0093604 | 0.0023459
3 | 0.0076612 | 0.0019201
4 | 0.0084462 | 0.0021168
5 | 0.005323 | 0.0013341
6 | 0.039297 | 0.0098488
7 | 0.011204 | 0.0028079
8 | 0.0060809 | 0.001524
9 | 0.0052361 | 0.0013123
10 | 0.0058801 | 0.0014737
11 | 0.006198 | 0.0015534
12 | 0.0055631 | 0.0013943
13 | 0.0044528 | 0.001116
14 | 0.0049544 | 0.0012417
15 | 0.0061198 | 0.0015338
16 | 0.012375 | 0.0031014
17 | 0.0057818 | 0.0014491
18 | 0.0080109 | 0.0020077
19 | 0.0044179 | 0.0011072
20 | 0.0047147 | 0.0011816
21 | 0.0084317 | 0.0021132
22 | 0.0081106 | 0.0020327

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1