## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-206_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-206_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1631-206_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1631-206_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1631-206_0_2_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1631-206_0_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_1631-206_0_2_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1631-206_0_2_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1631-206_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1631-206_0_2_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1631-206_0_2_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1631-206_0_2_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1631-206_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1631-206_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-206_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1631-206_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1631-206_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1631-206_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1631-206_0_2_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1631-206_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1631-206_0_2_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1631-206_0_2_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1631-206_0_2_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_1631-206_0_2_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1631-206_0_2_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1631-206_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_MV_145_1_node_167 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-206_0_2_load_0 | 0 | 0.0011694 | 0.00029308 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-206_0_2_load_4 | 3 | 0.00087008 | 0.00021806 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-206_0_2_load_20 | 5 | 0.0020393 | 0.00051109 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-206_0_2_load_21 | 6 | 0.0020663 | 0.00051786 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-206_0_2_load_12 | 7 | 0.0043549 | 0.0010914 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-206_0_2_load_6 | 8 | 0.0090882 | 0.0022777 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-206_0_2_load_19 | 9 | 0.002801 | 0.00070199 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-206_0_2_load_5 | 11 | 0.0074836 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-206_0_2_load_7 | 12 | 0.0054064 | 0.001355 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-206_0_2_load_9 | 13 | 0.0066037 | 0.001655 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-206_0_2_load_13 | 15 | 0.0043134 | 0.001081 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-206_0_2_load_11 | 16 | 0.0090527 | 0.0022688 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-206_0_2_load_18 | 19 | 0.005702 | 0.0014291 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-206_0_2_load_17 | 20 | 0.0013471 | 0.00033763 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-206_0_2_load_15 | 21 | 0.0058339 | 0.0014621 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-206_0_2_load_25 | 22 | 0.0017994 | 0.00045097 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-206_0_2_load_26 | 23 | 0.0017677 | 0.00044303 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-206_0_2_load_23 | 24 | 0.0032567 | 0.0008162 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-206_0_2_load_24 | 25 | 0.00095933 | 0.00024043 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-206_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.035884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-206_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.012982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-206_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.024464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-206_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.038886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-206_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.061043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-206_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.015713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-206_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.016084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-206_0_2_line_7 | NAYY 4x150 SE | 4 | 8 | 0.003921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-206_0_2_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0017256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-206_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.027187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-206_0_2_line_10 | NAYY 4x150 SE | 7 | 15 | 0.0061295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-206_0_2_line_11 | NAYY 4x150 SE | 8 | 11 | 0.012109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-206_0_2_line_12 | NAYY 4x150 SE | 10 | 24 | 0.014723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-206_0_2_line_13 | NAYY 4x150 SE | 10 | 25 | 0.012835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-206_0_2_line_14 | NAYY 4x150 SE | 11 | 12 | 0.0026841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-206_0_2_line_15 | NAYY 4x150 SE | 12 | 13 | 0.0010563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-206_0_2_line_16 | NAYY 4x150 SE | 13 | 14 | 0.023061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-206_0_2_line_17 | NAYY 4x150 SE | 14 | 16 | 0.017093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-206_0_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.007828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-206_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.017368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-206_0_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.034753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-206_0_2_line_21 | NAYY 4x150 SE | 18 | 20 | 0.0091624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-206_0_2_line_22 | NAYY 4x150 SE | 18 | 21 | 0.017176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-206_0_2_line_23 | NAYY 4x150 SE | 20 | 22 | 0.023952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-206_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0068895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-206_0_2_trafo_12 | 0.25 MVA 20/0.4 kV | 26 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2730481.0145 | 1204698.8076 | 2730486.8752 | 1204703.2947 | 2730488.6882 | 1204710.173 | 2730491.4415 | 1204731.3845
1 | 2730481.0145 | 1204698.8076 | 2730477.4556 | 1204707.0363 | 2730475.8077 | 1204710.7032
2 | 2730481.0145 | 1204698.8076 | 2730490.851 | 1204676.6942 | 2730490.9649 | 1204676.4591
3 | 2730459.7368 | 1204746.1242 | 2730475.8077 | 1204710.7032
4 | 2730475.8077 | 1204710.7032 | 2730474.2288 | 1204703.9078 | 2730478.0386 | 1204695.3399 | 2730481.4323 | 1204675.5208 | 2730480.7729 | 1204672.96 | 2730479.3872 | 1204671.2506 | 2730477.2664 | 1204670.0922 | 2730473.2293 | 1204670.2597 | 2730470.6534 | 1204671.471 | 2730468.4826 | 1204675.0375 | 2730466.0471 | 1204680.8032
5 | 2730490.9649 | 1204676.4591 | 2730497.8159 | 1204662.3181
6 | 2730459.7368 | 1204746.1242 | 2730447.8857 | 1204735.2501
7 | 2730459.7368 | 1204746.1242 | 2730458.4126 | 1204749.8148
8 | 2730466.0471 | 1204680.8032 | 2730465.3756 | 1204682.3928
9 | 2730514.7542 | 1204641.2333 | 2730511.8043 | 1204643.882 | 2730507.5674 | 1204648.3151 | 2730503.5293 | 1204653.3975 | 2730498.1436 | 1204661.6418 | 2730497.8159 | 1204662.3181
10 | 2730443.3693 | 1204731.1061 | 2730447.8857 | 1204735.2501
11 | 2730454.3721 | 1204761.2278 | 2730454.5665 | 1204760.5336 | 2730458.4126 | 1204749.8148
12 | 2730514.7542 | 1204641.2333 | 2730524.9421 | 1204651.8619
13 | 2730514.7542 | 1204641.2333 | 2730519.6796 | 1204637.6826 | 2730525.2947 | 1204633.9135
14 | 2730453.6484 | 1204763.8124 | 2730454.3721 | 1204761.2278
15 | 2730453.6484 | 1204763.8124 | 2730453.3636 | 1204764.8295
16 | 2730447.1456 | 1204787.0366 | 2730453.3636 | 1204764.8295
17 | 2730447.1456 | 1204787.0366 | 2730430.5087 | 1204782.9145
18 | 2730437.6014 | 1204725.8137 | 2730443.3693 | 1204731.1061
19 | 2730437.6014 | 1204725.8137 | 2730424.4096 | 1204714.4723
20 | 2730437.6014 | 1204725.8137 | 2730419.4188 | 1204739.127 | 2730410.3274 | 1204747.2889
21 | 2730424.4096 | 1204714.4723 | 2730424.72 | 1204708.9748 | 2730423.074 | 1204705.7101
22 | 2730424.4096 | 1204714.4723 | 2730412.9196 | 1204727.2394
23 | 2730417.7438 | 1204683.4093 | 2730416.6061 | 1204688.148 | 2730416.7038 | 1204693.0762 | 2730423.074 | 1204705.7101
24 | 2730419.3522 | 1204676.7102 | 2730417.7438 | 1204683.4093

## bus_geodata
| x | y | coords
0 | 2730491.4415 | 1204731.3845
1 | 2730481.0145 | 1204698.8076
2 | 2730475.8077 | 1204710.7032
3 | 2730490.9649 | 1204676.4591
4 | 2730459.7368 | 1204746.1242
5 | 2730466.0471 | 1204680.8032
6 | 2730497.8159 | 1204662.3181
7 | 2730447.8857 | 1204735.2501
8 | 2730458.4126 | 1204749.8148
9 | 2730465.3756 | 1204682.3928
10 | 2730514.7542 | 1204641.2333
11 | 2730454.3721 | 1204761.2278
12 | 2730453.6484 | 1204763.8124
13 | 2730453.3636 | 1204764.8295
14 | 2730447.1456 | 1204787.0366
15 | 2730443.3693 | 1204731.1061
16 | 2730430.5087 | 1204782.9145
17 | 2730437.6014 | 1204725.8137
18 | 2730424.4096 | 1204714.4723
19 | 2730410.3274 | 1204747.2889
20 | 2730423.074 | 1204705.7101
21 | 2730412.9196 | 1204727.2394
22 | 2730417.7438 | 1204683.4093
23 | 2730419.3522 | 1204676.7102
24 | 2730524.9421 | 1204651.8619
25 | 2730525.2947 | 1204633.9135
26 | 2730437.6014 | 1204725.8137

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99789 | -0.014806 | 0.0011694 | 0.00029308
1 | 0.99795 | -0.014385 | 0 | 0
2 | 0.9981 | -0.013301 | 0 | 0
3 | 0.9977 | -0.016141 | 0.00087008 | 0.00021806
4 | 0.99883 | -0.0081685 | 0 | 0
5 | 0.99768 | -0.016264 | 0.0020393 | 0.00051109
6 | 0.99756 | -0.017132 | 0.0020663 | 0.00051786
7 | 1 | 0 | -0.072474 | -0.017973
8 | 0.99862 | -0.0096452 | 0.0090882 | 0.0022777
9 | 0.99767 | -0.016313 | 0.002801 | 0.00070199
10 | 0.99739 | -0.018283 | 0 | 0
11 | 0.99813 | -0.013107 | 0.0074836 | 0.0018756
12 | 0.99805 | -0.013673 | 0.0054064 | 0.001355
13 | 0.99802 | -0.013839 | 0.0066037 | 0.001655
14 | 0.99773 | -0.015932 | 0 | 0
15 | 0.99982 | -0.0012712 | 0.0043134 | 0.001081
16 | 0.9975 | -0.017484 | 0.0090527 | 0.0022688
17 | 0.99963 | -0.0025579 | 0 | 0
18 | 0.99937 | -0.0044239 | 0 | 0
19 | 0.99935 | -0.0045382 | 0.005702 | 0.0014291
20 | 0.9993 | -0.0048742 | 0.0013471 | 0.00033763
21 | 0.99923 | -0.0054256 | 0.0058339 | 0.0014621
22 | 0.99918 | -0.0057287 | 0.0017994 | 0.00045097
23 | 0.99917 | -0.0058504 | 0.0017677 | 0.00044303
24 | 0.99732 | -0.018764 | 0.0032567 | 0.0008162
25 | 0.99738 | -0.018406 | 0.00095933 | 0.00024043
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0011694 | -0.00029308 | 0.0011695 | 0.00029264 | 6.8081e-08 | -4.4263e-07 | 0.0017438 | 0.0017436 | 0.0017438 | 0.99789 | -0.014806 | 0.99795 | -0.014385 | 0.64584
1 | -0.0083254 | -0.0020853 | 0.0083266 | 0.0020856 | 1.2482e-06 | 3.1045e-07 | 0.012413 | 0.012413 | 0.012413 | 0.99795 | -0.014385 | 0.9981 | -0.013301 | 4.5975
2 | 0.0071559 | 0.0017927 | -0.0071541 | -0.0017923 | 1.7379e-06 | 3.4886e-07 | 0.01067 | 0.01067 | 0.01067 | 0.99795 | -0.014385 | 0.9977 | -0.016141 | 3.9518
3 | -0.013169 | -0.0032986 | 0.013178 | 0.0033017 | 9.3521e-06 | 3.0884e-06 | 0.019632 | 0.019632 | 0.019632 | 0.9981 | -0.013301 | 0.99883 | -0.0081685 | 7.2712
4 | 0.0048423 | 0.001213 | -0.0048403 | -0.0012131 | 1.9851e-06 | -3.3978e-08 | 0.0072189 | 0.0072191 | 0.0072191 | 0.9981 | -0.013301 | 0.99768 | -0.016264 | 2.6738
5 | 0.0062841 | 0.0015743 | -0.0062832 | -0.0015741 | 8.6125e-07 | 1.2608e-07 | 0.0093721 | 0.0093722 | 0.0093722 | 0.9977 | -0.016141 | 0.99756 | -0.017132 | 3.4712
6 | -0.050841 | -0.012744 | 0.050898 | 0.012766 | 5.7576e-05 | 2.1934e-05 | 0.075741 | 0.075741 | 0.075741 | 0.99883 | -0.0081685 | 1 | 0 | 28.0522
7 | 0.037663 | 0.0094421 | -0.037655 | -0.0094392 | 7.7028e-06 | 2.9113e-06 | 0.056109 | 0.056109 | 0.056109 | 0.99883 | -0.0081685 | 0.99862 | -0.0096452 | 20.7811
8 | 0.002801 | 0.00070197 | -0.002801 | -0.00070199 | 1.8793e-08 | -1.5306e-08 | 0.0041776 | 0.0041776 | 0.0041776 | 0.99768 | -0.016264 | 0.99767 | -0.016313 | 1.5473
9 | 0.0042169 | 0.0010563 | -0.0042162 | -0.0010564 | 6.7121e-07 | -9.6719e-08 | 0.00629 | 0.0062901 | 0.0062901 | 0.99756 | -0.017132 | 0.99739 | -0.018283 | 2.3297
10 | 0.020776 | 0.005207 | -0.020772 | -0.0052057 | 3.6556e-06 | 1.3256e-06 | 0.030915 | 0.030915 | 0.030915 | 1 | 0 | 0.99982 | -0.0012712 | 11.4501
11 | 0.028567 | 0.0071615 | -0.028553 | -0.0071564 | 1.3691e-05 | 5.1074e-06 | 0.042567 | 0.042567 | 0.042567 | 0.99862 | -0.0096452 | 0.99813 | -0.013107 | 15.7656
12 | 0.0032569 | 0.00081609 | -0.0032567 | -0.0008162 | 2.169e-07 | -1.0871e-07 | 0.0048589 | 0.004859 | 0.004859 | 0.99739 | -0.018283 | 0.99732 | -0.018764 | 1.7996
13 | 0.00095935 | 0.00024027 | -0.00095933 | -0.00024043 | 1.6406e-08 | -1.6119e-07 | 0.0014312 | 0.0014313 | 0.0014313 | 0.99739 | -0.018283 | 0.99738 | -0.018406 | 0.5301
14 | 0.021069 | 0.0052808 | -0.021068 | -0.0052802 | 1.6524e-06 | 6.0048e-07 | 0.03141 | 0.031411 | 0.031411 | 0.99813 | -0.013107 | 0.99805 | -0.013673 | 11.6335
15 | 0.015661 | 0.0039252 | -0.015661 | -0.0039251 | 3.5936e-07 | 1.2441e-07 | 0.02335 | 0.02335 | 0.02335 | 0.99805 | -0.013673 | 0.99802 | -0.013839 | 8.6481
16 | 0.0090573 | 0.0022701 | -0.0090547 | -0.0022694 | 2.6242e-06 | 7.0806e-07 | 0.013504 | 0.013504 | 0.013504 | 0.99802 | -0.013839 | 0.99773 | -0.015932 | 5.0016
17 | 0.0090547 | 0.0022694 | -0.0090527 | -0.0022688 | 1.9451e-06 | 5.2494e-07 | 0.013504 | 0.013504 | 0.013504 | 0.99773 | -0.015932 | 0.9975 | -0.017484 | 5.0016
18 | 0.016459 | 0.0041247 | -0.016456 | -0.0041236 | 2.931e-06 | 1.0247e-06 | 0.024496 | 0.024496 | 0.024496 | 0.99982 | -0.0012712 | 0.99963 | -0.0025579 | 9.0724
19 | 0.010752 | 0.0026944 | -0.01075 | -0.0026936 | 2.7764e-06 | 8.4021e-07 | 0.016006 | 0.016006 | 0.016006 | 0.99963 | -0.0025579 | 0.99937 | -0.0044239 | 5.928
20 | 0.0057036 | 0.0014292 | -0.005702 | -0.0014291 | 1.5632e-06 | 1.4574e-07 | 0.00849 | 0.0084902 | 0.0084902 | 0.99963 | -0.0025579 | 0.99935 | -0.0045382 | 3.1445
21 | 0.004915 | 0.0012314 | -0.0049147 | -0.0012314 | 3.0619e-07 | -2.2797e-09 | 0.0073181 | 0.0073181 | 0.0073181 | 0.99937 | -0.0044239 | 0.9993 | -0.0048742 | 2.7104
22 | 0.0058347 | 0.0014622 | -0.0058339 | -0.0014621 | 8.0893e-07 | 8.6105e-08 | 0.0086876 | 0.0086877 | 0.0086877 | 0.99937 | -0.0044239 | 0.99923 | -0.0054256 | 3.2176
23 | 0.0035675 | 0.00089377 | -0.0035671 | -0.00089392 | 4.2176e-07 | -1.5154e-07 | 0.0053121 | 0.0053123 | 0.0053123 | 0.9993 | -0.0048742 | 0.99918 | -0.0057287 | 1.9675
24 | 0.0017677 | 0.00044295 | -0.0017677 | -0.00044303 | 2.9794e-08 | -7.8777e-08 | 0.0026325 | 0.0026326 | 0.0026326 | 0.99918 | -0.0057287 | 0.99917 | -0.0058504 | 0.97502

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.076829 | 0.019064

## res_load
| p_mw | q_mvar
0 | 0.0011694 | 0.00029308
1 | 0.00087008 | 0.00021806
2 | 0.0020393 | 0.00051109
3 | 0.0020663 | 0.00051786
4 | 0.0043549 | 0.0010914
5 | 0.0090882 | 0.0022777
6 | 0.002801 | 0.00070199
7 | 0.0074836 | 0.0018756
8 | 0.0054064 | 0.001355
9 | 0.0066037 | 0.001655
10 | 0.0043134 | 0.001081
11 | 0.0090527 | 0.0022688
12 | 0.005702 | 0.0014291
13 | 0.0013471 | 0.00033763
14 | 0.0058339 | 0.0014621
15 | 0.0017994 | 0.00045097
16 | 0.0017677 | 0.00044303
17 | 0.0032567 | 0.0008162
18 | 0.00095933 | 0.00024043

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1