## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-26_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-26_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-26_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-26_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-26_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-26_0_2_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1631-26_0_2_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1631-26_0_2_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1631-26_0_2_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1631-26_0_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1631-26_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1631-26_0_2_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1631-26_0_2_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1631-26_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1631-26_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1631-26_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1631-26_0_2_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1631-26_0_2_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1631-26_0_2_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1631-26_0_2_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_1631-26_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1631-26_0_2_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_1631-26_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1631-26_0_2_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1631-26_0_2_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1631-26_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1631-26_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1631-26_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1631-26_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1631-26_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1631-26_0_2_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1631-26_0_2_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1631-26_0_2_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1631-26_0_2_node_26 | 0.4 | n |  | TRUE
34 | bus_MV_144_0_node_46 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-26_0_2_load_0 | 0 | 0.0038756 | 0.00097132 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-26_0_2_load_1 | 1 | 0.00091069 | 0.00022824 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-26_0_2_load_2 | 2 | 0.0084623 | 0.0021209 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-26_0_2_load_4 | 4 | 0.0037293 | 0.00093465 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-26_0_2_load_32 | 7 | 0.0017852 | 0.00044742 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-26_0_2_load_33 | 8 | 0.00070476 | 0.00017663 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-26_0_2_load_5 | 11 | 0.010275 | 0.0025751 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-26_0_2_load_6 | 12 | 0.012974 | 0.0032517 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-26_0_2_load_9 | 14 | 0.014074 | 0.0035273 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-26_0_2_load_30 | 16 | 0.0063863 | 0.0016006 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-26_0_2_load_29 | 17 | 0.0064454 | 0.0016154 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-26_0_2_load_28 | 18 | 0.0030816 | 0.00077232 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-26_0_2_load_34 | 19 | 0.010228 | 0.0025634 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-26_0_2_load_31 | 21 | 0.020117 | 0.0050419 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-26_0_2_load_16 | 22 | 0.011037 | 0.0027662 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-26_0_2_load_14 | 23 | 0.0038937 | 0.00097585 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-26_0_2_load_17 | 24 | 0.0069614 | 0.0017447 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-26_0_2_load_21 | 27 | 0.0068864 | 0.0017259 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-26_0_2_load_22 | 28 | 0.0054238 | 0.0013593 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-26_0_2_load_27 | 29 | 0.0034715 | 0.00087003 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-26_0_2_load_23 | 30 | 0.0028985 | 0.00072644 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-26_0_2_load_25 | 31 | 0.0068902 | 0.0017269 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-26_0_2_load_24 | 32 | 0.0035483 | 0.00088929 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-26_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-26_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.027096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-26_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.048723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-26_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.037224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-26_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.008676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-26_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.027965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-26_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.030002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-26_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.021914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-26_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.006477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-26_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.046437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-26_0_2_line_10 | NAYY 4x150 SE | 9 | 19 | 0.018021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-26_0_2_line_11 | NAYY 4x150 SE | 9 | 20 | 0.020457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-26_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.007376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-26_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.0081305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-26_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.012248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-26_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.01804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1631-26_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.002408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-26_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.020578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-26_0_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.022817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-26_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.010902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-26_0_2_line_20 | NAYY 4x150 SE | 18 | 33 | 0.003323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-26_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.025527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-26_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.015337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-26_0_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.0041469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-26_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.034413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-26_0_2_line_25 | NAYY 4x150 SE | 25 | 26 | 0.007134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-26_0_2_line_26 | NAYY 4x150 SE | 25 | 27 | 0.01814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-26_0_2_line_27 | NAYY 4x150 SE | 26 | 28 | 0.0074204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-26_0_2_line_28 | NAYY 4x150 SE | 27 | 29 | 0.0080804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-26_0_2_line_29 | NAYY 4x150 SE | 28 | 30 | 0.0044656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-26_0_2_line_30 | NAYY 4x150 SE | 29 | 31 | 0.0076255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-26_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0012995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-26_0_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.013117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-26_0_2_trafo_9 | 0.25 MVA 20/0.4 kV | 34 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2724935.0028 | 1208394.8762 | 2724935.5967 | 1208409.1832
1 | 2724935.0028 | 1208394.8762 | 2724934.7683 | 1208389.2277 | 2724933.4471 | 1208367.8257
2 | 2724936.0907 | 1208457.8859 | 2724936.4666 | 1208430.1391 | 2724935.5967 | 1208409.1832
3 | 2724931.1536 | 1208330.6726 | 2724933.4471 | 1208367.8257
4 | 2724936.0907 | 1208457.8859 | 2724927.4405 | 1208456.9485
5 | 2724929.4306 | 1208302.7607 | 2724931.1536 | 1208330.6726
6 | 2724927.4405 | 1208456.9485 | 2724925.8286 | 1208448.575 | 2724925.2591 | 1208427.1133
7 | 2724913.3432 | 1208443.3875 | 2724913.0697 | 1208448.8193 | 2724927.4405 | 1208456.9485
8 | 2724935.9228 | 1208302.5298 | 2724929.4306 | 1208302.7607
9 | 2724929.4306 | 1208302.7607 | 2724926.5682 | 1208256.4208
10 | 2724945.4913 | 1208289.0531 | 2724946.0047 | 1208293.5895 | 2724935.9228 | 1208302.5298
11 | 2724952.2961 | 1208314.5595 | 2724945.8309 | 1208309.1423 | 2724939.4172 | 1208303.815 | 2724935.9228 | 1208302.5298
12 | 2724926.5682 | 1208256.4208 | 2724920.9592 | 1208257.3263 | 2724919.6854 | 1208258.4437
13 | 2724917.4055 | 1208265.943 | 2724918.0191 | 1208262.6244 | 2724918.4955 | 1208259.4876 | 2724919.6854 | 1208258.4437
14 | 2724911.7808 | 1208276.1487 | 2724914.146 | 1208274.6971 | 2724915.604 | 1208272.626 | 2724916.8354 | 1208269.0268 | 2724917.4055 | 1208265.943
15 | 2724911.7808 | 1208276.1487 | 2724910.0732 | 1208294.1075
16 | 2724909.3927 | 1208276.5101 | 2724911.7808 | 1208276.1487
17 | 2724903.5409 | 1208292.6445 | 2724907.8285 | 1208292.7343 | 2724909.3927 | 1208276.5101
18 | 2724909.3927 | 1208276.5101 | 2724886.6057 | 1208277.6699
19 | 2724875.7175 | 1208278.2241 | 2724886.6057 | 1208277.6699
20 | 2724872.3988 | 1208278.393 | 2724875.7175 | 1208278.2241
21 | 2724945.4913 | 1208289.0531 | 2724951.1086 | 1208264.1516
22 | 2724953.5578 | 1208329.8421 | 2724952.2961 | 1208314.5595
23 | 2724952.2961 | 1208314.5595 | 2724955.8082 | 1208316.7645
24 | 2724824.333 | 1208282.7465 | 2724826.6887 | 1208263.5811 | 2724826.6396 | 1208253.5724 | 2724825.5405 | 1208248.598
25 | 2724823.69 | 1208289.8496 | 2724824.333 | 1208282.7465
26 | 2724824.333 | 1208282.7465 | 2724842.3991 | 1208281.1102
27 | 2724823.69 | 1208289.8496 | 2724823.0228 | 1208297.24
28 | 2724850.4465 | 1208280.3813 | 2724842.3991 | 1208281.1102
29 | 2724823.0228 | 1208297.24 | 2724822.6212 | 1208301.6874
30 | 2724850.4465 | 1208280.3813 | 2724858.0409 | 1208279.6935
31 | 2724859.3351 | 1208279.5762 | 2724858.0409 | 1208279.6935
32 | 2724872.3988 | 1208278.393 | 2724859.3351 | 1208279.5762

## bus_geodata
| x | y | coords
0 | 2724935.0028 | 1208394.8762
1 | 2724935.5967 | 1208409.1832
2 | 2724933.4471 | 1208367.8257
3 | 2724936.0907 | 1208457.8859
4 | 2724931.1536 | 1208330.6726
5 | 2724927.4405 | 1208456.9485
6 | 2724929.4306 | 1208302.7607
7 | 2724925.2591 | 1208427.1133
8 | 2724913.3432 | 1208443.3875
9 | 2724935.9228 | 1208302.5298
10 | 2724926.5682 | 1208256.4208
11 | 2724917.4055 | 1208265.943
12 | 2724919.6854 | 1208258.4437
13 | 2724911.7808 | 1208276.1487
14 | 2724910.0732 | 1208294.1075
15 | 2724909.3927 | 1208276.5101
16 | 2724903.5409 | 1208292.6445
17 | 2724886.6057 | 1208277.6699
18 | 2724875.7175 | 1208278.2241
19 | 2724945.4913 | 1208289.0531
20 | 2724952.2961 | 1208314.5595
21 | 2724951.1086 | 1208264.1516
22 | 2724953.5578 | 1208329.8421
23 | 2724955.8082 | 1208316.7645
24 | 2724825.5405 | 1208248.598
25 | 2724824.333 | 1208282.7465
26 | 2724823.69 | 1208289.8496
27 | 2724842.3991 | 1208281.1102
28 | 2724823.0228 | 1208297.24
29 | 2724850.4465 | 1208280.3813
30 | 2724822.6212 | 1208301.6874
31 | 2724858.0409 | 1208279.6935
32 | 2724859.3351 | 1208279.5762
33 | 2724872.3988 | 1208278.393
34 | 2724908.6596 | 1208308.9752

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98879 | -0.07861 | 0.0038756 | 0.00097132
1 | 0.98872 | -0.079109 | 0.00091069 | 0.00022824
2 | 0.98908 | -0.076594 | 0.0084623 | 0.0021209
3 | 0.98855 | -0.080351 | 0 | 0
4 | 0.98992 | -0.070616 | 0.0037293 | 0.00093465
5 | 0.98852 | -0.080572 | 0 | 0
6 | 0.99071 | -0.06507 | 0 | 0
7 | 0.98844 | -0.08112 | 0.0017852 | 0.00044742
8 | 0.98849 | -0.08073 | 0.00070476 | 0.00017663
9 | 0.99028 | -0.068054 | 0 | 0
10 | 0.99504 | -0.034617 | 0 | 0
11 | 0.99664 | -0.023446 | 0.010275 | 0.0025751
12 | 0.99573 | -0.029804 | 0.012974 | 0.0032517
13 | 0.99819 | -0.01263 | 0 | 0
14 | 1 | 0 | -0.14181 | -0.035469
15 | 0.99801 | -0.013884 | 0 | 0
16 | 0.99782 | -0.015202 | 0.0063863 | 0.0016006
17 | 0.99652 | -0.02433 | 0.0064454 | 0.0016154
18 | 0.9959 | -0.028624 | 0.0030816 | 0.00077232
19 | 0.9895 | -0.073625 | 0.010228 | 0.0025634
20 | 0.98984 | -0.071165 | 0 | 0
21 | 0.98876 | -0.078864 | 0.020117 | 0.0050419
22 | 0.9896 | -0.07289 | 0.011037 | 0.0027662
23 | 0.98982 | -0.071329 | 0.0038937 | 0.00097585
24 | 0.99372 | -0.044028 | 0.0069614 | 0.0017447
25 | 0.99406 | -0.041607 | 0 | 0
26 | 0.99397 | -0.042206 | 0 | 0
27 | 0.99446 | -0.038806 | 0.0068864 | 0.0017259
28 | 0.99388 | -0.04283 | 0.0054238 | 0.0013593
29 | 0.99471 | -0.036998 | 0.0034715 | 0.00087003
30 | 0.99387 | -0.042961 | 0.0028985 | 0.00072644
31 | 0.99499 | -0.035026 | 0.0068902 | 0.0017269
32 | 0.99505 | -0.0346 | 0.0035483 | 0.00088929
33 | 0.99573 | -0.029831 | 0 | 0
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0034016 | 0.00085105 | -0.0034013 | -0.00085114 | 2.3409e-07 | -9.3624e-08 | 0.0051184 | 0.0051185 | 0.0051185 | 0.98879 | -0.07861 | 0.98872 | -0.079109 | 1.8957
1 | -0.0072772 | -0.0018224 | 0.0072792 | 0.0018228 | 2.0276e-06 | 4.3217e-07 | 0.010951 | 0.010951 | 0.010951 | 0.98879 | -0.07861 | 0.98908 | -0.076594 | 4.0558
2 | 0.0024906 | 0.0006229 | -0.0024902 | -0.00062336 | 4.271e-07 | -4.605e-07 | 0.0037479 | 0.0037481 | 0.0037481 | 0.98872 | -0.079109 | 0.98855 | -0.080351 | 1.3882
3 | -0.015742 | -0.0039437 | 0.015755 | 0.0039482 | 1.3027e-05 | 4.5321e-06 | 0.023682 | 0.023682 | 0.023682 | 0.98908 | -0.076594 | 0.98992 | -0.070616 | 8.771
4 | 0.0024902 | 0.00062336 | -0.0024901 | -0.00062344 | 7.6057e-08 | -8.1975e-08 | 0.0037481 | 0.0037482 | 0.0037482 | 0.98855 | -0.080351 | 0.98852 | -0.080572 | 1.3882
5 | -0.019484 | -0.0048828 | 0.019499 | 0.0048882 | 1.4968e-05 | 5.397e-06 | 0.029287 | 0.029287 | 0.029287 | 0.98992 | -0.070616 | 0.99071 | -0.06507 | 10.8472
6 | 0.0017854 | 0.00044709 | -0.0017852 | -0.00044742 | 1.3521e-07 | -3.3258e-07 | 0.0026874 | 0.0026875 | 0.0026875 | 0.98852 | -0.080572 | 0.98844 | -0.08112 | 0.99538
7 | 0.00070477 | 0.00017635 | -0.00070476 | -0.00017663 | 1.5389e-08 | -2.7501e-07 | 0.0010608 | 0.0010609 | 0.0010609 | 0.98852 | -0.080572 | 0.98849 | -0.08073 | 0.39292
8 | 0.045342 | 0.011372 | -0.045324 | -0.011364 | 1.8747e-05 | 7.1269e-06 | 0.068106 | 0.068106 | 0.068106 | 0.99071 | -0.06507 | 0.99028 | -0.068054 | 25.2244
9 | -0.064841 | -0.01626 | 0.065116 | 0.016365 | 0.00027485 | 0.00010511 | 0.097393 | 0.097393 | 0.097393 | 0.99071 | -0.06507 | 0.99504 | -0.034617 | 36.0715
10 | 0.030384 | 0.0076194 | -0.03036 | -0.0076106 | 2.3441e-05 | 8.784e-06 | 0.045657 | 0.045657 | 0.045657 | 0.99028 | -0.068054 | 0.9895 | -0.073625 | 16.9099
11 | 0.01494 | 0.003745 | -0.014934 | -0.0037428 | 6.4333e-06 | 2.2113e-06 | 0.022449 | 0.022449 | 0.022449 | 0.99028 | -0.068054 | 0.98984 | -0.071165 | 8.3146
12 | -0.065116 | -0.016365 | 0.06516 | 0.016382 | 4.3658e-05 | 1.6695e-05 | 0.097393 | 0.097393 | 0.097393 | 0.99504 | -0.034617 | 0.99573 | -0.029804 | 36.0714
13 | 0.078203 | 0.01966 | -0.078134 | -0.019633 | 6.9191e-05 | 2.6506e-05 | 0.11678 | 0.11678 | 0.11678 | 0.99664 | -0.023446 | 0.99573 | -0.029804 | 43.2524
14 | -0.088478 | -0.022235 | 0.088612 | 0.022286 | 0.00013342 | 5.1154e-05 | 0.13212 | 0.13212 | 0.13212 | 0.99664 | -0.023446 | 0.99819 | -0.01263 | 48.9342
15 | -0.14076 | -0.035374 | 0.14101 | 0.035469 | 0.0002479 | 9.4872e-05 | 0.20987 | 0.20987 | 0.20987 | 0.99819 | -0.01263 | 1 | 0 | 38.8641
16 | 0.052147 | 0.013088 | -0.052138 | -0.013084 | 9.0818e-06 | 3.4615e-06 | 0.077744 | 0.077744 | 0.077744 | 0.99819 | -0.01263 | 0.99801 | -0.013884 | 28.794
17 | 0.0063874 | 0.0016007 | -0.0063863 | -0.0016006 | 1.1646e-06 | 1.7909e-07 | 0.0095236 | 0.0095237 | 0.0095237 | 0.99801 | -0.013884 | 0.99782 | -0.015202 | 3.5273
18 | 0.045751 | 0.011484 | -0.045685 | -0.011459 | 6.6261e-05 | 2.5187e-05 | 0.06822 | 0.06822 | 0.06822 | 0.99801 | -0.013884 | 0.99652 | -0.02433 | 25.2668
19 | 0.039239 | 0.0098432 | -0.039216 | -0.0098343 | 2.3358e-05 | 8.8419e-06 | 0.058596 | 0.058596 | 0.058596 | 0.99652 | -0.02433 | 0.9959 | -0.028624 | 21.7022
20 | 0.036134 | 0.009062 | -0.036128 | -0.0090597 | 6.0447e-06 | 2.2816e-06 | 0.053992 | 0.053992 | 0.053992 | 0.9959 | -0.028624 | 0.99573 | -0.029831 | 19.9969
21 | 0.020132 | 0.0050472 | -0.020117 | -0.0050419 | 1.46e-05 | 5.2879e-06 | 0.030275 | 0.030275 | 0.030275 | 0.9895 | -0.073625 | 0.98876 | -0.078864 | 11.2131
22 | 0.01104 | 0.002767 | -0.011037 | -0.0027662 | 2.6359e-06 | 8.1671e-07 | 0.016596 | 0.016596 | 0.016596 | 0.98984 | -0.071165 | 0.9896 | -0.07289 | 6.1467
23 | 0.0038938 | 0.00097583 | -0.0038937 | -0.00097585 | 8.8661e-08 | -1.9204e-08 | 0.0058534 | 0.0058534 | 0.0058534 | 0.98984 | -0.071165 | 0.98982 | -0.071329 | 2.1679
24 | -0.0069614 | -0.0017447 | 0.0069638 | 0.0017452 | 2.3334e-06 | 4.5149e-07 | 0.010424 | 0.010424 | 0.010424 | 0.99372 | -0.044028 | 0.99406 | -0.041607 | 3.8608
25 | 0.0083238 | 0.0020861 | -0.0083231 | -0.0020859 | 6.9111e-07 | 1.7334e-07 | 0.01246 | 0.01246 | 0.01246 | 0.99406 | -0.041607 | 0.99397 | -0.042206 | 4.6148
26 | -0.015288 | -0.0038312 | 0.015293 | 0.0038333 | 5.9277e-06 | 2.0446e-06 | 0.022884 | 0.022884 | 0.022884 | 0.99406 | -0.041607 | 0.99446 | -0.038806 | 8.4756
27 | 0.0083231 | 0.0020859 | -0.0083224 | -0.0020857 | 7.1887e-07 | 1.8031e-07 | 0.01246 | 0.01246 | 0.01246 | 0.99397 | -0.042206 | 0.99388 | -0.04283 | 4.6148
28 | -0.02218 | -0.0055592 | 0.022185 | 0.0055612 | 5.5537e-06 | 2.0312e-06 | 0.033188 | 0.033188 | 0.033188 | 0.99446 | -0.038806 | 0.99471 | -0.036998 | 12.2919
29 | 0.0028986 | 0.0007264 | -0.0028985 | -0.00072644 | 5.2477e-08 | -3.7686e-08 | 0.0043397 | 0.0043397 | 0.0043397 | 0.99388 | -0.04283 | 0.99387 | -0.042961 | 1.6073
30 | -0.025657 | -0.0064312 | 0.025664 | 0.0064338 | 7.0096e-06 | 2.597e-06 | 0.038381 | 0.038381 | 0.038381 | 0.99471 | -0.036998 | 0.99499 | -0.035026 | 14.2152
31 | -0.032554 | -0.0081607 | 0.032556 | 0.0081614 | 1.922e-06 | 7.2234e-07 | 0.048685 | 0.048685 | 0.048685 | 0.99499 | -0.035026 | 0.99505 | -0.0346 | 18.0317
32 | -0.036104 | -0.0090507 | 0.036128 | 0.0090597 | 2.386e-05 | 9.0066e-06 | 0.053992 | 0.053992 | 0.053992 | 0.99505 | -0.0346 | 0.99573 | -0.029831 | 19.9969

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15588 | 0.038996

## res_load
| p_mw | q_mvar
0 | 0.0038756 | 0.00097132
1 | 0.00091069 | 0.00022824
2 | 0.0084623 | 0.0021209
3 | 0.0037293 | 0.00093465
4 | 0.0017852 | 0.00044742
5 | 0.00070476 | 0.00017663
6 | 0.010275 | 0.0025751
7 | 0.012974 | 0.0032517
8 | 0.014074 | 0.0035273
9 | 0.0063863 | 0.0016006
10 | 0.0064454 | 0.0016154
11 | 0.0030816 | 0.00077232
12 | 0.010228 | 0.0025634
13 | 0.020117 | 0.0050419
14 | 0.011037 | 0.0027662
15 | 0.0038937 | 0.00097585
16 | 0.0069614 | 0.0017447
17 | 0.0068864 | 0.0017259
18 | 0.0054238 | 0.0013593
19 | 0.0034715 | 0.00087003
20 | 0.0028985 | 0.00072644
21 | 0.0068902 | 0.0017269
22 | 0.0035483 | 0.00088929

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1