## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-2_1_4_node_23 | 0.4 | n |  | TRUE
1 | bus_LV_1631-2_1_4_node_218 | 0.4 | n |  | TRUE
2 | bus_LV_1631-2_1_4_node_239 | 0.4 | n |  | TRUE
3 | bus_LV_1631-2_1_4_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_1631-2_1_4_node_231 | 0.4 | n |  | TRUE
5 | bus_LV_1631-2_1_4_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_1631-2_1_4_node_222 | 0.4 | n |  | TRUE
7 | bus_LV_1631-2_1_4_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1631-2_1_4_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_1631-2_1_4_node_161 | 0.4 | n |  | TRUE
10 | bus_LV_1631-2_1_4_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1631-2_1_4_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_1631-2_1_4_node_166 | 0.4 | n |  | TRUE
13 | bus_LV_1631-2_1_4_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_1631-2_1_4_node_191 | 0.4 | n |  | TRUE
15 | bus_LV_1631-2_1_4_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1631-2_1_4_node_189 | 0.4 | n |  | TRUE
17 | bus_LV_1631-2_1_4_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_1631-2_1_4_node_168 | 0.4 | n |  | TRUE
19 | bus_LV_1631-2_1_4_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1631-2_1_4_node_197 | 0.4 | n |  | TRUE
21 | bus_LV_1631-2_1_4_node_214 | 0.4 | n |  | TRUE
22 | bus_LV_1631-2_1_4_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_1631-2_1_4_node_183 | 0.4 | n |  | TRUE
24 | bus_LV_1631-2_1_4_node_215 | 0.4 | n |  | TRUE
25 | bus_LV_1631-2_1_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_1631-2_1_4_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_1631-2_1_4_node_188 | 0.4 | n |  | TRUE
28 | bus_LV_1631-2_1_4_node_158 | 0.4 | n |  | TRUE
29 | bus_LV_1631-2_1_4_node_198 | 0.4 | n |  | TRUE
30 | bus_LV_1631-2_1_4_node_182 | 0.4 | n |  | TRUE
31 | bus_LV_1631-2_1_4_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_1631-2_1_4_node_172 | 0.4 | n |  | TRUE
33 | bus_LV_1631-2_1_4_node_170 | 0.4 | n |  | TRUE
34 | bus_LV_1631-2_1_4_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_1631-2_1_4_node_236 | 0.4 | n |  | TRUE
36 | bus_LV_1631-2_1_4_node_155 | 0.4 | n |  | TRUE
37 | bus_LV_1631-2_1_4_node_156 | 0.4 | n |  | TRUE
38 | bus_LV_1631-2_1_4_node_157 | 0.4 | n |  | TRUE
39 | bus_LV_1631-2_1_4_node_159 | 0.4 | n |  | TRUE
40 | bus_LV_1631-2_1_4_node_160 | 0.4 | n |  | TRUE
41 | bus_LV_1631-2_1_4_node_190 | 0.4 | n |  | TRUE
42 | bus_LV_1631-2_1_4_node_194 | 0.4 | n |  | TRUE
43 | bus_LV_1631-2_1_4_node_162 | 0.4 | n |  | TRUE
44 | bus_LV_1631-2_1_4_node_163 | 0.4 | n |  | TRUE
45 | bus_LV_1631-2_1_4_node_164 | 0.4 | n |  | TRUE
46 | bus_LV_1631-2_1_4_node_165 | 0.4 | n |  | TRUE
47 | bus_LV_1631-2_1_4_node_167 | 0.4 | n |  | TRUE
48 | bus_LV_1631-2_1_4_node_169 | 0.4 | n |  | TRUE
49 | bus_LV_1631-2_1_4_node_171 | 0.4 | n |  | TRUE
50 | bus_LV_1631-2_1_4_node_195 | 0.4 | n |  | TRUE
51 | bus_LV_1631-2_1_4_node_173 | 0.4 | n |  | TRUE
52 | bus_LV_1631-2_1_4_node_174 | 0.4 | n |  | TRUE
53 | bus_LV_1631-2_1_4_node_175 | 0.4 | n |  | TRUE
54 | bus_LV_1631-2_1_4_node_176 | 0.4 | n |  | TRUE
55 | bus_LV_1631-2_1_4_node_177 | 0.4 | n |  | TRUE
56 | bus_LV_1631-2_1_4_node_179 | 0.4 | n |  | TRUE
57 | bus_LV_1631-2_1_4_node_178 | 0.4 | n |  | TRUE
58 | bus_LV_1631-2_1_4_node_180 | 0.4 | n |  | TRUE
59 | bus_LV_1631-2_1_4_node_181 | 0.4 | n |  | TRUE
60 | bus_LV_1631-2_1_4_node_184 | 0.4 | n |  | TRUE
61 | bus_LV_1631-2_1_4_node_185 | 0.4 | n |  | TRUE
62 | bus_LV_1631-2_1_4_node_187 | 0.4 | n |  | TRUE
63 | bus_LV_1631-2_1_4_node_186 | 0.4 | n |  | TRUE
64 | bus_LV_1631-2_1_4_node_192 | 0.4 | n |  | TRUE
65 | bus_LV_1631-2_1_4_node_193 | 0.4 | n |  | TRUE
66 | bus_LV_1631-2_1_4_node_196 | 0.4 | n |  | TRUE
67 | bus_LV_1631-2_1_4_node_244 | 0.4 | n |  | TRUE
68 | bus_LV_1631-2_1_4_node_202 | 0.4 | n |  | TRUE
69 | bus_LV_1631-2_1_4_node_199 | 0.4 | n |  | TRUE
70 | bus_LV_1631-2_1_4_node_200 | 0.4 | n |  | TRUE
71 | bus_LV_1631-2_1_4_node_243 | 0.4 | n |  | TRUE
72 | bus_LV_1631-2_1_4_node_242 | 0.4 | n |  | TRUE
73 | bus_LV_1631-2_1_4_node_201 | 0.4 | n |  | TRUE
74 | bus_LV_1631-2_1_4_node_203 | 0.4 | n |  | TRUE
75 | bus_LV_1631-2_1_4_node_206 | 0.4 | n |  | TRUE
76 | bus_LV_1631-2_1_4_node_204 | 0.4 | n |  | TRUE
77 | bus_LV_1631-2_1_4_node_232 | 0.4 | n |  | TRUE
78 | bus_LV_1631-2_1_4_node_205 | 0.4 | n |  | TRUE
79 | bus_LV_1631-2_1_4_node_210 | 0.4 | n |  | TRUE
80 | bus_LV_1631-2_1_4_node_207 | 0.4 | n |  | TRUE
81 | bus_LV_1631-2_1_4_node_208 | 0.4 | n |  | TRUE
82 | bus_LV_1631-2_1_4_node_209 | 0.4 | n |  | TRUE
83 | bus_LV_1631-2_1_4_node_211 | 0.4 | n |  | TRUE
84 | bus_LV_1631-2_1_4_node_212 | 0.4 | n |  | TRUE
85 | bus_LV_1631-2_1_4_node_213 | 0.4 | n |  | TRUE
86 | bus_LV_1631-2_1_4_node_216 | 0.4 | n |  | TRUE
87 | bus_LV_1631-2_1_4_node_217 | 0.4 | n |  | TRUE
88 | bus_LV_1631-2_1_4_node_219 | 0.4 | n |  | TRUE
89 | bus_LV_1631-2_1_4_node_240 | 0.4 | n |  | TRUE
90 | bus_LV_1631-2_1_4_node_220 | 0.4 | n |  | TRUE
91 | bus_LV_1631-2_1_4_node_221 | 0.4 | n |  | TRUE
92 | bus_LV_1631-2_1_4_node_223 | 0.4 | n |  | TRUE
93 | bus_LV_1631-2_1_4_node_235 | 0.4 | n |  | TRUE
94 | bus_MV_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-2_1_4_load_239 | 2 | 0.0014781 | 0.00037044 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-2_1_4_load_231 | 4 | 0.0038968 | 0.00097663 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-2_1_4_load_222 | 6 | 0.00046947 | 0.00011766 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-2_1_4_load_161 | 9 | 0.0002312 | 5.7945e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-2_1_4_load_166 | 12 | 0.00058108 | 0.00014563 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-2_1_4_load_191 | 14 | 0.0002234 | 5.599e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-2_1_4_load_189 | 16 | 0.0009316 | 0.00023348 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-2_1_4_load_168 | 18 | 0.001783 | 0.00044685 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-2_1_4_load_214 | 21 | 0.00049945 | 0.00012517 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-2_1_4_load_183 | 23 | 0.000286 | 7.1678e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-2_1_4_load_215 | 24 | 0.0011033 | 0.00027651 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-2_1_4_load_188 | 27 | 0.00020073 | 5.0307e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-2_1_4_load_158 | 28 | 0.00045244 | 0.00011339 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-2_1_4_load_182 | 30 | 0.00023484 | 5.8857e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-2_1_4_load_172 | 32 | 0.00016041 | 4.0203e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-2_1_4_load_170 | 33 | 0.00026665 | 6.683e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-2_1_4_load_56 | 34 | 0.00049209 | 0.00012333 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-2_1_4_load_236 | 35 | 0.00098113 | 0.0002459 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-2_1_4_load_155 | 36 | 0.00034709 | 8.6989e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-2_1_4_load_156 | 37 | 0.00027405 | 6.8684e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-2_1_4_load_160 | 40 | 0.00021891 | 5.4864e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-2_1_4_load_194 | 42 | 0.00027097 | 6.7911e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-2_1_4_load_162 | 43 | 0.00045294 | 0.00011352 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-2_1_4_load_163 | 44 | 0.00019581 | 4.9074e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-2_1_4_load_164 | 45 | 0.00022502 | 5.6395e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-2_1_4_load_165 | 46 | 0.0003696 | 9.2629e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-2_1_4_load_167 | 47 | 0.0013363 | 0.00033492 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-2_1_4_load_169 | 48 | 0.0048271 | 0.0012098 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-2_1_4_load_171 | 49 | 0.00027491 | 6.89e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-2_1_4_load_173 | 51 | 0.00037296 | 9.3473e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-2_1_4_load_174 | 52 | 0.0003542 | 8.8771e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-2_1_4_load_176 | 54 | 0.00019022 | 4.7674e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-2_1_4_load_177 | 55 | 0.00020231 | 5.0703e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-2_1_4_load_179 | 56 | 0.00042192 | 0.00010574 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1631-2_1_4_load_178 | 57 | 0.00026371 | 6.6092e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1631-2_1_4_load_181 | 59 | 0.00028293 | 7.0909e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1631-2_1_4_load_187 | 62 | 0.00017001 | 4.2608e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1631-2_1_4_load_186 | 63 | 0.00015838 | 3.9694e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1631-2_1_4_load_192 | 64 | 0.0005097 | 0.00012774 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1631-2_1_4_load_193 | 65 | 0.00031978 | 8.0144e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1631-2_1_4_load_244 | 67 | 0.0004207 | 0.00010544 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1631-2_1_4_load_200 | 70 | 0.00041953 | 0.00010514 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1631-2_1_4_load_243 | 71 | 0.000467 | 0.00011704 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1631-2_1_4_load_242 | 72 | 0.00029217 | 7.3224e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1631-2_1_4_load_203 | 74 | 0.00030556 | 7.6581e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1631-2_1_4_load_204 | 76 | 0.00017549 | 4.3981e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1631-2_1_4_load_232 | 77 | 0.00035283 | 8.8428e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1631-2_1_4_load_205 | 78 | 0.00047226 | 0.00011836 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1631-2_1_4_load_210 | 79 | 0.00040365 | 0.00010117 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1631-2_1_4_load_207 | 80 | 0.00030919 | 7.749e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1631-2_1_4_load_208 | 81 | 0.00024998 | 6.265e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1631-2_1_4_load_211 | 83 | 0.0044122 | 0.0011058 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1631-2_1_4_load_212 | 84 | 0.00062933 | 0.00015772 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1631-2_1_4_load_213 | 85 | 0.0047487 | 0.0011901 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1631-2_1_4_load_216 | 86 | 0.00026112 | 6.5443e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1631-2_1_4_load_217 | 87 | 0.0013848 | 0.00034707 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1631-2_1_4_load_219 | 88 | 0.0012884 | 0.0003229 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1631-2_1_4_load_240 | 89 | 0.0011654 | 0.00029208 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1631-2_1_4_load_220 | 90 | 0.0011088 | 0.00027788 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1631-2_1_4_load_221 | 91 | 0.0030287 | 0.00075907 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1631-2_1_4_load_223 | 92 | 0.0022998 | 0.00057639 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1631-2_1_4_load_235 | 93 | 0.0010251 | 0.00025691 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-2_1_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.054143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-2_1_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.22944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-2_1_4_line_2 | NAYY 4x150 SE | 1 | 89 | 0.056311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-2_1_4_line_3 | NAYY 4x150 SE | 1 | 5 | 0.17441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-2_1_4_line_4 | NAYY 4x150 SE | 3 | 4 | 0.009163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-2_1_4_line_5 | NAYY 4x150 SE | 3 | 5 | 0.25222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-2_1_4_line_6 | NAYY 4x150 SE | 3 | 6 | 0.0074564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-2_1_4_line_7 | NAYY 4x150 SE | 5 | 24 | 0.13473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-2_1_4_line_8 | NAYY 4x150 SE | 5 | 19 | 0.25734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-2_1_4_line_9 | NAYY 4x150 SE | 6 | 90 | 0.13785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-2_1_4_line_10 | NAYY 4x150 SE | 7 | 8 | 0.10825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-2_1_4_line_11 | NAYY 4x150 SE | 7 | 9 | 0.15272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-2_1_4_line_12 | NAYY 4x150 SE | 8 | 28 | 0.19259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-2_1_4_line_13 | NAYY 4x150 SE | 10 | 11 | 0.29055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-2_1_4_line_14 | NAYY 4x150 SE | 10 | 12 | 0.035251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-2_1_4_line_15 | NAYY 4x150 SE | 11 | 17 | 0.12994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-2_1_4_line_16 | NAYY 4x150 SE | 11 | 18 | 0.020553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-2_1_4_line_17 | NAYY 4x150 SE | 12 | 46 | 0.031506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-2_1_4_line_18 | NAYY 4x150 SE | 13 | 14 | 0.091555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-2_1_4_line_19 | NAYY 4x150 SE | 13 | 15 | 0.61676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-2_1_4_line_20 | NAYY 4x150 SE | 13 | 16 | 0.037816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-2_1_4_line_21 | NAYY 4x150 SE | 15 | 22 | 0.41651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-2_1_4_line_22 | NAYY 4x150 SE | 15 | 23 | 0.06002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-2_1_4_line_23 | NAYY 4x150 SE | 16 | 41 | 0.033756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-2_1_4_line_24 | NAYY 4x150 SE | 17 | 35 | 0.016159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-2_1_4_line_25 | NAYY 4x150 SE | 17 | 31 | 0.15064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-2_1_4_line_26 | NAYY 4x150 SE | 18 | 47 | 0.0055417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-2_1_4_line_27 | NAYY 4x150 SE | 19 | 20 | 0.16715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-2_1_4_line_28 | NAYY 4x150 SE | 19 | 21 | 0.065258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-2_1_4_line_29 | NAYY 4x150 SE | 20 | 68 | 0.046245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-2_1_4_line_30 | NAYY 4x150 SE | 20 | 69 | 0.17983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-2_1_4_line_31 | NAYY 4x150 SE | 20 | 70 | 0.015146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-2_1_4_line_32 | NAYY 4x150 SE | 20 | 50 | 0.13122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-2_1_4_line_33 | NAYY 4x150 SE | 21 | 85 | 0.01518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-2_1_4_line_34 | NAYY 4x150 SE | 22 | 34 | 0.036055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-2_1_4_line_35 | NAYY 4x150 SE | 23 | 60 | 0.010715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-2_1_4_line_36 | NAYY 4x150 SE | 24 | 86 | 0.00046124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-2_1_4_line_37 | NAYY 4x150 SE | 25 | 26 | 0.56039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-2_1_4_line_38 | NAYY 4x150 SE | 25 | 27 | 0.0091756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-2_1_4_line_39 | NAYY 4x150 SE | 26 | 29 | 0.1677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-2_1_4_line_40 | NAYY 4x150 SE | 26 | 30 | 0.068904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-2_1_4_line_41 | NAYY 4x150 SE | 27 | 62 | 0.3187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-2_1_4_line_42 | NAYY 4x150 SE | 28 | 37 | 0.0094926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-2_1_4_line_43 | NAYY 4x150 SE | 29 | 71 | 0.062705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-2_1_4_line_44 | NAYY 4x150 SE | 29 | 66 | 0.066006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-2_1_4_line_45 | NAYY 4x150 SE | 30 | 58 | 0.05083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-2_1_4_line_46 | NAYY 4x150 SE | 31 | 32 | 0.10153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_1631-2_1_4_line_47 | NAYY 4x150 SE | 31 | 33 | 0.059238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1631-2_1_4_line_48 | NAYY 4x150 SE | 32 | 50 | 0.015064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1631-2_1_4_line_49 | NAYY 4x150 SE | 33 | 49 | 0.013508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1631-2_1_4_line_50 | NAYY 4x150 SE | 35 | 93 | 0.0010601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1631-2_1_4_line_51 | NAYY 4x150 SE | 36 | 37 | 0.013157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1631-2_1_4_line_52 | NAYY 4x150 SE | 36 | 38 | 0.014504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1631-2_1_4_line_53 | NAYY 4x150 SE | 38 | 39 | 0.098166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1631-2_1_4_line_54 | NAYY 4x150 SE | 38 | 40 | 0.038257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1631-2_1_4_line_55 | NAYY 4x150 SE | 39 | 41 | 0.04623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1631-2_1_4_line_56 | NAYY 4x150 SE | 39 | 42 | 0.029815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1631-2_1_4_line_57 | NAYY 4x150 SE | 41 | 64 | 0.0042925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1631-2_1_4_line_58 | NAYY 4x150 SE | 43 | 44 | 0.0339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1631-2_1_4_line_59 | NAYY 4x150 SE | 43 | 45 | 0.0057769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1631-2_1_4_line_60 | NAYY 4x150 SE | 44 | 46 | 0.004925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1631-2_1_4_line_61 | NAYY 4x150 SE | 47 | 48 | 0.0039135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1631-2_1_4_line_62 | NAYY 4x150 SE | 50 | 66 | 0.081451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1631-2_1_4_line_63 | NAYY 4x150 SE | 51 | 52 | 0.032161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1631-2_1_4_line_64 | NAYY 4x150 SE | 51 | 53 | 0.090005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1631-2_1_4_line_65 | NAYY 4x150 SE | 52 | 54 | 0.13865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1631-2_1_4_line_66 | NAYY 4x150 SE | 53 | 55 | 0.063146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1631-2_1_4_line_67 | NAYY 4x150 SE | 54 | 56 | 0.14565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1631-2_1_4_line_68 | NAYY 4x150 SE | 56 | 57 | 0.046094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1631-2_1_4_line_69 | NAYY 4x150 SE | 57 | 58 | 0.030281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1631-2_1_4_line_70 | NAYY 4x150 SE | 58 | 59 | 0.01916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1631-2_1_4_line_71 | NAYY 4x150 SE | 60 | 61 | 0.29905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1631-2_1_4_line_72 | NAYY 4x150 SE | 61 | 62 | 0.026857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1631-2_1_4_line_73 | NAYY 4x150 SE | 61 | 63 | 0.059923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1631-2_1_4_line_74 | NAYY 4x150 SE | 64 | 65 | 0.014168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1631-2_1_4_line_75 | NAYY 4x150 SE | 66 | 67 | 0.011268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1631-2_1_4_line_76 | NAYY 4x150 SE | 68 | 75 | 0.029368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1631-2_1_4_line_77 | NAYY 4x150 SE | 68 | 76 | 0.024059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1631-2_1_4_line_78 | NAYY 4x150 SE | 69 | 72 | 0.033889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1631-2_1_4_line_79 | NAYY 4x150 SE | 70 | 73 | 0.10349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1631-2_1_4_line_80 | NAYY 4x150 SE | 73 | 74 | 0.081683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1631-2_1_4_line_81 | NAYY 4x150 SE | 74 | 77 | 9.8831e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1631-2_1_4_line_82 | NAYY 4x150 SE | 75 | 79 | 0.024509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1631-2_1_4_line_83 | NAYY 4x150 SE | 75 | 80 | 0.0077104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1631-2_1_4_line_84 | NAYY 4x150 SE | 76 | 78 | 0.00033533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1631-2_1_4_line_85 | NAYY 4x150 SE | 80 | 81 | 0.013952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1631-2_1_4_line_86 | NAYY 4x150 SE | 81 | 82 | 0.069165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1631-2_1_4_line_87 | NAYY 4x150 SE | 82 | 83 | 0.037896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1631-2_1_4_line_88 | NAYY 4x150 SE | 84 | 85 | 0.0099954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1631-2_1_4_line_89 | NAYY 4x150 SE | 86 | 87 | 0.11723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1631-2_1_4_line_90 | NAYY 4x150 SE | 87 | 88 | 0.020716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1631-2_1_4_line_91 | NAYY 4x150 SE | 90 | 91 | 0.053861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1631-2_1_4_line_92 | NAYY 4x150 SE | 91 | 92 | 0.047347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-2_1_4_trafo_40 | 0.25 MVA 20/0.4 kV | 94 | 31 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61 | x62 | y62 | x63 | y63 | x64 | y64 | x65 | y65 | x66 | y66 | x67 | y67 | x68 | y68 | x69 | y69 | x70 | y70 | x71 | y71 | x72 | y72 | x73 | y73 | x74 | y74 | x75 | y75 | x76 | y76 | x77 | y77 | x78 | y78 | x79 | y79 | x80 | y80 | x81 | y81 | x82 | y82 | x83 | y83 | x84 | y84 | x85 | y85
0 | 2732282.3181 | 1198598.3317 | 2732293.262 | 1198632.8784 | 2732295.7948 | 1198650.6038
1 | 2732282.3181 | 1198598.3317 | 2732293.5452 | 1198596.3563 | 2732321.8892 | 1198595.116 | 2732341.141 | 1198596.799 | 2732363.9693 | 1198599.3508 | 2732371.7331 | 1198599.3116 | 2732383.0125 | 1198597.7268 | 2732399.2014 | 1198595.6504 | 2732408.3515 | 1198597.6768 | 2732422.5995 | 1198605.4874 | 2732430.1442 | 1198610.8587 | 2732433.1102 | 1198614.5272 | 2732434.784 | 1198622.8708 | 2732436.6077 | 1198637.1667 | 2732440.5401 | 1198648.0957 | 2732444.705 | 1198653.6923 | 2732453.3355 | 1198660.6 | 2732461.9328 | 1198669.3417 | 2732465.2467 | 1198676.5541
2 | 2732295.7948 | 1198650.6038 | 2732303.1137 | 1198658.6053 | 2732307.7816 | 1198662.4783 | 2732313.9869 | 1198666.074 | 2732320.594 | 1198667.3434 | 2732326.5101 | 1198667.8303 | 2732330.4091 | 1198667.205 | 2732334.7808 | 1198665.8786 | 2732344.4648 | 1198660.3108
3 | 2732295.7948 | 1198650.6038 | 2732297.7224 | 1198671.5739 | 2732296.9666 | 1198682.6546 | 2732296.0298 | 1198692.6194 | 2732293.9753 | 1198702.148 | 2732288.341 | 1198721.2715 | 2732279.4009 | 1198748.9841 | 2732278.4962 | 1198752.3445 | 2732273.2942 | 1198773.279 | 2732268.3728 | 1198800.8137 | 2732266.6026 | 1198808.1692 | 2732263.5631 | 1198812.6387 | 2732258.3941 | 1198817.9841
4 | 2732270.8651 | 1198971.0456 | 2732267.9955 | 1198962.342
5 | 2732258.3941 | 1198817.9841 | 2732253.4566 | 1198821.4775 | 2732238.0773 | 1198829.6881 | 2732224.4186 | 1198835.1903 | 2732218.7772 | 1198838.4792 | 2732208.8742 | 1198847.4227 | 2732202.5851 | 1198856.9132 | 2732198.5262 | 1198868.8994 | 2732197.7546 | 1198871.4065 | 2732193.7472 | 1198880.0357 | 2732180.7004 | 1198904.0214 | 2732191.588 | 1198901.5269 | 2732208.5323 | 1198897.6319 | 2732219.4194 | 1198894.8149 | 2732230.7431 | 1198895.6772 | 2732239.5364 | 1198900.0418 | 2732247.7494 | 1198907.5626 | 2732252.6593 | 1198916.3225 | 2732255.0501 | 1198923.6033 | 2732267.9955 | 1198962.342
6 | 2732267.9955 | 1198962.342 | 2732273.0855 | 1198956.8931
7 | 2732258.3941 | 1198817.9841 | 2732259.4907 | 1198831.7635 | 2732248.8555 | 1198863.4528 | 2732249.2606 | 1198867.5205 | 2732252.9714 | 1198870.9163 | 2732267.7491 | 1198875.0799 | 2732274.4731 | 1198874.8507 | 2732292.46 | 1198872.7248 | 2732304.5942 | 1198870.0135 | 2732316.6668 | 1198866.6447 | 2732329.7358 | 1198868.504
8 | 2732126.0664 | 1199027.9877 | 2732157.381 | 1198949.1964 | 2732170.0215 | 1198920.4981 | 2732180.7004 | 1198904.0214 | 2732193.7472 | 1198880.0357 | 2732197.7546 | 1198871.4065 | 2732198.5262 | 1198868.8994 | 2732202.5851 | 1198856.9132 | 2732208.8742 | 1198847.4227 | 2732218.7772 | 1198838.4792 | 2732224.4186 | 1198835.1903 | 2732238.0773 | 1198829.6881 | 2732253.4566 | 1198821.4775 | 2732258.3941 | 1198817.9841
9 | 2732405.9201 | 1198952.4099 | 2732405.9201 | 1198952.4099 | 2732400.2515 | 1198950.0491 | 2732390.8522 | 1198950.3523 | 2732380.5236 | 1198945.8423 | 2732371.0765 | 1198943.4868 | 2732361.3874 | 1198942.7717 | 2732350.1165 | 1198944.3456 | 2732341.3366 | 1198943.8509 | 2732319.4597 | 1198944.4893 | 2732284.4319 | 1198948.6951 | 2732277.7956 | 1198951.8507 | 2732273.0855 | 1198956.8931
10 | 2731779.7526 | 1198550.6398 | 2731788.8363 | 1198527.7223 | 2731791.5397 | 1198516.3731 | 2731792.5288 | 1198502.6176 | 2731788.5122 | 1198500.9722 | 2731786.734 | 1198498.6979 | 2731786.0122 | 1198495.1571 | 2731789.4522 | 1198481.5001 | 2731792.1367 | 1198461.6884 | 2731793.9568 | 1198448.5961
11 | 2731793.9568 | 1198448.5961 | 2731784.5619 | 1198462.1328 | 2731767.3271 | 1198497.8139 | 2731746.4497 | 1198532.8587 | 2731742.1274 | 1198543.6941 | 2731729.8354 | 1198567.3638 | 2731728.6234 | 1198575.688 | 2731728.6809 | 1198582.4056 | 2731728.3135 | 1198584.7306
12 | 2731779.7526 | 1198550.6398 | 2731769.1454 | 1198577.7048 | 2731764.1509 | 1198591.0384 | 2731763.0973 | 1198601.501 | 2731762.0212 | 1198622.6604 | 2731758.72 | 1198633.4849 | 2731751.766 | 1198647.587 | 2731747.5231 | 1198659.3137 | 2731744.4022 | 1198685.1093 | 2731741.6575 | 1198693.4998 | 2731732.9728 | 1198703.5273 | 2731723.7285 | 1198710.9516 | 2731713.9111 | 1198726.2049
13 | 2732056.0073 | 1198581.0816 | 2732070.5143 | 1198576.5096 | 2732124.5452 | 1198559.4903 | 2732126.7915 | 1198597.7696 | 2732126.9717 | 1198640.5957 | 2732125.7581 | 1198667.5676 | 2732120.9793 | 1198719.6802 | 2732125.6844 | 1198721.1854 | 2732134.8438 | 1198733.1193 | 2732138.2721 | 1198744.1259 | 2732133.441 | 1198770.3617
14 | 2732056.0073 | 1198581.0816 | 2732037.4215 | 1198594.4147 | 2732029.8547 | 1198600.708 | 2732028.1878 | 1198602.6179
15 | 2732133.441 | 1198770.3617 | 2732126.2294 | 1198809.5105 | 2732105.6826 | 1198804.408 | 2732097.3976 | 1198842.1542 | 2732106.3282 | 1198844.798 | 2732119.3378 | 1198848.6552 | 2732126.4594 | 1198850.7698
16 | 2732133.441 | 1198770.3617 | 2732139.632 | 1198771.4994 | 2732152.3024 | 1198773.8258 | 2732153.6554 | 1198774.0746
17 | 2732020.5989 | 1198632.163 | 2732020.1215 | 1198628.1588 | 2732020.043 | 1198622.7529 | 2732021.1994 | 1198616.6181 | 2732023.0875 | 1198611.1556 | 2732025.6653 | 1198605.5081 | 2732028.1878 | 1198602.6179
18 | 2731626.6601 | 1198943.9829 | 2731627.0326 | 1198934.6839 | 2731626.7521 | 1198914.918 | 2731626.1981 | 1198912.0591 | 2731617.1477 | 1198896.1809 | 2731615.2127 | 1198891.3457 | 2731613.3138 | 1198871.0437 | 2731611.8363 | 1198855.4197
19 | 2731322.0242 | 1199283.4902 | 2731317.8798 | 1199279.0179 | 2731314.1411 | 1199272.7198 | 2731306.241 | 1199253.3646 | 2731301.7981 | 1199247.2178 | 2731291.3451 | 1199235.5347 | 2731285.8422 | 1199230.8324 | 2731280.0285 | 1199227.4466 | 2731275.0468 | 1199223.9789 | 2731269.389 | 1199218.695 | 2731267.1858 | 1199214.966 | 2731269.4136 | 1199208.5655 | 2731274.316 | 1199205.9378 | 2731277.0823 | 1199205.5316 | 2731280.0747 | 1199203.1621 | 2731282.7233 | 1199201.8748 | 2731284.1954 | 1199199.3608 | 2731286.2345 | 1199198.4271 | 2731289.844 | 1199199.863 | 2731296.3877 | 1199197.0712 | 2731300.3534 | 1199194.7788 | 2731306.8121 | 1199189.6167 | 2731310.2589 | 1199188.0578 | 2731314.7582 | 1199189.2131 | 2731332.3857 | 1199196.0946 | 2731336.316 | 1199198.1826 | 2731342.1499 | 1199199.2671 | 2731350.7008 | 1199198.3766 | 2731355.7021 | 1199195.0617 | 2731366.0044 | 1199186.9262 | 2731372.5847 | 1199183.5126 | 2731375.0892 | 1199179.4312 | 2731377.0045 | 1199173.7355 | 2731379.8747 | 1199170.3404 | 2731387.9302 | 1199165.6583 | 2731396.3266 | 1199163.4856 | 2731402.5572 | 1199164.5456 | 2731409.0072 | 1199164.9766 | 2731415.7311 | 1199163.0007 | 2731426.9684 | 1199161.5355 | 2731436.5709 | 1199160.9795 | 2731440.5945 | 1199159.5224 | 2731445.2552 | 1199156.1112 | 2731448.365 | 1199152.9104 | 2731449.7831 | 1199150.4286 | 2731450.2615 | 1199147.0365 | 2731452.8875 | 1199142.6241 | 2731459.9856 | 1199138.8773 | 2731463.0445 | 1199137.9883 | 2731466.037 | 1199135.9637 | 2731468.2929 | 1199133.8339 | 2731471.6042 | 1199129.0919 | 2731473.8437 | 1199124.2485 | 2731474.21 | 1199119.7198 | 2731472.0066 | 1199113.5776 | 2731471.9089 | 1199111.0958 | 2731473.6984 | 1199108.7 | 2731480.529 | 1199100.8441 | 2731483.0595 | 1199098.6981 | 2731491.1245 | 1199093.9385 | 2731503.9202 | 1199084.3236 | 2731505.8221 | 1199084.0875 | 2731507.0684 | 1199085.2603 | 2731509.1077 | 1199088.819 | 2731512.1768 | 1199091.9667 | 2731513.1161 | 1199093.244 | 2731513.6708 | 1199095.0353 | 2731515.061 | 1199101.7823 | 2731531.438 | 1199084.8517 | 2731541.1603 | 1199071.5998 | 2731556.5093 | 1199047.3966 | 2731570.0288 | 1199031.9044 | 2731585.0428 | 1199018.0797 | 2731590.7098 | 1199011.188 | 2731599.3239 | 1198995.6878 | 2731608.7112 | 1198986.9321 | 2731614.2748 | 1198980.2383 | 2731617.6938 | 1198973.3861 | 2731626.6601 | 1198943.9829
20 | 2731626.6601 | 1198943.9829 | 2731634.5026 | 1198938.2734 | 2731643.1918 | 1198929.4023 | 2731646.5615 | 1198924.4394 | 2731650.55 | 1198915.5981
21 | 2731064.4536 | 1199340.9149 | 2731072.9082 | 1199349.2623 | 2731077.5537 | 1199345.4834 | 2731084.0855 | 1199345.3043 | 2731091.9984 | 1199339.1175 | 2731097.9628 | 1199326.9611 | 2731099.0651 | 1199325.6732 | 2731102.9653 | 1199325.314 | 2731105.7732 | 1199325.4424 | 2731109.6198 | 1199326.4831 | 2731111.7668 | 1199326.5302 | 2731115.1173 | 1199325.1916 | 2731120.3769 | 1199326.7526 | 2731124.7823 | 1199325.9375 | 2731126.0668 | 1199326.4105 | 2731137.3596 | 1199334.1976 | 2731140.3345 | 1199339.2111 | 2731141.9988 | 1199340.7711 | 2731143.7963 | 1199340.7772 | 2731146.2985 | 1199339.2198 | 2731147.7902 | 1199337.1954 | 2731147.765 | 1199332.7914 | 2731149.38 | 1199332.4377 | 2731152.1498 | 1199332.5652 | 2731153.1716 | 1199334.945 | 2731160.4189 | 1199342.421 | 2731162.5974 | 1199343.4585 | 2731165.4475 | 1199343.3987 | 2731166.1202 | 1199338.0872 | 2731172.6545 | 1199331.203 | 2731179.1969 | 1199319.7933 | 2731191.7452 | 1199300.9319 | 2731194.843 | 1199288.5569 | 2731192.089 | 1199285.6276 | 2731193.8649 | 1199281.7636 | 2731195.0688 | 1199277.9315 | 2731194.5114 | 1199275.2171 | 2731192.6652 | 1199272.5746 | 2731195.3013 | 1199271.5094 | 2731204.0862 | 1199271.0574 | 2731201.908 | 1199267.5735 | 2731197.8779 | 1199266.2174 | 2731198.8213 | 1199263.1468 | 2731203.3444 | 1199262.8681 | 2731203.8003 | 1199261.5326 | 2731202.6166 | 1199260.2835 | 2731206.5085 | 1199257.8781 | 2731217.2934 | 1199257.5813 | 2731220.9188 | 1199256.9048 | 2731223.2573 | 1199257.9458 | 2731226.0771 | 1199260.6543 | 2731228.2739 | 1199260.1688 | 2731228.1164 | 1199257.9748 | 2731228.8459 | 1199255.9781 | 2731230.0882 | 1199255.2493 | 2731232.7612 | 1199254.5852 | 2731236.2573 | 1199254.5953 | 2731242.7738 | 1199256.8512 | 2731246.3958 | 1199260.4891 | 2731251.3562 | 1199266.6584 | 2731252.9987 | 1199266.094 | 2731261.5699 | 1199258.7321 | 2731267.3121 | 1199258.091 | 2731274.5915 | 1199259.5965 | 2731284.2567 | 1199266.9255 | 2731285.659 | 1199266.8896 | 2731287.1044 | 1199264.8976 | 2731289.2024 | 1199263.7094 | 2731290.0691 | 1199262.0494 | 2731291.1549 | 1199262.2067 | 2731292.2291 | 1199263.5869 | 2731293.3647 | 1199263.5563 | 2731294.0759 | 1199263.0827 | 2731294.6802 | 1199261.9284 | 2731294.173 | 1199257.625 | 2731294.8914 | 1199257.5185 | 2731296.09 | 1199258.4344 | 2731297.6129 | 1199257.7674 | 2731297.7603 | 1199256.2583 | 2731297.2949 | 1199253.8685 | 2731299.6612 | 1199251.9078 | 2731302.1239 | 1199254.9198 | 2731306.241 | 1199253.3646 | 2731314.1411 | 1199272.7198 | 2731317.8798 | 1199279.0179 | 2731322.0242 | 1199283.4902
22 | 2731322.0242 | 1199283.4902 | 2731325.9472 | 1199283.8322 | 2731344.1409 | 1199297.1645 | 2731356.3962 | 1199306.8969 | 2731360.6618 | 1199312.4393 | 2731362.4248 | 1199316.092 | 2731364.7201 | 1199322.5211
23 | 2731660.085 | 1198883.2164 | 2731650.55 | 1198915.5981
24 | 2732126.4594 | 1198850.7698 | 2732131.3909 | 1198835.3814
25 | 2732072.3988 | 1198959.8599 | 2732091.29 | 1198869.9742 | 2732094.8396 | 1198853.7956 | 2732097.3976 | 1198842.1542 | 2732106.3282 | 1198844.798 | 2732119.3378 | 1198848.6552 | 2732126.4594 | 1198850.7698
26 | 2732159.1056 | 1198775.077 | 2732153.6554 | 1198774.0746
27 | 2732058.0889 | 1199179.8591 | 2732064.4014 | 1199171.3475 | 2732071.7885 | 1199144.2118 | 2732082.3192 | 1199116.8455 | 2732097.2731 | 1199082.7049 | 2732126.0664 | 1199027.9877
28 | 2732126.0664 | 1199027.9877 | 2732145.8795 | 1199039.012 | 2732183.0869 | 1199059.7257
29 | 2732058.0889 | 1199179.8591 | 2732064.4014 | 1199171.3475 | 2732073.7784 | 1199159.9792 | 2732078.8964 | 1199154.8549 | 2732083.7439 | 1199152.3156 | 2732089.1648 | 1199152.4355 | 2732091.8706 | 1199153.0513
30 | 2731969.8496 | 1199303.6176 | 2731983.9387 | 1199284.436 | 2731994.2801 | 1199268.3629 | 2732000.1455 | 1199256.9836 | 2732005.962 | 1199243.6795 | 2732012.5746 | 1199226.4121 | 2732016.8547 | 1199213.0074 | 2732020.1264 | 1199201.1148 | 2732025.6049 | 1199175.5382 | 2732026.8025 | 1199169.9492 | 2732037.0532 | 1199172.8111 | 2732054.3261 | 1199178.4749 | 2732058.0889 | 1199179.8591
31 | 2732058.0889 | 1199179.8591 | 2732056.9849 | 1199194.9644
32 | 2732048.425 | 1199073.9633 | 2732037.5463 | 1199122.2494 | 2732032.9344 | 1199142.7301 | 2732026.8025 | 1199169.9492 | 2732037.0532 | 1199172.8111 | 2732054.3261 | 1199178.4749 | 2732058.0889 | 1199179.8591
33 | 2732196.3499 | 1199067.1094 | 2732183.0869 | 1199059.7257
34 | 2731064.4536 | 1199340.9149 | 2731064.5676 | 1199333.6339 | 2731060.112 | 1199328.41 | 2731056.0503 | 1199325.0183 | 2731047.2844 | 1199331.8981 | 2731043.0093 | 1199328.482
35 | 2731368.3227 | 1199332.6122 | 2731364.7201 | 1199322.5211
36 | 2732330.1925 | 1198868.5689 | 2732329.7358 | 1198868.504
37 | 2731647.7094 | 1199278.806 | 2731650.1202 | 1199280.0156 | 2731652.5277 | 1199282.4149 | 2731656.6567 | 1199287.5765 | 2731660.0927 | 1199293.4234 | 2731681.9361 | 1199342.9541 | 2731683.3115 | 1199348.978 | 2731683.4849 | 1199370.4763 | 2731684.514 | 1199376.3146 | 2731686.4037 | 1199383.1949 | 2731689.6722 | 1199390.7616 | 2731694.3195 | 1199399.7043 | 2731695.8625 | 1199405.0313 | 2731695.8628 | 1199409.8573 | 2731690.1936 | 1199427.5683 | 2731689.5047 | 1199432.2123 | 2731690.7048 | 1199435.1299 | 2731692.7728 | 1199436.3431 | 2731696.0406 | 1199436.3373 | 2731698.615 | 1199434.2702 | 2731706.1854 | 1199424.2959 | 2731715.6446 | 1199413.6405 | 2731718.908 | 1199408.3083 | 2731720.2827 | 1199404.6913 | 2731722.5247 | 1199392.1421 | 2731724.5875 | 1199376.6645 | 2731733.6982 | 1199340.7151 | 2731736.4474 | 1199336.25 | 2731749.5251 | 1199323.862 | 2731754.5136 | 1199317.3335 | 2731758.4665 | 1199309.7592 | 2731762.9401 | 1199291.6994 | 2731763.6361 | 1199286.7331 | 2731764.1427 | 1199283.1081 | 2731763.7956 | 1199276.0505 | 2731760.8737 | 1199267.624 | 2731757.7767 | 1199261.6067 | 2731751.2403 | 1199252.6668 | 2731744.8792 | 1199245.0985 | 2731742.65 | 1199241.1796 | 2731741.2032 | 1199235.6323 | 2731741.75 | 1199231.9082 | 2731744.112 | 1199228.4242 | 2731746.067 | 1199227.8557 | 2731747.9075 | 1199227.6406 | 2731755.6798 | 1199229.5912 | 2731764.4085 | 1199232.3857 | 2731772.6875 | 1199234.5032 | 2731778.4163 | 1199235.1633 | 2731783.6984 | 1199235.3577 | 2731791.3414 | 1199233.5026 | 2731798.8529 | 1199229.3205 | 2731814.0512 | 1199216.4679 | 2731825.7659 | 1199201.6591 | 2731827.9943 | 1199195.6036 | 2731828.515 | 1199188.2316 | 2731827.9797 | 1199182.4597 | 2731822.2533 | 1199166.4988 | 2731822.1567 | 1199161.5595 | 2731823.7999 | 1199158.8937 | 2731827.0292 | 1199155.807 | 2731832.092 | 1199154.2063
38 | 2731647.7094 | 1199278.806 | 2731644.7883 | 1199279.6646 | 2731643.067 | 1199281.0388 | 2731642.0389 | 1199284.8303
39 | 2731832.092 | 1199154.2063 | 2731838.1066 | 1199162.2896 | 2731847.4006 | 1199171.2238 | 2731854.965 | 1199178.1071 | 2731866.6543 | 1199186.1934 | 2731872.5046 | 1199188.6022 | 2731877.6618 | 1199189.9725 | 2731882.6548 | 1199189.8048 | 2731885.0278 | 1199189.279 | 2731886.7757 | 1199188.428 | 2731890.2185 | 1199184.9902 | 2731893.3147 | 1199178.9649 | 2731894.8643 | 1199170.8817 | 2731894.86 | 1199163.487 | 2731893.6593 | 1199148.182 | 2731893.4836 | 1199141.3061 | 2731894.0052 | 1199137.3478 | 2731895.7226 | 1199133.0491 | 2731898.9903 | 1199128.5732 | 2731904.1508 | 1199124.2727 | 2731929.1946 | 1199109.892
40 | 2731832.092 | 1199154.2063 | 2731830.9711 | 1199146.3199 | 2731831.9092 | 1199140.7474 | 2731834.0057 | 1199133.766 | 2731837.1382 | 1199126.0958 | 2731847.274 | 1199106.5597 | 2731848.0269 | 1199100.0602 | 2731848.4828 | 1199093.5541 | 2731848.0565 | 1199088.9345
41 | 2731642.0389 | 1199284.8303 | 2731641.6905 | 1199303.7484 | 2731638.4249 | 1199322.6578 | 2731635.676 | 1199330.9148 | 2731630.8556 | 1199342.2618 | 2731630.1708 | 1199348.4516 | 2731630.1674 | 1199354.4784 | 2731628.9642 | 1199356.8871 | 2731626.2146 | 1199358.2609 | 2731623.64 | 1199357.2257 | 2731621.9182 | 1199354.8192 | 2731620.7098 | 1199345.7078 | 2731616.9269 | 1199336.5952 | 2731612.9768 | 1199329.1914 | 2731607.983 | 1199323.8662 | 2731585.9787 | 1199305.8122 | 2731580.6426 | 1199302.1919 | 2731567.9138 | 1199297.7194 | 2731561.7765 | 1199293.1252 | 2731558.3308 | 1199289.4465 | 2731555.079 | 1199287.6847 | 2731552.668 | 1199287.8651 | 2731551.7661 | 1199290.425 | 2731551.5167 | 1199292.4099 | 2731552.5054 | 1199294.2109 | 2731556.0742 | 1199298.8708 | 2731559.8669 | 1199305.4705 | 2731562.5039 | 1199313.0122 | 2731563.8529 | 1199319.2022 | 2731564.2619 | 1199323.8037 | 2731564.3087 | 1199335.5138 | 2731562.0329 | 1199376.2397 | 2731560.8147 | 1199382.7846 | 2731559.4361 | 1199385.2006 | 2731558.0268 | 1199386.5929 | 2731555.7764 | 1199386.7435 | 2731554.1095 | 1199385.9951 | 2731550.8734 | 1199379.719 | 2731547.88 | 1199371.7581 | 2731540.1368 | 1199363.8559
42 | 2731713.9111 | 1198726.2049 | 2731708.7736 | 1198734.1871
43 | 2731929.1946 | 1199109.892 | 2731918.8223 | 1199092.1826 | 2731916.783 | 1199087.256 | 2731915.1864 | 1199080.9048 | 2731915.1586 | 1199072.8534 | 2731916.027 | 1199065.9561 | 2731921.6509 | 1199051.7136
44 | 2731929.1946 | 1199109.892 | 2731938.921 | 1199104.7693 | 2731945.6166 | 1199099.9467 | 2731950.9209 | 1199093.6255 | 2731962.6958 | 1199071.6351 | 2731966.8669 | 1199065.2333 | 2731970.8956 | 1199060.7966
45 | 2731853.8657 | 1199039.4975 | 2731849.2232 | 1199050.6927 | 2731847.2347 | 1199057.265 | 2731846.0055 | 1199066.7119 | 2731848.0565 | 1199088.9345
46 | 2732072.3988 | 1198959.8599 | 2732051.5224 | 1199059.2209
47 | 2732072.3988 | 1198959.8599 | 2732045.8549 | 1198954.5249 | 2732042.1475 | 1198953.7313 | 2732040.0178 | 1198950.8265 | 2732029.8943 | 1198937.3702 | 2732023.2483 | 1198933.0423
48 | 2732048.425 | 1199073.9633 | 2732051.5224 | 1199059.2209
49 | 2732021.4392 | 1198920.1145 | 2732020.9391 | 1198928.61 | 2732022.3629 | 1198931.3992 | 2732023.2483 | 1198933.0423
50 | 2732131.7144 | 1198834.3718 | 2732131.3909 | 1198835.3814
51 | 2731702.2866 | 1198745.6281 | 2731707.3921 | 1198736.3335 | 2731708.7736 | 1198734.1871
52 | 2731696.6771 | 1198758.9817 | 2731700.8683 | 1198748.2101 | 2731702.2866 | 1198745.6281
53 | 2731696.6771 | 1198758.9817 | 2731693.5832 | 1198770.4335 | 2731690.5043 | 1198778.4385 | 2731688.5894 | 1198781.6767 | 2731686.2707 | 1198784.2275 | 2731679.8873 | 1198787.6674 | 2731670.8009 | 1198791.3923 | 2731668.4802 | 1198793.6875 | 2731667.0589 | 1198795.9579 | 2731666.4438 | 1198797.9459 | 2731666.6517 | 1198800.6081 | 2731667.4769 | 1198803.2617 | 2731673.2914 | 1198813.1863 | 2731675.7976 | 1198820.4471 | 2731676.5622 | 1198830.3383 | 2731675.9714 | 1198841.2449
54 | 2731696.6771 | 1198758.9817 | 2731690.5343 | 1198754.9655 | 2731684.5996 | 1198745.305 | 2731681.4232 | 1198725.9843
55 | 2731660.085 | 1198883.2164 | 2731661.6176 | 1198879.0024 | 2731663.8029 | 1198874.9029 | 2731670.3822 | 1198867.064 | 2731672.9162 | 1198862.6942 | 2731674.5186 | 1198858.4262 | 2731675.2738 | 1198854.2284 | 2731675.9714 | 1198841.2449
56 | 2731675.9714 | 1198841.2449 | 2731680.7029 | 1198853.9923 | 2731681.6953 | 1198860.1189 | 2731680.0687 | 1198869.9968
57 | 2731660.085 | 1198883.2164 | 2731661.1272 | 1198887.3804
58 | 2732021.1819 | 1198637.0534 | 2732021.7218 | 1198641.5824 | 2732021.8028 | 1198646.8772 | 2732020.8402 | 1198651.137 | 2732019.041 | 1198653.955 | 2732016.0275 | 1198656.2235 | 2732012.2351 | 1198656.8514 | 2732009.0397 | 1198655.969 | 2732006.4364 | 1198653.4652 | 2732005.2093 | 1198652.1625
59 | 2732001.2483 | 1198647.9574 | 2732005.2093 | 1198652.1625
60 | 2732021.1819 | 1198637.0534 | 2732020.5989 | 1198632.163
61 | 2732162.9546 | 1198775.785 | 2732159.1056 | 1198775.077
62 | 2732048.425 | 1199073.9633 | 2732015.4082 | 1199060.9796 | 2732006.689 | 1199058.0959 | 2731992.7452 | 1199055.8529 | 2731982.414 | 1199056.2807 | 2731976.9289 | 1199057.3382 | 2731970.8956 | 1199060.7966
63 | 2731833.997 | 1198921.212 | 2731829.9471 | 1198923.1575 | 2731809.6225 | 1198941.9304
64 | 2731770.6376 | 1199019.4245 | 2731774.0609 | 1198993.7356 | 2731778.7888 | 1198978.6615 | 2731785.2752 | 1198967.0955 | 2731804.0914 | 1198947.0392 | 2731809.6225 | 1198941.9304
65 | 2731811.9749 | 1199023.3611 | 2731807.0325 | 1199021.573 | 2731802.5282 | 1199017.8819 | 2731796.0837 | 1199004.4183 | 2731796.5403 | 1198997.1894 | 2731800.007 | 1198993.0182 | 2731813.8247 | 1198987.1739 | 2731818.847 | 1198981.5469 | 2731821.2643 | 1198973.8387 | 2731822.7893 | 1198964.7986 | 2731826.5677 | 1198955.8194 | 2731842.9934 | 1198936.0552 | 2731844.1676 | 1198933.935 | 2731844.8805 | 1198930.9707 | 2731845.2344 | 1198928.7434 | 2731845.2395 | 1198926.0971 | 2731844.3321 | 1198923.3749 | 2731842.5197 | 1198921.2778 | 2731839.3791 | 1198920.3411 | 2731833.997 | 1198921.212 | 2731833.997 | 1198921.212
66 | 2731760.3645 | 1199081.1015 | 2731760.4291 | 1199056.0724 | 2731764.195 | 1199038.3305 | 2731770.6376 | 1199019.4245
67 | 2731811.9749 | 1199023.3611 | 2731818.5867 | 1199022.3395 | 2731823.7453 | 1199019.1619 | 2731839.1597 | 1199002.0663 | 2731852.6758 | 1198991.2561 | 2731858.4767 | 1198987.6256 | 2731883.0275 | 1198972.4777 | 2731899.4427 | 1198962.1652 | 2731904.1741 | 1198960.7463 | 2731907.9555 | 1198960.6074 | 2731910.7459 | 1198961.5363 | 2731912.95 | 1198963.4865 | 2731913.9505 | 1198968.2011 | 2731912.7038 | 1198974.6342 | 2731909.5997 | 1198980.3256 | 2731905.9397 | 1198983.7895
68 | 2731905.9397 | 1198983.7895 | 2731884.7887 | 1199003.8075 | 2731873.5294 | 1199016.5076
69 | 2731853.8657 | 1199039.4975 | 2731859.4378 | 1199032.0813 | 2731864.774 | 1199026.3835 | 2731873.5294 | 1199016.5076
70 | 2731853.8657 | 1199039.4975 | 2731854.9919 | 1199043.6923 | 2731853.4479 | 1199058.4252
71 | 2731368.3227 | 1199332.6122 | 2731369.9788 | 1199334.8948 | 2731373.4502 | 1199337.0617 | 2731376.3449 | 1199338.0928 | 2731386.4435 | 1199338.5151 | 2731388.4837 | 1199338.9158 | 2731391.6164 | 1199340.2079 | 2731396.3464 | 1199343.6812 | 2731401.3968 | 1199348.5182 | 2731412.0083 | 1199363.0182 | 2731415.9639 | 1199368.7986 | 2731433.8347 | 1199387.784 | 2731439.2614 | 1199394.2083 | 2731446.4576 | 1199403.6405 | 2731463.2678 | 1199431.3539 | 2731465.2372 | 1199437.0461 | 2731465.6966 | 1199441.4373 | 2731463.7439 | 1199449.1782 | 2731463.6722 | 1199452.4347 | 2731464.8463 | 1199454.8068 | 2731466.3519 | 1199455.963 | 2731469.2125 | 1199455.7702 | 2731472.0543 | 1199454.3539 | 2731476.0682 | 1199448.482 | 2731480.4727 | 1199443.8976 | 2731489.2043 | 1199438.5967 | 2731495.3319 | 1199433.939 | 2731512.0638 | 1199413.9916 | 2731516.5425 | 1199407.7742 | 2731520.2422 | 1199399.9162 | 2731522.4702 | 1199393.8605 | 2731523.0516 | 1199388.2134 | 2731523.2679 | 1199371.4718 | 2731523.4837 | 1199364.0931 | 2731521.8327 | 1199355.7058 | 2731521.1988 | 1199351.9778 | 2731521.6517 | 1199349.7416
72 | 2731521.6517 | 1199349.7416 | 2731523.939 | 1199347.9128 | 2731527.1629 | 1199347.8281 | 2731529.8052 | 1199350.6328 | 2731533.7057 | 1199356.8346 | 2731538.0912 | 1199361.7683 | 2731540.1368 | 1199363.8559
73 | 2731521.6517 | 1199349.7416 | 2731512.5105 | 1199347.3498 | 2731505.9218 | 1199345.2699 | 2731500.2981 | 1199340.8761 | 2731491.3761 | 1199319.1852 | 2731487.0275 | 1199312.5733 | 2731484.7735 | 1199308.0425
74 | 2731664.4474 | 1198901.1501 | 2731664.1737 | 1198899.5524 | 2731661.1272 | 1198887.3804
75 | 2731970.8956 | 1199060.7966 | 2731960.2539 | 1199057.0031
76 | 2732120.5465 | 1199159.7569 | 2732091.8706 | 1199153.0513
77 | 2732091.8706 | 1199153.0513 | 2732094.1173 | 1199159.6172 | 2732095.9448 | 1199176.6384
78 | 2731969.8496 | 1199303.6176 | 2731949.4545 | 1199295.1719 | 2731947.8535 | 1199293.513 | 2731947.5084 | 1199290.8589 | 2731951.9141 | 1199285.552
79 | 2732057.3588 | 1199298.3239 | 2732054.8254 | 1199239.6112 | 2732055.0201 | 1199221.8461 | 2732056.9849 | 1199194.9644
80 | 2732057.3588 | 1199298.3239 | 2732060.5034 | 1199299.0717 | 2732064.1888 | 1199299.1309 | 2732067.3742 | 1199298.3785 | 2732070.0798 | 1199295.903 | 2732071.9133 | 1199286.0136 | 2732075.0477 | 1199264.4884 | 2732079.8337 | 1199241.9878 | 2732083.827 | 1199229.6055
81 | 2732083.8573 | 1199229.5114 | 2732083.827 | 1199229.6055
82 | 2732120.5465 | 1199159.7569 | 2732113.6203 | 1199183.2666
83 | 2732120.5465 | 1199159.7569 | 2732128.0604 | 1199161.4864
84 | 2732095.9806 | 1199176.9718 | 2732095.9448 | 1199176.6384
85 | 2732128.0604 | 1199161.4864 | 2732129.7396 | 1199161.8729 | 2732134.2526 | 1199161.3722 | 2732137.344 | 1199159.7059 | 2732141.0354 | 1199157.7518
86 | 2732204.5969 | 1199162.1615 | 2732172.6389 | 1199147.499 | 2732167.1354 | 1199146.9769 | 2732157.3454 | 1199149.1177 | 2732141.0354 | 1199157.7518
87 | 2732204.5969 | 1199162.1615 | 2732217.798 | 1199156.6492 | 2732228.3218 | 1199151.9895 | 2732237.4095 | 1199147.5093 | 2732239.0659 | 1199146.3228
88 | 2732205.0832 | 1199071.9713 | 2732196.3499 | 1199067.1094
89 | 2732436.8895 | 1198830.0851 | 2732429.9159 | 1198833.1709 | 2732401.8462 | 1198852.3307 | 2732390.577 | 1198858.2857 | 2732379.5782 | 1198863.3795 | 2732356.7722 | 1198870.8692 | 2732347.1257 | 1198870.9779 | 2732330.1925 | 1198868.5689
90 | 2732436.8895 | 1198830.0851 | 2732439.8711 | 1198828.7658 | 2732446.3296 | 1198825.3951 | 2732452.3117 | 1198819.8011 | 2732453.9493 | 1198818.6878
91 | 2732405.9201 | 1198952.4099 | 2732408.6918 | 1198956.2409 | 2732415.8714 | 1198988.7141 | 2732416.1283 | 1198998.772 | 2732417.1288 | 1199004.4986 | 2732417.1288 | 1199004.4986
92 | 2732417.1288 | 1199004.4986 | 2732409.3745 | 1199036.0959 | 2732408.8559 | 1199041.2773 | 2732409.0747 | 1199045.1519 | 2732409.8261 | 1199048.0263 | 2732411.2123 | 1199050.4048

## bus_geodata
| x | y | coords
0 | 2732282.3181 | 1198598.3317
1 | 2732295.7948 | 1198650.6038
2 | 2732465.2467 | 1198676.5541
3 | 2732267.9955 | 1198962.342
4 | 2732270.8651 | 1198971.0456
5 | 2732258.3941 | 1198817.9841
6 | 2732273.0855 | 1198956.8931
7 | 2731793.9568 | 1198448.5961
8 | 2731779.7526 | 1198550.6398
9 | 2731728.3135 | 1198584.7306
10 | 2732056.0073 | 1198581.0816
11 | 2732133.441 | 1198770.3617
12 | 2732028.1878 | 1198602.6179
13 | 2731626.6601 | 1198943.9829
14 | 2731611.8363 | 1198855.4197
15 | 2731322.0242 | 1199283.4902
16 | 2731650.55 | 1198915.5981
17 | 2732126.4594 | 1198850.7698
18 | 2732153.6554 | 1198774.0746
19 | 2732126.0664 | 1199027.9877
20 | 2732058.0889 | 1199179.8591
21 | 2732183.0869 | 1199059.7257
22 | 2731064.4536 | 1199340.9149
23 | 2731364.7201 | 1199322.5211
24 | 2732329.7358 | 1198868.504
25 | 2731647.7094 | 1199278.806
26 | 2731832.092 | 1199154.2063
27 | 2731642.0389 | 1199284.8303
28 | 2731713.9111 | 1198726.2049
29 | 2731929.1946 | 1199109.892
30 | 2731848.0565 | 1199088.9345
31 | 2732072.3988 | 1198959.8599
32 | 2732051.5224 | 1199059.2209
33 | 2732023.2483 | 1198933.0423
34 | 2731043.0093 | 1199328.482
35 | 2732131.3909 | 1198835.3814
36 | 2731702.2866 | 1198745.6281
37 | 2731708.7736 | 1198734.1871
38 | 2731696.6771 | 1198758.9817
39 | 2731675.9714 | 1198841.2449
40 | 2731681.4232 | 1198725.9843
41 | 2731660.085 | 1198883.2164
42 | 2731680.0687 | 1198869.9968
43 | 2732005.2093 | 1198652.1625
44 | 2732021.1819 | 1198637.0534
45 | 2732001.2483 | 1198647.9574
46 | 2732020.5989 | 1198632.163
47 | 2732159.1056 | 1198775.0771
48 | 2732162.9546 | 1198775.785
49 | 2732021.4392 | 1198920.1145
50 | 2732048.425 | 1199073.9633
51 | 2731809.6225 | 1198941.9304
52 | 2731833.997 | 1198921.212
53 | 2731770.6376 | 1199019.4245
54 | 2731811.9749 | 1199023.3611
55 | 2731760.3645 | 1199081.1015
56 | 2731905.9397 | 1198983.7895
57 | 2731873.5294 | 1199016.5076
58 | 2731853.8657 | 1199039.4975
59 | 2731853.4479 | 1199058.4252
60 | 2731368.3227 | 1199332.6122
61 | 2731521.6517 | 1199349.7416
62 | 2731540.1368 | 1199363.8559
63 | 2731484.7735 | 1199308.0425
64 | 2731661.1272 | 1198887.3804
65 | 2731664.4474 | 1198901.1501
66 | 2731970.8956 | 1199060.7966
67 | 2731960.2539 | 1199057.0031
68 | 2732091.8706 | 1199153.0513
69 | 2731969.8496 | 1199303.6176
70 | 2732056.9849 | 1199194.9644
71 | 2731921.6509 | 1199051.7136
72 | 2731951.9141 | 1199285.552
73 | 2732057.3588 | 1199298.3239
74 | 2732083.827 | 1199229.6055
75 | 2732120.5465 | 1199159.7569
76 | 2732095.9448 | 1199176.6384
77 | 2732083.8573 | 1199229.5114
78 | 2732095.9806 | 1199176.9718
79 | 2732113.6203 | 1199183.2666
80 | 2732128.0604 | 1199161.4864
81 | 2732141.0354 | 1199157.7518
82 | 2732204.5969 | 1199162.1615
83 | 2732239.0659 | 1199146.3228
84 | 2732205.0832 | 1199071.9713
85 | 2732196.3499 | 1199067.1094
86 | 2732330.1925 | 1198868.5689
87 | 2732436.8895 | 1198830.0851
88 | 2732453.9493 | 1198818.6878
89 | 2732344.4648 | 1198660.3108
90 | 2732405.9201 | 1198952.4099
91 | 2732417.1288 | 1199004.4986
92 | 2732411.2123 | 1199050.4048
93 | 2732131.7144 | 1198834.3718
94 | 2732072.3988 | 1198959.8599

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97732 | -0.16037 | 0 | 0
1 | 0.97744 | -0.15952 | 0 | 0
2 | 0.97683 | -0.16394 | 0.0014781 | 0.00037044
3 | 0.97412 | -0.18327 | 0 | 0
4 | 0.97407 | -0.18365 | 0.0038968 | 0.00097663
5 | 0.97811 | -0.15464 | 0 | 0
6 | 0.97404 | -0.18382 | 0.00046947 | 0.00011766
7 | 0.97947 | -0.15022 | 0 | 0
8 | 0.97951 | -0.14994 | 0 | 0
9 | 0.97942 | -0.1506 | 0.0002312 | 5.7945e-05
10 | 0.99488 | -0.036083 | 0 | 0
11 | 0.99564 | -0.030669 | 0 | 0
12 | 0.99479 | -0.036734 | 0.00058108 | 0.00014563
13 | 0.98029 | -0.14412 | 0 | 0
14 | 0.98026 | -0.14434 | 0.0002234 | 5.599e-05
15 | 0.98368 | -0.11928 | 0 | 0
16 | 0.98009 | -0.14555 | 0.0009316 | 0.00023348
17 | 0.99746 | -0.017847 | 0 | 0
18 | 0.99541 | -0.032314 | 0.001783 | 0.00044685
19 | 0.98469 | -0.10766 | 0 | 0
20 | 0.99039 | -0.067418 | 0 | 0
21 | 0.98413 | -0.11161 | 0.00049945 | 0.00012517
22 | 0.98338 | -0.1215 | 0 | 0
23 | 0.98405 | -0.11652 | 0.000286 | 7.1678e-05
24 | 0.97732 | -0.16034 | 0.0011033 | 0.00027651
25 | 0.9886 | -0.08276 | 0 | 0
26 | 0.99274 | -0.052146 | 0 | 0
27 | 0.98854 | -0.083261 | 0.00020073 | 5.0307e-05
28 | 0.97957 | -0.14941 | 0.00045244 | 0.00011339
29 | 0.99453 | -0.03893 | 0 | 0
30 | 0.99251 | -0.053811 | 0.00023484 | 5.8857e-05
31 | 1 | 0 | -0.053111 | -0.013113
32 | 0.99711 | -0.020267 | 0.00016041 | 4.0203e-05
33 | 0.99995 | -0.00032269 | 0.00026665 | 6.683e-05
34 | 0.98335 | -0.12168 | 0.00049209 | 0.00012333
35 | 0.99741 | -0.018173 | 0.00098113 | 0.0002459
36 | 0.9796 | -0.1492 | 0.00034709 | 8.6989e-05
37 | 0.97958 | -0.14934 | 0.00027405 | 6.8684e-05
38 | 0.97963 | -0.149 | 0 | 0
39 | 0.97985 | -0.14739 | 0 | 0
40 | 0.97962 | -0.14909 | 0.00021891 | 5.4864e-05
41 | 0.97997 | -0.14649 | 0 | 0
42 | 0.97983 | -0.14747 | 0.00027097 | 6.7911e-05
43 | 0.9947 | -0.037407 | 0.00045294 | 0.00011352
44 | 0.99473 | -0.037175 | 0.00019581 | 4.9074e-05
45 | 0.99469 | -0.037421 | 0.00022502 | 5.6395e-05
46 | 0.99474 | -0.037131 | 0.0003696 | 9.2629e-05
47 | 0.99536 | -0.032658 | 0.0013363 | 0.00033492
48 | 0.99533 | -0.032848 | 0.0048271 | 0.0012098
49 | 0.99995 | -0.00035985 | 0.00027491 | 6.89e-05
50 | 0.99626 | -0.026278 | 0 | 0
51 | 0.99173 | -0.059473 | 0.00037296 | 9.3473e-05
52 | 0.99175 | -0.05928 | 0.0003542 | 8.8771e-05
53 | 0.9917 | -0.059668 | 0 | 0
54 | 0.99194 | -0.057938 | 0.00019022 | 4.7674e-05
55 | 0.99168 | -0.059799 | 0.00020231 | 5.0703e-05
56 | 0.99217 | -0.056228 | 0.00042192 | 0.00010574
57 | 0.99227 | -0.055486 | 0.00026371 | 6.6092e-05
58 | 0.99235 | -0.054916 | 0 | 0
59 | 0.99235 | -0.054971 | 0.00028293 | 7.0909e-05
60 | 0.98412 | -0.116 | 0 | 0
61 | 0.9861 | -0.10135 | 0 | 0
62 | 0.98628 | -0.099992 | 0.00017001 | 4.2608e-05
63 | 0.98608 | -0.10145 | 0.00015838 | 3.9694e-05
64 | 0.97996 | -0.14653 | 0.0005097 | 0.00012774
65 | 0.97995 | -0.14658 | 0.00031978 | 8.0144e-05
66 | 0.99528 | -0.033419 | 0 | 0
67 | 0.99527 | -0.033466 | 0.0004207 | 0.00010544
68 | 0.98999 | -0.070264 | 0 | 0
69 | 0.99031 | -0.067975 | 0 | 0
70 | 0.99036 | -0.067587 | 0.00041953 | 0.00010514
71 | 0.99449 | -0.039227 | 0.000467 | 0.00011704
72 | 0.9903 | -0.068076 | 0.00029217 | 7.3224e-05
73 | 0.99026 | -0.068294 | 0 | 0
74 | 0.99019 | -0.068845 | 0.00030556 | 7.6581e-05
75 | 0.98976 | -0.071876 | 0 | 0
76 | 0.98996 | -0.070423 | 0.00017549 | 4.3981e-05
77 | 0.99019 | -0.068845 | 0.00035283 | 8.8428e-05
78 | 0.98996 | -0.070424 | 0.00047226 | 0.00011836
79 | 0.98974 | -0.071977 | 0.00040365 | 0.00010117
80 | 0.9897 | -0.072268 | 0.00030919 | 7.749e-05
81 | 0.98961 | -0.072932 | 0.00024998 | 6.265e-05
82 | 0.98917 | -0.076048 | 0 | 0
83 | 0.98893 | -0.077755 | 0.0044122 | 0.0011058
84 | 0.98401 | -0.11252 | 0.00062933 | 0.00015772
85 | 0.98402 | -0.11245 | 0.0047487 | 0.0011901
86 | 0.97732 | -0.16036 | 0.00026112 | 6.5443e-05
87 | 0.97686 | -0.16364 | 0.0013848 | 0.00034707
88 | 0.97682 | -0.16392 | 0.0012884 | 0.0003229
89 | 0.97734 | -0.16021 | 0.0011654 | 0.00029208
90 | 0.97274 | -0.19319 | 0.0011088 | 0.00027788
91 | 0.97232 | -0.19622 | 0.0030287 | 0.00075907
92 | 0.97216 | -0.19737 | 0.0022998 | 0.00057639
93 | 0.99741 | -0.018184 | 0.0010251 | 0.00025691
94 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0014788 | -0.00036785 | 0.001479 | 0.00036724 | 1.711e-07 | -6.1274e-07 | 0.0022506 | 0.0022503 | 0.0022506 | 0.97732 | -0.16037 | 0.97744 | -0.15952 | 0.83354
1 | 0.0014788 | 0.00036785 | -0.0014781 | -0.00037044 | 7.2549e-07 | -2.5946e-06 | 0.0022506 | 0.0022516 | 0.0022516 | 0.97732 | -0.16037 | 0.97683 | -0.16394 | 0.83392
2 | 0.0011655 | 0.00029141 | -0.0011654 | -0.00029208 | 1.1061e-07 | -6.6319e-07 | 0.0017741 | 0.0017743 | 0.0017743 | 0.97744 | -0.15952 | 0.97734 | -0.16021 | 0.65716
3 | -0.0026445 | -0.00065865 | 0.0026463 | 0.00065714 | 1.7623e-06 | -1.5097e-06 | 0.0040244 | 0.0040236 | 0.0040244 | 0.97744 | -0.15952 | 0.97811 | -0.15464 | 1.4905
4 | 0.003897 | 0.0009766 | -0.0038968 | -0.00097663 | 2.0262e-07 | -3.6135e-08 | 0.0059528 | 0.0059529 | 0.0059529 | 0.97412 | -0.18327 | 0.97407 | -0.18365 | 2.2048
5 | -0.010815 | -0.0027089 | 0.010858 | 0.0027223 | 4.2951e-05 | 1.3367e-05 | 0.01652 | 0.016519 | 0.01652 | 0.97412 | -0.18327 | 0.97811 | -0.15464 | 6.1186
6 | 0.0069183 | 0.0017324 | -0.0069177 | -0.0017322 | 5.1958e-07 | 1.0702e-07 | 0.010567 | 0.010567 | 0.010567 | 0.97412 | -0.18327 | 0.97404 | -0.18382 | 3.9139
7 | 0.0040421 | 0.0010102 | -0.0040389 | -0.0010107 | 3.1783e-06 | -4.6723e-07 | 0.0061483 | 0.0061489 | 0.0061489 | 0.97811 | -0.15464 | 0.97732 | -0.16034 | 2.2774
8 | -0.017547 | -0.0043897 | 0.017661 | 0.0044304 | 0.0001144 | 4.0746e-05 | 0.026691 | 0.02669 | 0.026691 | 0.97811 | -0.15464 | 0.98469 | -0.10766 | 9.8856
9 | 0.0064483 | 0.0016146 | -0.0064399 | -0.0016131 | 8.347e-06 | 1.4968e-06 | 0.0098503 | 0.0098509 | 0.0098509 | 0.97404 | -0.18382 | 0.97274 | -0.19319 | 3.6485
10 | -0.00023122 | -5.6028e-05 | 0.00023122 | 5.4669e-05 | 8.2909e-09 | -1.3593e-06 | 0.00035059 | 0.00035012 | 0.00035059 | 0.97947 | -0.15022 | 0.97951 | -0.14994 | 0.12985
11 | 0.00023122 | 5.6028e-05 | -0.0002312 | -5.7945e-05 | 1.1735e-08 | -1.9175e-06 | 0.00035059 | 0.00035126 | 0.00035126 | 0.97947 | -0.15022 | 0.97942 | -0.1506 | 0.1301
12 | -0.00023122 | -5.4669e-05 | 0.00023124 | 5.225e-05 | 1.4698e-08 | -2.4187e-06 | 0.00035012 | 0.00034931 | 0.00035012 | 0.97951 | -0.14994 | 0.97957 | -0.14941 | 0.12967
13 | -0.0018247 | -0.0004559 | 0.0018261 | 0.00045265 | 1.3492e-06 | -3.2568e-06 | 0.0027287 | 0.0027273 | 0.0027287 | 0.99488 | -0.036083 | 0.99564 | -0.030669 | 1.0106
14 | 0.0018247 | 0.0004559 | -0.0018245 | -0.0004563 | 1.6379e-07 | -3.9471e-07 | 0.0027287 | 0.0027288 | 0.0027288 | 0.99488 | -0.036083 | 0.99479 | -0.036734 | 1.0107
15 | -0.0097747 | -0.0024447 | 0.009792 | 0.0024496 | 1.7298e-05 | 4.9602e-06 | 0.014607 | 0.014606 | 0.014607 | 0.99564 | -0.030669 | 0.99746 | -0.017847 | 5.4099
16 | 0.0079486 | 0.001992 | -0.0079468 | -0.0019916 | 1.8098e-06 | 4.2887e-07 | 0.011879 | 0.011879 | 0.011879 | 0.99564 | -0.030669 | 0.99541 | -0.032314 | 4.3998
17 | 0.0012435 | 0.00031067 | -0.0012434 | -0.00031105 | 6.7993e-08 | -3.8286e-07 | 0.0018596 | 0.0018598 | 0.0018598 | 0.99479 | -0.036734 | 0.99474 | -0.037131 | 0.68881
18 | 0.00022341 | 5.4838e-05 | -0.0002234 | -5.599e-05 | 6.5622e-09 | -1.1517e-06 | 0.00033871 | 0.00033912 | 0.00033912 | 0.98029 | -0.14412 | 0.98026 | -0.14434 | 0.1256
19 | -0.0037808 | -0.00093665 | 0.0037935 | 0.00093371 | 1.2653e-05 | -2.9361e-06 | 0.0057352 | 0.0057324 | 0.0057352 | 0.98029 | -0.14412 | 0.98368 | -0.11928 | 2.1241
20 | 0.0035574 | 0.00088181 | -0.0035567 | -0.00088202 | 6.8722e-07 | -2.1235e-07 | 0.0053965 | 0.0053966 | 0.0053966 | 0.98029 | -0.14412 | 0.98009 | -0.14555 | 1.9987
21 | 0.00049224 | 0.00011765 | -0.0004921 | -0.00012288 | 1.4369e-07 | -5.2305e-06 | 0.00074262 | 0.00074446 | 0.00074446 | 0.98368 | -0.11928 | 0.98338 | -0.1215 | 0.27573
22 | -0.0042857 | -0.0010514 | 0.0042873 | 0.0010512 | 1.5702e-06 | -1.583e-07 | 0.006475 | 0.0064748 | 0.006475 | 0.98368 | -0.11928 | 0.98405 | -0.11652 | 2.3982
23 | 0.0026251 | 0.00064854 | -0.0026248 | -0.00064884 | 3.3405e-07 | -2.9687e-07 | 0.0039822 | 0.0039824 | 0.0039824 | 0.98009 | -0.14555 | 0.97997 | -0.14649 | 1.475
24 | 0.0020063 | 0.00050262 | -0.0020062 | -0.00050279 | 9.0327e-08 | -1.7617e-07 | 0.0029929 | 0.002993 | 0.002993 | 0.99746 | -0.017847 | 0.99741 | -0.018173 | 1.1085
25 | -0.011798 | -0.0029522 | 0.011827 | 0.0029615 | 2.9114e-05 | 9.2263e-06 | 0.017599 | 0.017598 | 0.017599 | 0.99746 | -0.017847 | 1 | 0 | 6.5182
26 | 0.0061638 | 0.0015447 | -0.0061635 | -0.0015447 | 2.9359e-07 | 4.0885e-08 | 0.0092142 | 0.0092142 | 0.0092142 | 0.99541 | -0.032314 | 0.99536 | -0.032658 | 3.4127
27 | -0.023542 | -0.0059038 | 0.023674 | 0.0059524 | 0.00013201 | 4.8635e-05 | 0.035577 | 0.035576 | 0.035577 | 0.98469 | -0.10766 | 0.99039 | -0.067418 | 13.1767
28 | 0.0058813 | 0.0014734 | -0.0058781 | -0.001473 | 3.2165e-06 | 4.0744e-07 | 0.0088873 | 0.0088876 | 0.0088876 | 0.98469 | -0.10766 | 0.98413 | -0.11161 | 3.2917
29 | 0.00603 | 0.001509 | -0.0060276 | -0.0015086 | 2.3682e-06 | 3.1599e-07 | 0.009059 | 0.0090592 | 0.0090592 | 0.99039 | -0.067418 | 0.98999 | -0.070264 | 3.3552
30 | 0.00029219 | 7.0484e-05 | -0.00029217 | -7.279e-05 | 2.1572e-08 | -2.3057e-06 | 0.00043805 | 0.00043886 | 0.00043886 | 0.99039 | -0.067418 | 0.99031 | -0.067975 | 0.16254
31 | 0.0010781 | 0.00026763 | -0.001078 | -0.00026781 | 2.4769e-08 | -1.8537e-07 | 0.0016188 | 0.0016189 | 0.0016189 | 0.99039 | -0.067418 | 0.99036 | -0.067587 | 0.5996
32 | -0.031074 | -0.0077995 | 0.031253 | 0.0078664 | 0.00017851 | 6.6961e-05 | 0.046692 | 0.046692 | 0.046692 | 0.99039 | -0.067418 | 0.99626 | -0.026278 | 17.2934
33 | 0.0053787 | 0.0013478 | -0.005378 | -0.0013477 | 6.2647e-07 | 4.8093e-08 | 0.0081325 | 0.0081325 | 0.0081325 | 0.98413 | -0.11161 | 0.98402 | -0.11245 | 3.0121
34 | 0.0004921 | 0.00012288 | -0.00049209 | -0.00012333 | 1.2472e-08 | -4.5261e-07 | 0.00074446 | 0.00074463 | 0.00074463 | 0.98338 | -0.1215 | 0.98335 | -0.12168 | 0.27579
35 | -0.0045733 | -0.0011229 | 0.0045736 | 0.0011229 | 3.1899e-07 | -1.3445e-08 | 0.0069072 | 0.0069072 | 0.0069072 | 0.98405 | -0.11652 | 0.98412 | -0.116 | 2.5582
36 | 0.0029356 | 0.00073417 | -0.0029356 | -0.00073417 | 5.7482e-09 | -3.5688e-09 | 0.004469 | 0.004469 | 0.004469 | 0.97732 | -0.16034 | 0.97732 | -0.16036 | 1.6552
37 | -0.0051237 | -0.0012544 | 0.0051445 | 0.0012552 | 2.0735e-05 | 7.5952e-07 | 0.0077016 | 0.0076991 | 0.0077016 | 0.9886 | -0.08276 | 0.99274 | -0.052146 | 2.8525
38 | 0.0051237 | 0.0012544 | -0.0051234 | -0.0012544 | 3.3961e-07 | 1.2979e-08 | 0.0077016 | 0.0077017 | 0.0077017 | 0.9886 | -0.08276 | 0.98854 | -0.083261 | 2.8525
39 | -0.0074691 | -0.0018292 | 0.0074822 | 0.001832 | 1.308e-05 | 2.8586e-06 | 0.011181 | 0.01118 | 0.011181 | 0.99274 | -0.052146 | 0.99453 | -0.03893 | 4.1409
40 | 0.0023247 | 0.00057398 | -0.0023241 | -0.00057467 | 5.2117e-07 | -6.9023e-07 | 0.0034814 | 0.0034817 | 0.0034817 | 0.99274 | -0.052146 | 0.99251 | -0.053811 | 1.2895
41 | 0.0049226 | 0.0012041 | -0.0049118 | -0.001204 | 1.0891e-05 | 1.1225e-07 | 0.0073995 | 0.0074009 | 0.0074009 | 0.98854 | -0.083261 | 0.98628 | -0.099992 | 2.7411
42 | -0.00068368 | -0.00016564 | 0.00068368 | 0.00016552 | 6.3637e-09 | -1.1705e-07 | 0.0010365 | 0.0010365 | 0.0010365 | 0.97957 | -0.14941 | 0.97958 | -0.14934 | 0.3839
43 | 0.00046702 | 0.00011624 | -0.000467 | -0.00011704 | 1.9097e-08 | -8.0629e-07 | 0.00069848 | 0.00069876 | 0.00069876 | 0.99453 | -0.03893 | 0.99449 | -0.039227 | 0.2588
44 | -0.0079492 | -0.0019483 | 0.007955 | 0.0019497 | 5.8112e-06 | 1.3779e-06 | 0.011878 | 0.011878 | 0.011878 | 0.99453 | -0.03893 | 0.99528 | -0.033419 | 4.3994
45 | 0.0020893 | 0.00051582 | -0.002089 | -0.00051635 | 3.1069e-07 | -5.373e-07 | 0.0031296 | 0.0031299 | 0.0031299 | 0.99251 | -0.053811 | 0.99235 | -0.054916 | 1.1592
46 | 0.039942 | 0.010016 | -0.03983 | -0.0099761 | 0.00011191 | 4.0385e-05 | 0.059436 | 0.059437 | 0.059437 | 1 | 0 | 0.99711 | -0.020267 | 11.0069
47 | 0.00054159 | 0.00013479 | -0.00054157 | -0.00013555 | 2.3996e-08 | -7.679e-07 | 0.00080557 | 0.00080584 | 0.00080584 | 1 | 0 | 0.99995 | -0.00032269 | 0.29846
48 | 0.03967 | 0.0099359 | -0.039637 | -0.0099234 | 3.2942e-05 | 1.2474e-05 | 0.059198 | 0.059198 | 0.059198 | 0.99711 | -0.020267 | 0.99626 | -0.026278 | 21.9252
49 | 0.00027492 | 6.8723e-05 | -0.00027491 | -6.89e-05 | 1.4105e-09 | -1.7666e-07 | 0.00040904 | 0.0004091 | 0.0004091 | 0.99995 | -0.00032269 | 0.99995 | -0.00035985 | 0.15152
50 | 0.0010251 | 0.0002569 | -0.0010251 | -0.00025691 | 1.5472e-09 | -1.3242e-08 | 0.0015293 | 0.0015293 | 0.0015293 | 0.99741 | -0.018173 | 0.99741 | -0.018184 | 0.56641
51 | 0.00095775 | 0.00023405 | -0.00095774 | -0.00023421 | 1.7327e-08 | -1.5897e-07 | 0.0014527 | 0.0014528 | 0.0014528 | 0.9796 | -0.1492 | 0.97958 | -0.14934 | 0.53806
52 | -0.0013048 | -0.00032104 | 0.0013049 | 0.00032087 | 3.5478e-08 | -1.6896e-07 | 0.0019799 | 0.0019799 | 0.0019799 | 0.9796 | -0.1492 | 0.97963 | -0.149 | 0.73331
53 | -0.0015238 | -0.00037525 | 0.0015241 | 0.00037414 | 3.2743e-07 | -1.1103e-06 | 0.0023122 | 0.0023118 | 0.0023122 | 0.97963 | -0.149 | 0.97985 | -0.14739 | 0.85638
54 | 0.00021891 | 5.4383e-05 | -0.00021891 | -5.4864e-05 | 2.6381e-09 | -4.8064e-07 | 0.00033235 | 0.00033252 | 0.00033252 | 0.97963 | -0.149 | 0.97962 | -0.14909 | 0.12315
55 | -0.0017951 | -0.00044168 | 0.0017953 | 0.00044118 | 2.139e-07 | -5.001e-07 | 0.0027232 | 0.0027229 | 0.0027232 | 0.97985 | -0.14739 | 0.97997 | -0.14649 | 1.0086
56 | 0.00027097 | 6.7537e-05 | -0.00027097 | -6.7911e-05 | 3.1494e-09 | -3.7432e-07 | 0.00041137 | 0.00041151 | 0.00041151 | 0.97985 | -0.14739 | 0.97983 | -0.14747 | 0.15241
57 | 0.00082949 | 0.00020766 | -0.00082948 | -0.00020771 | 4.2487e-09 | -5.2447e-08 | 0.0012594 | 0.0012595 | 0.0012595 | 0.97997 | -0.14649 | 0.97996 | -0.14653 | 0.46647
58 | -0.00067796 | -0.00016984 | 0.00067799 | 0.00016941 | 2.1754e-08 | -4.3168e-07 | 0.0010142 | 0.001014 | 0.0010142 | 0.9947 | -0.037407 | 0.99473 | -0.037175 | 0.37562
59 | 0.00022502 | 5.632e-05 | -0.00022502 | -5.6395e-05 | 4.0843e-10 | -7.4829e-08 | 0.00033659 | 0.00033662 | 0.00033662 | 0.9947 | -0.037407 | 0.99469 | -0.037421 | 0.12467
60 | -0.00087379 | -0.00021848 | 0.0008738 | 0.00021842 | 5.2491e-09 | -6.1915e-08 | 0.0013069 | 0.0013069 | 0.0013069 | 0.99473 | -0.037175 | 0.99474 | -0.037131 | 0.48405
61 | 0.0048272 | 0.0012098 | -0.0048271 | -0.0012098 | 1.2717e-07 | -1.953e-09 | 0.0072164 | 0.0072164 | 0.0072164 | 0.99536 | -0.032658 | 0.99533 | -0.032848 | 2.6728
62 | 0.0083837 | 0.0020569 | -0.0083757 | -0.0020549 | 7.95e-06 | 1.9981e-06 | 0.012507 | 0.012507 | 0.012507 | 0.99626 | -0.026278 | 0.99528 | -0.033419 | 4.6322
63 | -0.00057528 | -0.0001422 | 0.00057529 | 0.00014179 | 1.4925e-08 | -4.0925e-07 | 0.00086247 | 0.00086232 | 0.00086247 | 0.99173 | -0.059473 | 0.99175 | -0.05928 | 0.31943
64 | 0.00020232 | 4.873e-05 | -0.00020231 | -4.989e-05 | 5.1588e-09 | -1.1593e-06 | 0.00030287 | 0.00030327 | 0.00030327 | 0.99173 | -0.059473 | 0.9917 | -0.059668 | 0.11232
65 | -0.00092949 | -0.00023056 | 0.00092966 | 0.00022884 | 1.6799e-07 | -1.7248e-06 | 0.0013938 | 0.0013931 | 0.0013938 | 0.99175 | -0.05928 | 0.99194 | -0.057938 | 0.51621
66 | 0.00020231 | 4.989e-05 | -0.00020231 | -5.0703e-05 | 3.6275e-09 | -8.1333e-07 | 0.00030327 | 0.00030356 | 0.00030356 | 0.9917 | -0.059668 | 0.99168 | -0.059799 | 0.11243
67 | -0.0011199 | -0.00027651 | 0.0011201 | 0.00027473 | 2.5596e-07 | -1.7822e-06 | 0.0016785 | 0.0016778 | 0.0016785 | 0.99194 | -0.057938 | 0.99217 | -0.056228 | 0.62166
68 | -0.0015421 | -0.00038047 | 0.0015422 | 0.00037994 | 1.5355e-07 | -5.363e-07 | 0.0023106 | 0.0023104 | 0.0023106 | 0.99217 | -0.056228 | 0.99227 | -0.055486 | 0.85578
69 | -0.0018059 | -0.00044603 | 0.0018061 | 0.00044569 | 1.3834e-07 | -3.3797e-07 | 0.0027058 | 0.0027057 | 0.0027058 | 0.99227 | -0.055486 | 0.99235 | -0.054916 | 1.0022
70 | 0.00028293 | 7.0663e-05 | -0.00028293 | -7.0909e-05 | 2.1515e-09 | -2.4671e-07 | 0.00042417 | 0.00042425 | 0.00042425 | 0.99235 | -0.054916 | 0.99235 | -0.054971 | 0.15713
71 | -0.0045736 | -0.0011229 | 0.0045825 | 0.0011225 | 8.9012e-06 | -3.8383e-07 | 0.0069072 | 0.0069058 | 0.0069072 | 0.98412 | -0.116 | 0.9861 | -0.10135 | 2.5582
72 | -0.0047409 | -0.0011614 | 0.0047418 | 0.0011614 | 8.5544e-07 | -1.3665e-08 | 0.0071446 | 0.0071445 | 0.0071446 | 0.9861 | -0.10135 | 0.98628 | -0.099992 | 2.6461
73 | 0.00015838 | 3.8931e-05 | -0.00015838 | -3.9694e-05 | 2.1335e-09 | -7.6361e-07 | 0.00023873 | 0.000239 | 0.000239 | 0.9861 | -0.10135 | 0.98608 | -0.10145 | 0.088519
74 | 0.00031978 | 7.9967e-05 | -0.00031978 | -8.0144e-05 | 2.0843e-09 | -1.777e-07 | 0.00048551 | 0.00048557 | 0.00048557 | 0.97996 | -0.14653 | 0.97995 | -0.14658 | 0.17984
75 | 0.0004207 | 0.00010529 | -0.0004207 | -0.00010544 | 2.7814e-09 | -1.4537e-07 | 0.00062893 | 0.00062898 | 0.00062898 | 0.99528 | -0.033419 | 0.99527 | -0.033466 | 0.23296
76 | 0.0053798 | 0.0013466 | -0.0053786 | -0.0013465 | 1.1981e-06 | 8.3289e-08 | 0.0080857 | 0.0080858 | 0.0080858 | 0.98999 | -0.070264 | 0.98976 | -0.071876 | 2.9947
77 | 0.00064776 | 0.00016203 | -0.00064774 | -0.00016234 | 1.4229e-08 | -3.0386e-07 | 0.00097351 | 0.00097362 | 0.00097362 | 0.98999 | -0.070264 | 0.98996 | -0.070423 | 0.3606
78 | 0.00029217 | 7.279e-05 | -0.00029217 | -7.3224e-05 | 4.0742e-09 | -4.3445e-07 | 0.00043886 | 0.00043901 | 0.00043901 | 0.99031 | -0.067975 | 0.9903 | -0.068076 | 0.1626
79 | 0.00065851 | 0.00016267 | -0.00065844 | -0.00016398 | 6.3138e-08 | -1.3072e-06 | 0.00098857 | 0.00098904 | 0.00098904 | 0.99036 | -0.067587 | 0.99026 | -0.068294 | 0.36631
80 | 0.00065844 | 0.00016398 | -0.00065839 | -0.00016501 | 4.9878e-08 | -1.0316e-06 | 0.00098904 | 0.00098941 | 0.00098941 | 0.99026 | -0.068294 | 0.99019 | -0.068845 | 0.36645
81 | 0.00035283 | 8.8427e-05 | -0.00035283 | -8.8428e-05 | 1.7611e-11 | -1.2649e-09 | 0.00053022 | 0.00053022 | 0.00053022 | 0.99019 | -0.068845 | 0.99019 | -0.068845 | 0.19638
82 | 0.00040366 | 0.00010085 | -0.00040365 | -0.00010117 | 5.6315e-09 | -3.1282e-07 | 0.00060676 | 0.00060687 | 0.00060687 | 0.98976 | -0.071876 | 0.98974 | -0.071977 | 0.22477
83 | 0.004975 | 0.0012457 | -0.0049747 | -0.0012457 | 2.6912e-07 | 4.4217e-09 | 0.007479 | 0.0074791 | 0.0074791 | 0.98976 | -0.071876 | 0.9897 | -0.072268 | 2.77
84 | 0.00047226 | 0.00011835 | -0.00047226 | -0.00011836 | 1.0554e-10 | -4.2709e-09 | 0.00070985 | 0.00070985 | 0.00070985 | 0.98996 | -0.070423 | 0.98996 | -0.070424 | 0.26291
85 | 0.0046655 | 0.0011682 | -0.0046651 | -0.0011682 | 4.2834e-07 | -1.453e-08 | 0.0070142 | 0.0070143 | 0.0070143 | 0.9897 | -0.072268 | 0.98961 | -0.072932 | 2.5979
86 | 0.0044151 | 0.0011055 | -0.0044132 | -0.0011057 | 1.902e-06 | -1.5669e-07 | 0.0066384 | 0.0066387 | 0.0066387 | 0.98961 | -0.072932 | 0.98917 | -0.076048 | 2.4588
87 | 0.0044132 | 0.0011057 | -0.0044122 | -0.0011058 | 1.0422e-06 | -8.5488e-08 | 0.0066387 | 0.0066389 | 0.0066389 | 0.98917 | -0.076048 | 0.98893 | -0.077755 | 2.4588
88 | -0.00062933 | -0.00015772 | 0.00062933 | 0.0001576 | 5.6486e-09 | -1.248e-07 | 0.00095167 | 0.00095163 | 0.00095167 | 0.98401 | -0.11252 | 0.98402 | -0.11245 | 0.35247
89 | 0.0026745 | 0.00066873 | -0.0026733 | -0.00066973 | 1.2128e-06 | -1.0019e-06 | 0.0040715 | 0.004072 | 0.004072 | 0.97732 | -0.16036 | 0.97686 | -0.16364 | 1.5082
90 | 0.0012884 | 0.00032266 | -0.0012884 | -0.0003229 | 4.9791e-08 | -2.4018e-07 | 0.0019625 | 0.0019626 | 0.0019626 | 0.97686 | -0.16364 | 0.97682 | -0.16392 | 0.7269
91 | 0.0053311 | 0.0013352 | -0.0053289 | -0.001335 | 2.2351e-06 | 1.9131e-07 | 0.0081548 | 0.008155 | 0.008155 | 0.97274 | -0.19319 | 0.97232 | -0.19622 | 3.0204
92 | 0.0023002 | 0.00057594 | -0.0022998 | -0.00057639 | 3.6607e-07 | -4.4636e-07 | 0.0035199 | 0.0035201 | 0.0035201 | 0.97232 | -0.19622 | 0.97216 | -0.19737 | 1.3038

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.053111 | 0.013113

## res_load
| p_mw | q_mvar
0 | 0.0014781 | 0.00037044
1 | 0.0038968 | 0.00097663
2 | 0.00046947 | 0.00011766
3 | 0.0002312 | 5.7945e-05
4 | 0.00058108 | 0.00014563
5 | 0.0002234 | 5.599e-05
6 | 0.0009316 | 0.00023348
7 | 0.001783 | 0.00044685
8 | 0.00049945 | 0.00012517
9 | 0.000286 | 7.1678e-05
10 | 0.0011033 | 0.00027651
11 | 0.00020073 | 5.0307e-05
12 | 0.00045244 | 0.00011339
13 | 0.00023484 | 5.8857e-05
14 | 0.00016041 | 4.0203e-05
15 | 0.00026665 | 6.683e-05
16 | 0.00049209 | 0.00012333
17 | 0.00098113 | 0.0002459
18 | 0.00034709 | 8.6989e-05
19 | 0.00027405 | 6.8684e-05
20 | 0.00021891 | 5.4864e-05
21 | 0.00027097 | 6.7911e-05
22 | 0.00045294 | 0.00011352
23 | 0.00019581 | 4.9074e-05
24 | 0.00022502 | 5.6395e-05
25 | 0.0003696 | 9.2629e-05
26 | 0.0013363 | 0.00033492
27 | 0.0048271 | 0.0012098
28 | 0.00027491 | 6.89e-05
29 | 0.00037296 | 9.3473e-05
30 | 0.0003542 | 8.8771e-05
31 | 0.00019022 | 4.7674e-05
32 | 0.00020231 | 5.0703e-05
33 | 0.00042192 | 0.00010574
34 | 0.00026371 | 6.6092e-05
35 | 0.00028293 | 7.0909e-05
36 | 0.00017001 | 4.2608e-05
37 | 0.00015838 | 3.9694e-05
38 | 0.0005097 | 0.00012774
39 | 0.00031978 | 8.0144e-05
40 | 0.0004207 | 0.00010544
41 | 0.00041953 | 0.00010514
42 | 0.000467 | 0.00011704
43 | 0.00029217 | 7.3224e-05
44 | 0.00030556 | 7.6581e-05
45 | 0.00017549 | 4.3981e-05
46 | 0.00035283 | 8.8428e-05
47 | 0.00047226 | 0.00011836
48 | 0.00040365 | 0.00010117
49 | 0.00030919 | 7.749e-05
50 | 0.00024998 | 6.265e-05
51 | 0.0044122 | 0.0011058
52 | 0.00062933 | 0.00015772
53 | 0.0047487 | 0.0011901
54 | 0.00026112 | 6.5443e-05
55 | 0.0013848 | 0.00034707
56 | 0.0012884 | 0.0003229
57 | 0.0011654 | 0.00029208
58 | 0.0011088 | 0.00027788
59 | 0.0030287 | 0.00075907
60 | 0.0022998 | 0.00057639
61 | 0.0010251 | 0.00025691

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1