## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-35_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-35_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-35_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-35_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-35_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-35_0_3_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1631-35_0_3_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1631-35_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1631-35_0_3_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1631-35_0_3_node_77 | 0.4 | n |  | TRUE
10 | bus_LV_1631-35_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1631-35_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1631-35_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1631-35_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1631-35_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1631-35_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1631-35_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1631-35_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1631-35_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1631-35_0_3_node_64 | 0.4 | n |  | TRUE
20 | bus_LV_1631-35_0_3_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1631-35_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1631-35_0_3_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_1631-35_0_3_node_66 | 0.4 | n |  | TRUE
24 | bus_LV_1631-35_0_3_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1631-35_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1631-35_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1631-35_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1631-35_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1631-35_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1631-35_0_3_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_1631-35_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1631-35_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_1631-35_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1631-35_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1631-35_0_3_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_1631-35_0_3_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_1631-35_0_3_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_1631-35_0_3_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1631-35_0_3_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_1631-35_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_1631-35_0_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1631-35_0_3_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_1631-35_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1631-35_0_3_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_1631-35_0_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1631-35_0_3_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_1631-35_0_3_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_1631-35_0_3_node_58 | 0.4 | n |  | TRUE
49 | bus_LV_1631-35_0_3_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_1631-35_0_3_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_1631-35_0_3_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_1631-35_0_3_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_1631-35_0_3_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_1631-35_0_3_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_1631-35_0_3_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_1631-35_0_3_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_1631-35_0_3_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_1631-35_0_3_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_1631-35_0_3_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_1631-35_0_3_node_75 | 0.4 | n |  | TRUE
61 | bus_LV_1631-35_0_3_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_1631-35_0_3_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_1631-35_0_3_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_1631-35_0_3_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_1631-35_0_3_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_1631-35_0_3_node_65 | 0.4 | n |  | TRUE
67 | bus_LV_1631-35_0_3_node_67 | 0.4 | n |  | TRUE
68 | bus_LV_1631-35_0_3_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_1631-35_0_3_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_1631-35_0_3_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_1631-35_0_3_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_1631-35_0_3_node_74 | 0.4 | n |  | TRUE
73 | bus_LV_1631-35_0_3_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_1631-35_0_3_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_1631-35_0_3_node_79 | 0.4 | n |  | TRUE
76 | bus_MV_144_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-35_0_3_load_0 | 0 | 0.0031892 | 0.00079928 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-35_0_3_load_1 | 1 | 0.0020051 | 0.00050254 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-35_0_3_load_3 | 3 | 0.0075574 | 0.0018941 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-35_0_3_load_19 | 5 | 0.0028296 | 0.00070916 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-35_0_3_load_20 | 6 | 0.0024428 | 0.00061223 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-35_0_3_load_23 | 8 | 0.0029601 | 0.00074186 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-35_0_3_load_77 | 9 | 0.0013052 | 0.00032711 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-35_0_3_load_5 | 11 | 0.00088364 | 0.00022146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-35_0_3_load_10 | 15 | 0.0041625 | 0.0010432 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-35_0_3_load_11 | 16 | 0.0041723 | 0.0010457 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-35_0_3_load_15 | 17 | 0.0022789 | 0.00057114 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-35_0_3_load_12 | 18 | 0.0031239 | 0.00078292 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-35_0_3_load_64 | 19 | 0.0016929 | 0.00042427 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-35_0_3_load_66 | 23 | 0.0031369 | 0.00078618 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-35_0_3_load_14 | 25 | 0.0022183 | 0.00055596 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-35_0_3_load_16 | 26 | 0.0020409 | 0.00051151 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-35_0_3_load_17 | 27 | 0.0011253 | 0.00028202 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-35_0_3_load_78 | 30 | 0.0013609 | 0.00034107 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-35_0_3_load_24 | 31 | 0.0050178 | 0.0012576 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-35_0_3_load_27 | 33 | 0.010075 | 0.002525 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-35_0_3_load_28 | 34 | 0.0092025 | 0.0023064 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-35_0_3_load_38 | 35 | 0.0090266 | 0.0022623 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-35_0_3_load_44 | 36 | 0.0032344 | 0.00081061 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-35_0_3_load_45 | 37 | 0.0030613 | 0.00076722 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-35_0_3_load_43 | 38 | 0.0066818 | 0.0016746 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-35_0_3_load_30 | 39 | 0.0028307 | 0.00070944 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-35_0_3_load_37 | 41 | 0.0022444 | 0.00056249 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-35_0_3_load_35 | 43 | 0.0014438 | 0.00036185 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-35_0_3_load_40 | 44 | 0.010448 | 0.0026186 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-35_0_3_load_41 | 45 | 0.0049272 | 0.0012349 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-35_0_3_load_58 | 48 | 0.0047493 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-35_0_3_load_48 | 49 | 0.0062042 | 0.0015549 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-35_0_3_load_46 | 50 | 0.0048414 | 0.0012134 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-35_0_3_load_49 | 54 | 0.0049762 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1631-35_0_3_load_50 | 55 | 0.0047853 | 0.0011993 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1631-35_0_3_load_52 | 56 | 0.0088277 | 0.0022124 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1631-35_0_3_load_57 | 57 | 0.0051865 | 0.0012999 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1631-35_0_3_load_55 | 59 | 0.0058859 | 0.0014752 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1631-35_0_3_load_75 | 60 | 0.0038019 | 0.00095286 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1631-35_0_3_load_54 | 61 | 0.0036245 | 0.00090839 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1631-35_0_3_load_56 | 62 | 0.0020896 | 0.00052369 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1631-35_0_3_load_60 | 63 | 0.0060152 | 0.0015076 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1631-35_0_3_load_61 | 64 | 0.007905 | 0.0019812 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1631-35_0_3_load_62 | 65 | 0.0033061 | 0.0008286 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1631-35_0_3_load_65 | 66 | 0.0077688 | 0.0019471 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1631-35_0_3_load_67 | 67 | 0.0022023 | 0.00055195 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1631-35_0_3_load_68 | 68 | 0.004059 | 0.0010173 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1631-35_0_3_load_70 | 70 | 0.0043785 | 0.0010974 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1631-35_0_3_load_71 | 71 | 0.0046855 | 0.0011743 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1631-35_0_3_load_74 | 72 | 0.0033859 | 0.00084858 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1631-35_0_3_load_79 | 75 | 0.0038905 | 0.00097505 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-35_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0023666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-35_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0059892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-35_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.077649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-35_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.07162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-35_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.10663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-35_0_3_line_5 | NAYY 4x150 SE | 4 | 8 | 0.0092899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-35_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.039623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-35_0_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.0088505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-35_0_3_line_8 | NAYY 4x150 SE | 6 | 28 | 0.0031609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-35_0_3_line_9 | NAYY 4x150 SE | 7 | 27 | 0.013157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-35_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.021481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-35_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.022243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-35_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.024971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-35_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.12992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-35_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.00541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-35_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.08059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-35_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.082666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-35_0_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.031768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-35_0_3_line_18 | NAYY 4x150 SE | 14 | 18 | 0.0313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-35_0_3_line_19 | NAYY 4x150 SE | 15 | 19 | 0.0056517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1631-35_0_3_line_20 | NAYY 4x150 SE | 16 | 20 | 0.010308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-35_0_3_line_21 | NAYY 4x150 SE | 18 | 21 | 0.019755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-35_0_3_line_22 | NAYY 4x150 SE | 19 | 22 | 0.006697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1631-35_0_3_line_23 | NAYY 4x150 SE | 20 | 23 | 0.011712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-35_0_3_line_24 | NAYY 4x150 SE | 20 | 24 | 0.19184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-35_0_3_line_25 | NAYY 4x150 SE | 21 | 25 | 0.034694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-35_0_3_line_26 | NAYY 4x150 SE | 22 | 66 | 0.018868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-35_0_3_line_27 | NAYY 4x150 SE | 22 | 65 | 0.0054747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1631-35_0_3_line_28 | NAYY 4x150 SE | 24 | 40 | 0.24846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-35_0_3_line_29 | NAYY 4x150 SE | 24 | 39 | 0.16503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-35_0_3_line_30 | NAYY 4x150 SE | 25 | 26 | 0.086413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-35_0_3_line_31 | NAYY 4x150 SE | 26 | 27 | 0.006225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-35_0_3_line_32 | NAYY 4x150 SE | 28 | 29 | 0.18364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-35_0_3_line_33 | NAYY 4x150 SE | 29 | 30 | 0.099245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-35_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.038099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-35_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.06781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-35_0_3_line_36 | NAYY 4x150 SE | 32 | 34 | 0.040133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-35_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.033697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-35_0_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.021365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-35_0_3_line_39 | NAYY 4x150 SE | 36 | 37 | 0.0097414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-35_0_3_line_40 | NAYY 4x150 SE | 36 | 38 | 0.043725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-35_0_3_line_41 | NAYY 4x150 SE | 37 | 50 | 0.0078183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-35_0_3_line_42 | NAYY 4x150 SE | 40 | 41 | 0.0079148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-35_0_3_line_43 | NAYY 4x150 SE | 41 | 42 | 0.093363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-35_0_3_line_44 | NAYY 4x150 SE | 42 | 43 | 0.22468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-35_0_3_line_45 | NAYY 4x150 SE | 44 | 45 | 0.051625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-35_0_3_line_46 | NAYY 4x150 SE | 45 | 46 | 0.0088043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1631-35_0_3_line_47 | NAYY 4x150 SE | 46 | 47 | 0.00813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1631-35_0_3_line_48 | NAYY 4x150 SE | 46 | 48 | 0.011664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1631-35_0_3_line_49 | NAYY 4x150 SE | 47 | 49 | 0.015959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1631-35_0_3_line_50 | NAYY 4x150 SE | 47 | 50 | 0.0047263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1631-35_0_3_line_51 | NAYY 4x150 SE | 48 | 51 | 0.005808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_1631-35_0_3_line_52 | NAYY 4x150 SE | 49 | 52 | 0.0087123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1631-35_0_3_line_53 | NAYY 4x150 SE | 51 | 63 | 0.0076971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1631-35_0_3_line_54 | NAYY 4x150 SE | 51 | 64 | 0.009671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1631-35_0_3_line_55 | NAYY 4x150 SE | 52 | 53 | 0.020015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1631-35_0_3_line_56 | NAYY 4x150 SE | 52 | 54 | 0.013105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1631-35_0_3_line_57 | NAYY 4x150 SE | 53 | 57 | 0.010119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1631-35_0_3_line_58 | NAYY 4x150 SE | 53 | 58 | 0.019473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1631-35_0_3_line_59 | NAYY 4x150 SE | 54 | 55 | 0.0087928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1631-35_0_3_line_60 | NAYY 4x150 SE | 55 | 56 | 0.012663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1631-35_0_3_line_61 | NAYY 4x150 SE | 57 | 59 | 0.005287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1631-35_0_3_line_62 | NAYY 4x150 SE | 58 | 60 | 0.13696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1631-35_0_3_line_63 | NAYY 4x150 SE | 59 | 61 | 0.003616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1631-35_0_3_line_64 | NAYY 4x150 SE | 60 | 72 | 0.019439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1631-35_0_3_line_65 | NAYY 4x150 SE | 61 | 62 | 0.01765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1631-35_0_3_line_66 | NAYY 4x150 SE | 63 | 65 | 0.011657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_1631-35_0_3_line_67 | NAYY 4x150 SE | 67 | 68 | 0.0083115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1631-35_0_3_line_68 | NAYY 4x150 SE | 67 | 69 | 0.026276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1631-35_0_3_line_69 | NAYY 4x150 SE | 68 | 70 | 0.028591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1631-35_0_3_line_70 | NAYY 4x150 SE | 69 | 71 | 0.041127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1631-35_0_3_line_71 | NAYY 4x150 SE | 70 | 72 | 0.002683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1631-35_0_3_line_72 | NAYY 4x150 SE | 71 | 73 | 0.061172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1631-35_0_3_line_73 | NAYY 4x150 SE | 73 | 74 | 0.004896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1631-35_0_3_line_74 | NAYY 4x150 SE | 74 | 75 | 0.075329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-35_0_3_trafo_10 | 0.25 MVA 20/0.4 kV | 76 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47
0 | 2725639.8384 | 1206764.2052 | 2725639.7066 | 1206764.2433 | 2725637.4937 | 1206764.5138
1 | 2725645.5925 | 1206762.5436 | 2725639.8384 | 1206764.2052
2 | 2725637.4937 | 1206764.5138 | 2725632.9567 | 1206765.0685 | 2725625.6531 | 1206763.2912 | 2725611.3356 | 1206755.0059 | 2725583.5486 | 1206737.5301 | 2725568.3219 | 1206732.0183
3 | 2725645.5925 | 1206762.5436 | 2725648.1828 | 1206764.166 | 2725664.1709 | 1206765.3701 | 2725666.0713 | 1206767.2449 | 2725666.8423 | 1206769.2849 | 2725666.275 | 1206772.0195 | 2725662.8284 | 1206776.0167 | 2725649.5686 | 1206787.9468 | 2725635.4573 | 1206796.6009 | 2725630.3209 | 1206798.1162
4 | 2725677.2768 | 1206660.7342 | 2725645.5925 | 1206762.5436
5 | 2725630.3209 | 1206798.1162 | 2725622.0609 | 1206798.0423 | 2725621.0334 | 1206798.1069
6 | 2725713.5823 | 1206676.2153 | 2725707.7099 | 1206674.6505 | 2725691.6124 | 1206668.518 | 2725682.1299 | 1206663.6368 | 2725677.2768 | 1206660.7342
7 | 2725669.6811 | 1206656.1913 | 2725677.2768 | 1206660.7342
8 | 2725716.6366 | 1206677.0292 | 2725713.5823 | 1206676.2153
9 | 2725669.6811 | 1206656.1913 | 2725658.3909 | 1206649.4367
10 | 2725477.9838 | 1206641.5592 | 2725471.1529 | 1206661.9248
11 | 2725477.9838 | 1206641.5592 | 2725481.4846 | 1206632.8149 | 2725486.3185 | 1206626.1559 | 2725489.6492 | 1206622.9679
12 | 2725489.6492 | 1206622.9679 | 2725489.8334 | 1206620.3586 | 2725491.686 | 1206615.8274 | 2725489.8385 | 1206613.965 | 2725486.1072 | 1206613.7753 | 2725486.3898 | 1206610.4676 | 2725478.6285 | 1206611.0153
13 | 2725466.595 | 1206529.0781 | 2725466.5057 | 1206531.1556 | 2725463.5496 | 1206534.6183 | 2725462.6022 | 1206536.2552 | 2725460.7084 | 1206541.2971 | 2725454.5149 | 1206554.3658 | 2725449.3611 | 1206567.9124 | 2725449.6529 | 1206568.5078 | 2725450.6879 | 1206568.8521 | 2725458.5315 | 1206565.948 | 2725459.417 | 1206566.1668 | 2725460.4468 | 1206569.2908 | 2725463.0609 | 1206573.7714 | 2725462.7716 | 1206578.847 | 2725463.0282 | 1206580.7538 | 2725463.9834 | 1206581.9971 | 2725465.5996 | 1206582.9206 | 2725467.3139 | 1206583.1568 | 2725478.1227 | 1206580.3374 | 2725479.0852 | 1206580.5133 | 2725479.8517 | 1206581.6859 | 2725474.9775 | 1206589.9008 | 2725473.1989 | 1206596.3351 | 2725468.4918 | 1206609.6241 | 2725468.5682 | 1206610.6932 | 2725469.0943 | 1206611.3603 | 2725470.2455 | 1206611.6069 | 2725478.6285 | 1206611.0153
14 | 2725494.5442 | 1206620.6356 | 2725489.6492 | 1206622.9679
15 | 2725466.595 | 1206529.0781 | 2725456.5343 | 1206533.5812 | 2725443.9671 | 1206541.5121 | 2725429.1164 | 1206551.6746 | 2725421.2584 | 1206558.8817 | 2725418.2417 | 1206562.3321 | 2725410.1488 | 1206577.8184 | 2725407.6873 | 1206580.9628
16 | 2725466.595 | 1206529.0781 | 2725474.6514 | 1206525.4668 | 2725503.3254 | 1206511.3254 | 2725515.2058 | 1206506.3936 | 2725524.9569 | 1206503.9523 | 2725535.6543 | 1206502.098 | 2725543.5904 | 1206500.5113
17 | 2725494.5442 | 1206620.6356 | 2725495.6404 | 1206614.4539 | 2725500.2561 | 1206608.4019 | 2725498.7978 | 1206607.5706 | 2725496.9831 | 1206607.7659 | 2725491.6235 | 1206611.5673 | 2725487.9424 | 1206604.6513
18 | 2725494.5442 | 1206620.6356 | 2725516.9799 | 1206611.5448 | 2725523.4441 | 1206608.6254
19 | 2725404.0674 | 1206585.3019 | 2725406.7404 | 1206582.1723 | 2725407.6873 | 1206580.9628
20 | 2725553.5947 | 1206498.0499 | 2725546.9765 | 1206499.8343 | 2725543.5904 | 1206500.5113
21 | 2725542.017 | 1206602.1084 | 2725532.2718 | 1206604.6388 | 2725523.4441 | 1206608.6254
22 | 2725398.3472 | 1206588.423 | 2725402.7938 | 1206586.793 | 2725404.0674 | 1206585.3019
23 | 2725553.5947 | 1206498.0499 | 2725562.2286 | 1206490.1365
24 | 2725553.5947 | 1206498.0499 | 2725561.5047 | 1206495.6144 | 2725593.6963 | 1206486.0508 | 2725620.8406 | 1206479.1833 | 2725637.3593 | 1206474.7386 | 2725651.5953 | 1206471.3912 | 2725726.2477 | 1206463.1898 | 2725741.3826 | 1206463.7645
25 | 2725542.017 | 1206602.1084 | 2725553.4364 | 1206602.4488 | 2725567.7156 | 1206604.9844 | 2725576.0221 | 1206607.7884
26 | 2725398.3472 | 1206588.423 | 2725404.7489 | 1206599.4659 | 2725399.4764 | 1206602.5404
27 | 2725398.3472 | 1206588.423 | 2725394.583 | 1206587.9881 | 2725393.0281 | 1206587.3378
28 | 2725741.3826 | 1206463.7645 | 2725742.4274 | 1206461.1178 | 2725744.4957 | 1206458.6373 | 2725751.1078 | 1206454.2621 | 2725754.9272 | 1206449.9169 | 2725761.3027 | 1206445.9371 | 2725765.5059 | 1206442.5119 | 2725771.7295 | 1206442.1316 | 2725775.507 | 1206440.1318 | 2725779.7374 | 1206436.8629 | 2725792.3122 | 1206434.0145 | 2725799.7645 | 1206429.8461 | 2725804.1452 | 1206429.5493 | 2725828.7532 | 1206430.7799 | 2725830.9166 | 1206430.6477 | 2725837.6498 | 1206428.1098 | 2725832.2531 | 1206425.7165 | 2725828.5094 | 1206425.0259 | 2725827.1397 | 1206424.3188 | 2725827.7046 | 1206422.785 | 2725828.7533 | 1206422.1177 | 2725837.1107 | 1206420.1257 | 2725839.8664 | 1206418.9606 | 2725840.1381 | 1206417.6209 | 2725839.3066 | 1206416.6471 | 2725828.5787 | 1206414.1635 | 2725825.894 | 1206412.6836 | 2725824.1376 | 1206411.1899 | 2725823.029 | 1206409.2873 | 2725837.3473 | 1206404.2185 | 2725839.476 | 1206402.4842 | 2725838.8473 | 1206401.9928 | 2725834.8643 | 1206402.1868 | 2725834.4214 | 1206401.5436 | 2725834.5918 | 1206400.6799 | 2725837.114 | 1206399.4099 | 2725838.2686 | 1206395.8871 | 2725839.9287 | 1206392.5639 | 2725842.0469 | 1206389.5285 | 2725844.5919 | 1206386.8134 | 2725847.4935 | 1206384.5061 | 2725850.7056 | 1206382.6279 | 2725854.1507 | 1206381.2439 | 2725857.7678 | 1206380.3639 | 2725867.7274 | 1206378.5169 | 2725874.4869 | 1206377.2585 | 2725882.7724 | 1206382.6373 | 2725884.6571 | 1206391.7507
29 | 2725741.3826 | 1206463.7645 | 2725746.2083 | 1206464.7336 | 2725770.3709 | 1206473.0155 | 2725812.8382 | 1206491.0018 | 2725897.4868 | 1206516.6333
30 | 2725653.0489 | 1206646.2407 | 2725615.5286 | 1206623.7935 | 2725594.8718 | 1206614.1515 | 2725576.0221 | 1206607.7884
31 | 2725653.0489 | 1206646.2407 | 2725658.3909 | 1206649.4367
32 | 2725899.6335 | 1206684.9915 | 2725887.9544 | 1206681.4647 | 2725874.4524 | 1206678.5222 | 2725858.342 | 1206676.6145 | 2725836.432 | 1206675.5518 | 2725823.5797 | 1206676.0702 | 2725803.7234 | 1206676.8301 | 2725775.0547 | 1206678.8165 | 2725725.1736 | 1206676.2417 | 2725716.6366 | 1206677.0292
33 | 2725899.6335 | 1206684.9915 | 2725906.8724 | 1206684.7884 | 2725922.2338 | 1206685.7799 | 2725926.8146 | 1206685.365 | 2725931.4052 | 1206684.1276 | 2725936.7318 | 1206682.2607 | 2725940.5834 | 1206681.7972 | 2725944.9258 | 1206681.8666 | 2725951.164 | 1206682.9435 | 2725960.8567 | 1206685.4277 | 2725981.1397 | 1206688.9583 | 2725997.5465 | 1206692.3183
34 | 2725314.8513 | 1206660.6363 | 2725314.9996 | 1206668.4231 | 2725318.1736 | 1206691.8855 | 2725319.4914 | 1206698.3882
35 | 2725314.8513 | 1206660.6363 | 2725312.7756 | 1206659.8588 | 2725311.993 | 1206655.8282 | 2725307.9379 | 1206642.4439 | 2725302.0915 | 1206624.5186 | 2725301.5479 | 1206620.3373 | 2725299.6719 | 1206609.3229 | 2725299.1827 | 1206607.6224 | 2725298.7333 | 1206608.0133 | 2725295.135 | 1206615.9772 | 2725292.9948 | 1206615.7321
36 | 2725314.8513 | 1206660.6363 | 2725315.9277 | 1206648.5052 | 2725320.6004 | 1206632.491 | 2725324.9942 | 1206622.1105
37 | 2725263.6256 | 1206605.4917 | 2725273.4861 | 1206610.8078 | 2725286.3442 | 1206610.3773 | 2725289.5935 | 1206610.3343 | 2725292.9948 | 1206615.7321
38 | 2725335.6387 | 1206603.6068 | 2725331.1504 | 1206610.8403 | 2725325.6995 | 1206620.4443 | 2725324.9942 | 1206622.1105
39 | 2725335.6387 | 1206603.6068 | 2725339.7141 | 1206596.8316 | 2725340.9357 | 1206595.4624
40 | 2725335.6387 | 1206603.6068 | 2725339.7897 | 1206607.7193 | 2725353.5296 | 1206611.6663 | 2725352.2358 | 1206626.8953 | 2725343.9736 | 1206627.7135
41 | 2725340.9357 | 1206595.4624 | 2725343.1032 | 1206593.0332 | 2725346.4273 | 1206589.9078
42 | 2725884.6571 | 1206391.7507 | 2725892.2127 | 1206394.1078
43 | 2725976.4135 | 1206434.3409 | 2725966.1922 | 1206430.211 | 2725901.9259 | 1206398.2865 | 2725893.2204 | 1206394.4222 | 2725892.2127 | 1206394.1078
44 | 2725976.4135 | 1206434.3409 | 2725977.6073 | 1206438.3358 | 2725978.9386 | 1206440.4989 | 2725982.882 | 1206444.3406 | 2725998.0144 | 1206452.5996 | 2726005.399 | 1206455.6022 | 2726037.2986 | 1206462.0694 | 2726048.1346 | 1206465.9122 | 2726054.348 | 1206468.8901 | 2726069.1736 | 1206479.4224 | 2726077.9753 | 1206485.2016 | 2726086.4594 | 1206489.4507 | 2726118.5974 | 1206504.0629 | 2726143.7872 | 1206518.7841 | 2726147.6094 | 1206521.5114 | 2726159.5593 | 1206533.1062 | 2726167.1027 | 1206538.3029 | 2726169.8213 | 1206539.8455
45 | 2725352.0712 | 1206650.4169 | 2725353.0779 | 1206642.9363 | 2725355.13 | 1206627.8234 | 2725356.7748 | 1206611.4565 | 2725356.857 | 1206599.0807
46 | 2725356.9156 | 1206590.2766 | 2725356.857 | 1206599.0807
47 | 2725349.8707 | 1206586.6704 | 2725352.9577 | 1206589.2816 | 2725355.2839 | 1206590.0866 | 2725356.9156 | 1206590.2766
48 | 2725356.9156 | 1206590.2766 | 2725368.5445 | 1206589.3704
49 | 2725349.8707 | 1206586.6704 | 2725355.046 | 1206580.7745 | 2725359.5166 | 1206574.0029
50 | 2725349.8707 | 1206586.6704 | 2725346.4273 | 1206589.9078
51 | 2725374.3349 | 1206588.9191 | 2725368.5445 | 1206589.3704
52 | 2725363.9647 | 1206566.5286 | 2725362.4243 | 1206569.5987 | 2725359.5166 | 1206574.0029
53 | 2725374.3349 | 1206588.9191 | 2725381.92 | 1206587.6106
54 | 2725381.8577 | 1206582.8169 | 2725374.3349 | 1206588.9191
55 | 2725363.9647 | 1206566.5286 | 2725365.0107 | 1206563.0924 | 2725365.244 | 1206559.2277 | 2725365.337 | 1206554.804 | 2725364.2045 | 1206550.4102 | 2725363.1047 | 1206546.9956
56 | 2725363.9647 | 1206566.5286 | 2725351.2007 | 1206563.5584 | 2725351.2007 | 1206563.5584
57 | 2725363.1047 | 1206546.9956 | 2725373.1207 | 1206545.554
58 | 2725349.6395 | 1206533.2246 | 2725353.051 | 1206535.965 | 2725357.8991 | 1206539.8475 | 2725360.6354 | 1206542.8628 | 2725363.1047 | 1206546.9956
59 | 2725351.2007 | 1206563.5584 | 2725345.2667 | 1206560.6649 | 2725343.641 | 1206559.1962
60 | 2725334.465 | 1206550.4748 | 2725339.5329 | 1206555.485 | 2725343.641 | 1206559.1962
61 | 2725378.3538 | 1206544.8008 | 2725373.1207 | 1206545.554
62 | 2725349.6395 | 1206533.2246 | 2725352.351 | 1206532.3475 | 2725354.4011 | 1206531.8124 | 2725362.7951 | 1206529.5091 | 2725380.4235 | 1206523.6414 | 2725413.4074 | 1206506.7657 | 2725416.6605 | 1206503.6539 | 2725421.3143 | 1206494.3445 | 2725429.134 | 1206482.8111 | 2725434.3415 | 1206472.8573 | 2725439.8279 | 1206464.4773 | 2725435.9526 | 1206457.0235 | 2725438.8952 | 1206448.3424
63 | 2725381.9329 | 1206544.2857 | 2725378.3538 | 1206544.8008
64 | 2725444.3596 | 1206430.8174 | 2725440.3072 | 1206435.5319 | 2725441.0948 | 1206441.8532 | 2725438.8952 | 1206448.3424
65 | 2725399.1955 | 1206540.8266 | 2725392.8339 | 1206542.7167 | 2725381.9329 | 1206544.2857
66 | 2725381.92 | 1206587.6106 | 2725383.5278 | 1206587.3332 | 2725386.9959 | 1206585.9272 | 2725390.1035 | 1206586.1148 | 2725393.0281 | 1206587.3378
67 | 2725477.7139 | 1206410.0548 | 2725471.008 | 1206414.383 | 2725470.7237 | 1206414.5508
68 | 2725493.324 | 1206391.1231 | 2725494.1005 | 1206394.353 | 2725485.1064 | 1206405.2834 | 2725477.7139 | 1206410.0548
69 | 2725446.1086 | 1206428.7828 | 2725447.0763 | 1206427.6569 | 2725452.7211 | 1206423.6836 | 2725465.7312 | 1206417.4967 | 2725470.7237 | 1206414.5508
70 | 2725493.324 | 1206391.1231 | 2725478.7047 | 1206391.3493 | 2725464.5291 | 1206390.7287 | 2725456.5916 | 1206390.1281 | 2725452.2653 | 1206389.6135
71 | 2725444.3596 | 1206430.8174 | 2725446.1086 | 1206428.7828
72 | 2725392.6204 | 1206376.2403 | 2725431.345 | 1206385.9723 | 2725447.7355 | 1206389.0746 | 2725452.2653 | 1206389.6135
73 | 2725387.8603 | 1206375.0394 | 2725392.6204 | 1206376.2403
74 | 2725387.8603 | 1206375.0394 | 2725387.7366 | 1206391.783 | 2725386.7505 | 1206395.2649 | 2725384.4811 | 1206398.631 | 2725379.6102 | 1206402.3426 | 2725365.2456 | 1206408.5457 | 2725357.4536 | 1206412.6074 | 2725352.2393 | 1206415.6447 | 2725349.2915 | 1206420.1641 | 2725350.2154 | 1206424.7092 | 2725352.5881 | 1206428.3729

## bus_geodata
| x | y | coords
0 | 2725639.8384 | 1206764.2052
1 | 2725637.4937 | 1206764.5138
2 | 2725645.5925 | 1206762.5436
3 | 2725568.3219 | 1206732.0183
4 | 2725630.3209 | 1206798.1162
5 | 2725677.2768 | 1206660.7342
6 | 2725713.5823 | 1206676.2153
7 | 2725669.6811 | 1206656.1913
8 | 2725621.0334 | 1206798.1069
9 | 2725471.1529 | 1206661.9248
10 | 2725477.9838 | 1206641.5592
11 | 2725478.6285 | 1206611.0153
12 | 2725489.6492 | 1206622.9679
13 | 2725466.595 | 1206529.0781
14 | 2725494.5442 | 1206620.6356
15 | 2725407.6873 | 1206580.9628
16 | 2725543.5904 | 1206500.5113
17 | 2725487.9424 | 1206604.6513
18 | 2725523.4441 | 1206608.6254
19 | 2725404.0674 | 1206585.3019
20 | 2725553.5947 | 1206498.0499
21 | 2725542.017 | 1206602.1084
22 | 2725398.3472 | 1206588.423
23 | 2725562.2286 | 1206490.1365
24 | 2725741.3826 | 1206463.7645
25 | 2725576.0221 | 1206607.7884
26 | 2725653.0489 | 1206646.2407
27 | 2725658.3909 | 1206649.4367
28 | 2725716.6366 | 1206677.0292
29 | 2725899.6335 | 1206684.9915
30 | 2725997.5465 | 1206692.3183
31 | 2725319.4914 | 1206698.3882
32 | 2725314.8513 | 1206660.6363
33 | 2725292.9948 | 1206615.7321
34 | 2725324.9942 | 1206622.1105
35 | 2725263.6256 | 1206605.4917
36 | 2725335.6387 | 1206603.6068
37 | 2725340.9357 | 1206595.4624
38 | 2725343.9736 | 1206627.7135
39 | 2725897.4868 | 1206516.6333
40 | 2725884.6571 | 1206391.7507
41 | 2725892.2127 | 1206394.1078
42 | 2725976.4135 | 1206434.3409
43 | 2726169.8213 | 1206539.8455
44 | 2725352.0712 | 1206650.4169
45 | 2725356.857 | 1206599.0807
46 | 2725356.9156 | 1206590.2766
47 | 2725349.8707 | 1206586.6704
48 | 2725368.5445 | 1206589.3704
49 | 2725359.5166 | 1206574.0029
50 | 2725346.4273 | 1206589.9078
51 | 2725374.3349 | 1206588.9191
52 | 2725363.9647 | 1206566.5287
53 | 2725363.1047 | 1206546.9956
54 | 2725351.2007 | 1206563.5584
55 | 2725343.641 | 1206559.1962
56 | 2725334.465 | 1206550.4748
57 | 2725373.1207 | 1206545.554
58 | 2725349.6395 | 1206533.2246
59 | 2725378.3538 | 1206544.8008
60 | 2725438.8952 | 1206448.3424
61 | 2725381.9329 | 1206544.2857
62 | 2725399.1955 | 1206540.8266
63 | 2725381.92 | 1206587.6106
64 | 2725381.8577 | 1206582.8169
65 | 2725393.0281 | 1206587.3378
66 | 2725399.4764 | 1206602.5404
67 | 2725477.7139 | 1206410.0548
68 | 2725470.7237 | 1206414.5508
69 | 2725493.324 | 1206391.1231
70 | 2725446.1086 | 1206428.7828
71 | 2725452.2653 | 1206389.6135
72 | 2725444.3596 | 1206430.8174
73 | 2725392.6204 | 1206376.2403
74 | 2725387.8603 | 1206375.0394
75 | 2725352.5881 | 1206428.3729
76 | 2725398.3472 | 1206588.423

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97574 | -0.17085 | 0.0031892 | 0.00079928
1 | 0.9757 | -0.17109 | 0.0020051 | 0.00050254
2 | 0.97585 | -0.17005 | 0 | 0
3 | 0.97485 | -0.17725 | 0.0075574 | 0.0018941
4 | 0.97554 | -0.17228 | 0 | 0
5 | 0.9783 | -0.15252 | 0.0028296 | 0.00070916
6 | 0.97808 | -0.1541 | 0.0024428 | 0.00061223
7 | 0.97858 | -0.15045 | 0 | 0
8 | 0.9755 | -0.17257 | 0.0029601 | 0.00074186
9 | 0.98623 | -0.096105 | 0.0013052 | 0.00032711
10 | 0.98627 | -0.095817 | 0 | 0
11 | 0.98757 | -0.086686 | 0.00088364 | 0.00022146
12 | 0.98632 | -0.095518 | 0 | 0
13 | 0.99425 | -0.039923 | 0 | 0
14 | 0.98606 | -0.097362 | 0 | 0
15 | 1 | 0 | -0.2183 | -0.054794
16 | 0.99261 | -0.051562 | 0.0041723 | 0.0010457
17 | 0.98595 | -0.098106 | 0.0022789 | 0.00057114
18 | 0.98465 | -0.10731 | 0.0031239 | 0.00078292
19 | 0.99933 | -0.0046858 | 0.0016929 | 0.00042427
20 | 0.99247 | -0.05258 | 0 | 0
21 | 0.98385 | -0.11297 | 0 | 0
22 | 0.99853 | -0.01019 | 0 | 0
23 | 0.99241 | -0.052953 | 0.0031369 | 0.00078618
24 | 0.99066 | -0.06543 | 0 | 0
25 | 0.98245 | -0.12293 | 0.0022183 | 0.00055596
26 | 0.97923 | -0.14585 | 0.0020409 | 0.00051151
27 | 0.97901 | -0.14738 | 0.0011253 | 0.00028202
28 | 0.97807 | -0.15415 | 0 | 0
29 | 0.97771 | -0.15679 | 0 | 0
30 | 0.97751 | -0.1582 | 0.0013609 | 0.00034107
31 | 0.98923 | -0.075462 | 0.0050178 | 0.0012576
32 | 0.9895 | -0.073512 | 0 | 0
33 | 0.98763 | -0.086744 | 0.010075 | 0.002525
34 | 0.9909 | -0.063653 | 0.0092025 | 0.0023064
35 | 0.9872 | -0.089859 | 0.0090266 | 0.0022623
36 | 0.99193 | -0.05642 | 0.0032344 | 0.00081061
37 | 0.99253 | -0.052148 | 0.0030613 | 0.00076722
38 | 0.99151 | -0.059386 | 0.0066818 | 0.0016746
39 | 0.98999 | -0.070197 | 0.0028307 | 0.00070944
40 | 0.98935 | -0.074871 | 0 | 0
41 | 0.9893 | -0.075171 | 0.0022444 | 0.00056249
42 | 0.98911 | -0.07657 | 0 | 0
43 | 0.98864 | -0.079906 | 0.0014438 | 0.00036185
44 | 0.99313 | -0.04796 | 0.010448 | 0.0026186
45 | 0.99391 | -0.042505 | 0.0049272 | 0.0012349
46 | 0.9941 | -0.041138 | 0 | 0
47 | 0.9934 | -0.046035 | 0 | 0
48 | 0.99523 | -0.03322 | 0.0047493 | 0.0011903
49 | 0.99184 | -0.057033 | 0.0062042 | 0.0015549
50 | 0.99306 | -0.048481 | 0.0048414 | 0.0012134
51 | 0.99582 | -0.029145 | 0 | 0
52 | 0.99106 | -0.062502 | 0 | 0
53 | 0.98981 | -0.071306 | 0 | 0
54 | 0.99071 | -0.064978 | 0.0049762 | 0.0012471
55 | 0.99054 | -0.066196 | 0.0047853 | 0.0011993
56 | 0.99038 | -0.067333 | 0.0088277 | 0.0022124
57 | 0.98956 | -0.073037 | 0.0051865 | 0.0012999
58 | 0.98906 | -0.076555 | 0 | 0
59 | 0.98948 | -0.073662 | 0.0058859 | 0.0014752
60 | 0.98382 | -0.11369 | 0.0038019 | 0.00095286
61 | 0.98945 | -0.073873 | 0.0036245 | 0.00090839
62 | 0.98939 | -0.074249 | 0.0020896 | 0.00052369
63 | 0.99663 | -0.023446 | 0.0060152 | 0.0015076
64 | 0.99571 | -0.029914 | 0.007905 | 0.0019812
65 | 0.99792 | -0.014482 | 0.0033061 | 0.0008286
66 | 0.99832 | -0.011657 | 0.0077688 | 0.0019471
67 | 0.98236 | -0.12408 | 0.0022023 | 0.00055195
68 | 0.98249 | -0.12315 | 0.004059 | 0.0010173
69 | 0.98203 | -0.12642 | 0 | 0
70 | 0.9831 | -0.11876 | 0.0043785 | 0.0010974
71 | 0.98152 | -0.13008 | 0.0046855 | 0.0011743
72 | 0.98318 | -0.11823 | 0.0033859 | 0.00084858
73 | 0.98117 | -0.13255 | 0 | 0
74 | 0.98114 | -0.13275 | 0 | 0
75 | 0.98072 | -0.13579 | 0.0038905 | 0.00097505
76 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0095693 | 0.0023982 | -0.009569 | -0.0023981 | 3.145e-07 | 9.1401e-08 | 0.014593 | 0.014593 | 0.014593 | 0.97574 | -0.17085 | 0.9757 | -0.17109 | 5.4049
1 | -0.012758 | -0.0031975 | 0.01276 | 0.003198 | 1.4148e-06 | 4.6934e-07 | 0.019457 | 0.019457 | 0.019457 | 0.97574 | -0.17085 | 0.97585 | -0.17005 | 7.2062
2 | 0.0075638 | 0.0018956 | -0.0075574 | -0.0018941 | 6.4475e-06 | 1.5109e-06 | 0.011535 | 0.011536 | 0.011536 | 0.9757 | -0.17109 | 0.97485 | -0.17725 | 4.2725
3 | 0.0029611 | 0.00074125 | -0.0029602 | -0.00074179 | 9.1105e-07 | -5.4408e-07 | 0.0045149 | 0.0045152 | 0.0045152 | 0.97585 | -0.17005 | 0.97554 | -0.17228 | 1.6723
4 | -0.015721 | -0.0039392 | 0.015759 | 0.0039526 | 3.8233e-05 | 1.3369e-05 | 0.023972 | 0.023971 | 0.023972 | 0.97585 | -0.17005 | 0.9783 | -0.15252 | 8.8784
5 | 0.0029602 | 0.00074179 | -0.0029601 | -0.00074186 | 1.1818e-07 | -7.0527e-08 | 0.0045152 | 0.0045152 | 0.0045152 | 0.97554 | -0.17228 | 0.9755 | -0.17257 | 1.6723
6 | 0.0038053 | 0.00094982 | -0.0038045 | -0.00095 | 8.2792e-07 | -1.7897e-07 | 0.0057866 | 0.0057867 | 0.0057867 | 0.9783 | -0.15252 | 0.97808 | -0.1541 | 2.1432
7 | -0.022394 | -0.0056116 | 0.0224 | 0.0056139 | 6.4075e-06 | 2.3532e-06 | 0.034062 | 0.034062 | 0.034062 | 0.9783 | -0.15252 | 0.97858 | -0.15045 | 12.6154
8 | 0.0013616 | 0.00033777 | -0.0013616 | -0.00033781 | 8.4542e-09 | -3.6419e-08 | 0.0020703 | 0.0020703 | 0.0020703 | 0.97808 | -0.1541 | 0.97807 | -0.15415 | 0.76679
9 | -0.0224 | -0.0056139 | 0.02241 | 0.0056174 | 9.5248e-06 | 3.498e-06 | 0.034062 | 0.034062 | 0.034062 | 0.97858 | -0.15045 | 0.97901 | -0.14738 | 12.6154
10 | -0.0013052 | -0.00032711 | 0.0013052 | 0.00032685 | 5.1976e-08 | -2.5413e-07 | 0.0019692 | 0.0019691 | 0.0019692 | 0.98623 | -0.096105 | 0.98627 | -0.095817 | 0.72935
11 | -0.0013052 | -0.00032685 | 0.0013053 | 0.00032659 | 5.3815e-08 | -2.6317e-07 | 0.0019691 | 0.001969 | 0.0019691 | 0.98627 | -0.095817 | 0.98632 | -0.095518 | 0.72931
12 | 0.034744 | 0.0087374 | -0.034701 | -0.0087213 | 4.2721e-05 | 1.6112e-05 | 0.052361 | 0.052361 | 0.052361 | 0.98757 | -0.086686 | 0.98632 | -0.095518 | 19.3931
13 | -0.035628 | -0.0089589 | 0.035862 | 0.0090471 | 0.00023371 | 8.8215e-05 | 0.053693 | 0.053692 | 0.053693 | 0.98757 | -0.086686 | 0.99425 | -0.039923 | 19.8862
14 | 0.033396 | 0.0083947 | -0.033388 | -0.0083915 | 8.5726e-06 | 3.2281e-06 | 0.050392 | 0.050392 | 0.050392 | 0.98632 | -0.095518 | 0.98606 | -0.097362 | 18.6638
15 | -0.049733 | -0.012516 | 0.050011 | 0.012622 | 0.00027873 | 0.00010615 | 0.074449 | 0.074449 | 0.074449 | 0.99425 | -0.039923 | 1 | 0 | 27.5737
16 | 0.013871 | 0.0034688 | -0.013849 | -0.0034613 | 2.2225e-05 | 7.4778e-06 | 0.020757 | 0.020757 | 0.020757 | 0.99425 | -0.039923 | 0.99261 | -0.051562 | 7.6879
17 | 0.0022791 | 0.00057083 | -0.0022789 | -0.00057114 | 2.3448e-07 | -3.15e-07 | 0.0034392 | 0.0034393 | 0.0034393 | 0.98606 | -0.097362 | 0.98595 | -0.098106 | 1.2738
18 | 0.031109 | 0.0078207 | -0.031065 | -0.0078045 | 4.3059e-05 | 1.6163e-05 | 0.046953 | 0.046953 | 0.046953 | 0.98606 | -0.097362 | 0.98465 | -0.10731 | 17.3901
19 | 0.16749 | 0.042172 | -0.16738 | -0.04213 | 0.00010959 | 4.2002e-05 | 0.2493 | 0.2493 | 0.2493 | 1 | 0 | 0.99933 | -0.0046858 | 46.1663
20 | 0.0096765 | 0.0024157 | -0.0096752 | -0.0024153 | 1.3528e-06 | 3.871e-07 | 0.014503 | 0.014503 | 0.014503 | 0.99261 | -0.051562 | 0.99247 | -0.05258 | 5.3714
21 | 0.027942 | 0.0070216 | -0.02792 | -0.0070134 | 2.1986e-05 | 8.2051e-06 | 0.042232 | 0.042233 | 0.042233 | 0.98465 | -0.10731 | 0.98385 | -0.11297 | 15.6417
22 | 0.16569 | 0.041706 | -0.16556 | -0.041657 | 0.00012725 | 4.8765e-05 | 0.24678 | 0.24678 | 0.24678 | 0.99933 | -0.0046858 | 0.99853 | -0.01019 | 45.6995
23 | 0.0031371 | 0.00078609 | -0.0031369 | -0.00078618 | 1.6167e-07 | -8.9154e-08 | 0.0047034 | 0.0047035 | 0.0047035 | 0.99247 | -0.05258 | 0.99241 | -0.052953 | 1.742
24 | 0.0065381 | 0.0016292 | -0.0065266 | -0.0016273 | 1.1496e-05 | 1.947e-06 | 0.0097993 | 0.0098002 | 0.0098002 | 0.99247 | -0.05258 | 0.99066 | -0.06543 | 3.6297
25 | 0.02792 | 0.0070134 | -0.027881 | -0.006999 | 3.8613e-05 | 1.4411e-05 | 0.042233 | 0.042233 | 0.042233 | 0.98385 | -0.11297 | 0.98245 | -0.12293 | 15.6417
26 | 0.0077704 | 0.0019474 | -0.0077688 | -0.0019471 | 1.5786e-06 | 3.6041e-07 | 0.011579 | 0.01158 | 0.01158 | 0.99853 | -0.01019 | 0.99832 | -0.011657 | 4.2887
27 | 0.15779 | 0.03971 | -0.1577 | -0.039674 | 9.4489e-05 | 3.6199e-05 | 0.2352 | 0.2352 | 0.2352 | 0.99853 | -0.01019 | 0.99792 | -0.014482 | 43.5552
28 | 0.003694 | 0.00091922 | -0.0036893 | -0.00092058 | 4.77e-06 | -1.3601e-06 | 0.0055462 | 0.0055474 | 0.0055474 | 0.99066 | -0.06543 | 0.98935 | -0.074871 | 2.0546
29 | 0.0028326 | 0.00070803 | -0.0028307 | -0.00070944 | 1.8638e-06 | -1.4065e-06 | 0.004254 | 0.0042547 | 0.0042547 | 0.99066 | -0.06543 | 0.98999 | -0.070197 | 1.5758
30 | 0.025663 | 0.006443 | -0.025581 | -0.0064128 | 8.1482e-05 | 3.0249e-05 | 0.038873 | 0.038873 | 0.038873 | 0.98245 | -0.12293 | 0.97923 | -0.14585 | 14.3975
31 | 0.02354 | 0.0059013 | -0.023535 | -0.0058994 | 4.9706e-06 | 1.8335e-06 | 0.035772 | 0.035772 | 0.035772 | 0.97923 | -0.14585 | 0.97901 | -0.14738 | 13.2488
32 | 0.0013616 | 0.00033781 | -0.0013611 | -0.00033992 | 4.9136e-07 | -2.1149e-06 | 0.0020703 | 0.0020711 | 0.0020711 | 0.97807 | -0.15415 | 0.97771 | -0.15679 | 0.76709
33 | 0.0013611 | 0.00033992 | -0.0013609 | -0.00034107 | 2.6571e-07 | -1.1422e-06 | 0.0020711 | 0.0020716 | 0.0020716 | 0.97771 | -0.15679 | 0.97751 | -0.1582 | 0.76726
34 | -0.0050178 | -0.0012576 | 0.0050192 | 0.0012576 | 1.3544e-06 | 3.1661e-08 | 0.0075479 | 0.0075478 | 0.0075479 | 0.98923 | -0.075462 | 0.9895 | -0.073512 | 2.7955
35 | 0.01914 | 0.0048009 | -0.019105 | -0.0047883 | 3.5059e-05 | 1.2615e-05 | 0.028785 | 0.028785 | 0.028785 | 0.9895 | -0.073512 | 0.98763 | -0.086744 | 10.6611
36 | -0.024159 | -0.0060585 | 0.024193 | 0.0060707 | 3.3057e-05 | 1.2198e-05 | 0.036332 | 0.036332 | 0.036332 | 0.9895 | -0.073512 | 0.9909 | -0.063653 | 13.4564
37 | 0.0090305 | 0.0022633 | -0.0090266 | -0.0022623 | 3.8925e-06 | 1.0661e-06 | 0.013606 | 0.013606 | 0.013606 | 0.98763 | -0.086744 | 0.9872 | -0.089859 | 5.0392
38 | -0.033395 | -0.0083771 | 0.033429 | 0.0083897 | 3.3532e-05 | 1.2621e-05 | 0.050151 | 0.050151 | 0.050151 | 0.9909 | -0.063653 | 0.99193 | -0.05642 | 18.5746
39 | -0.043347 | -0.010875 | 0.043373 | 0.010885 | 2.5706e-05 | 9.7612e-06 | 0.065031 | 0.065031 | 0.065031 | 0.99193 | -0.05642 | 0.99253 | -0.052148 | 24.0854
40 | 0.0066845 | 0.0016751 | -0.0066818 | -0.0016746 | 2.7436e-06 | 4.9103e-07 | 0.010028 | 0.010028 | 0.010028 | 0.99193 | -0.05642 | 0.99151 | -0.059386 | 3.714
41 | -0.046434 | -0.011652 | 0.046458 | 0.011661 | 2.3647e-05 | 8.9937e-06 | 0.06962 | 0.06962 | 0.06962 | 0.99253 | -0.052148 | 0.99306 | -0.048481 | 25.7852
42 | 0.0036893 | 0.00092058 | -0.0036891 | -0.00092062 | 1.5198e-07 | -4.3176e-08 | 0.0055474 | 0.0055474 | 0.0055474 | 0.98935 | -0.074871 | 0.9893 | -0.075171 | 2.0546
43 | 0.0014447 | 0.00035813 | -0.0014445 | -0.00035922 | 2.748e-07 | -1.0929e-06 | 0.0021716 | 0.0021721 | 0.0021721 | 0.9893 | -0.075171 | 0.98911 | -0.07657 | 0.80447
44 | 0.0014445 | 0.00035922 | -0.0014438 | -0.00036185 | 6.6175e-07 | -2.6279e-06 | 0.0021721 | 0.0021731 | 0.0021731 | 0.98911 | -0.07657 | 0.98864 | -0.079906 | 0.80485
45 | -0.010448 | -0.0026186 | 0.010456 | 0.002621 | 7.8946e-06 | 2.3678e-06 | 0.015655 | 0.015654 | 0.015655 | 0.99313 | -0.04796 | 0.99391 | -0.042505 | 5.798
46 | -0.015383 | -0.0038558 | 0.015386 | 0.0038568 | 2.9141e-06 | 1.0067e-06 | 0.023031 | 0.023031 | 0.023031 | 0.99391 | -0.042505 | 0.9941 | -0.041138 | 8.5301
47 | 0.11979 | 0.030103 | -0.11971 | -0.030072 | 8.1585e-05 | 3.1168e-05 | 0.17934 | 0.17934 | 0.17934 | 0.9941 | -0.041138 | 0.9934 | -0.046035 | 33.2115
48 | -0.13518 | -0.03396 | 0.13533 | 0.034017 | 0.00014904 | 5.7022e-05 | 0.20237 | 0.20237 | 0.20237 | 0.9941 | -0.041138 | 0.99523 | -0.03322 | 37.4765
49 | 0.068396 | 0.01719 | -0.068292 | -0.01715 | 0.00010456 | 4.001e-05 | 0.10247 | 0.10247 | 0.10247 | 0.9934 | -0.046035 | 0.99184 | -0.057033 | 37.951
50 | 0.051317 | 0.012881 | -0.051299 | -0.012875 | 1.7429e-05 | 6.6422e-06 | 0.076874 | 0.076875 | 0.076875 | 0.9934 | -0.046035 | 0.99306 | -0.048481 | 28.472
51 | -0.14008 | -0.035207 | 0.14016 | 0.035237 | 7.9514e-05 | 3.0431e-05 | 0.20947 | 0.20947 | 0.20947 | 0.99523 | -0.03322 | 0.99582 | -0.029145 | 38.7915
52 | 0.062087 | 0.015595 | -0.06204 | -0.015577 | 4.7182e-05 | 1.8035e-05 | 0.09316 | 0.09316 | 0.09316 | 0.99184 | -0.057033 | 0.99106 | -0.062502 | 34.5036
53 | -0.14806 | -0.037219 | 0.14818 | 0.037264 | 0.0001176 | 4.5029e-05 | 0.22129 | 0.22129 | 0.22129 | 0.99582 | -0.029145 | 0.99663 | -0.023446 | 40.9791
54 | 0.0079058 | 0.0019814 | -0.007905 | -0.0019812 | 8.4219e-07 | 1.9812e-07 | 0.011813 | 0.011813 | 0.011813 | 0.99582 | -0.029145 | 0.99571 | -0.029914 | 4.3754
55 | 0.043441 | 0.010915 | -0.043388 | -0.010895 | 5.3148e-05 | 2.0184e-05 | 0.065234 | 0.065234 | 0.065234 | 0.99106 | -0.062502 | 0.98981 | -0.071306 | 24.1607
56 | 0.018599 | 0.0046623 | -0.018593 | -0.00466 | 6.3773e-06 | 2.284e-06 | 0.027926 | 0.027926 | 0.027926 | 0.99106 | -0.062502 | 0.99071 | -0.064978 | 10.343
57 | 0.016792 | 0.0042087 | -0.016788 | -0.0042073 | 4.0239e-06 | 1.4176e-06 | 0.025244 | 0.025244 | 0.025244 | 0.98981 | -0.071306 | 0.98956 | -0.073037 | 9.3496
58 | 0.026596 | 0.006686 | -0.026577 | -0.0066788 | 1.9432e-05 | 7.2238e-06 | 0.03999 | 0.03999 | 0.03999 | 0.98981 | -0.071306 | 0.98906 | -0.076555 | 14.8111
59 | 0.013617 | 0.0034129 | -0.013614 | -0.0034121 | 2.295e-06 | 7.6948e-07 | 0.020452 | 0.020452 | 0.020452 | 0.99071 | -0.064978 | 0.99054 | -0.066196 | 7.5748
60 | 0.0088291 | 0.0022128 | -0.0088277 | -0.0022124 | 1.39e-06 | 3.7165e-07 | 0.013263 | 0.013263 | 0.013263 | 0.99054 | -0.066196 | 0.99038 | -0.067333 | 4.9124
61 | 0.011601 | 0.0029074 | -0.0116 | -0.0029071 | 1.004e-06 | 3.1823e-07 | 0.017445 | 0.017445 | 0.017445 | 0.98956 | -0.073037 | 0.98948 | -0.073662 | 6.4611
62 | 0.026577 | 0.0066788 | -0.02644 | -0.0066279 | 0.00013668 | 5.082e-05 | 0.03999 | 0.039991 | 0.039991 | 0.98906 | -0.076555 | 0.98382 | -0.11369 | 14.8114
63 | 0.0057143 | 0.0014319 | -0.0057142 | -0.0014319 | 1.6663e-07 | 1.7642e-08 | 0.0085934 | 0.0085934 | 0.0085934 | 0.98948 | -0.073662 | 0.98945 | -0.073873 | 3.1827
64 | 0.022638 | 0.0056751 | -0.022624 | -0.0056698 | 1.4221e-05 | 5.2229e-06 | 0.03424 | 0.03424 | 0.03424 | 0.98382 | -0.11369 | 0.98318 | -0.11823 | 12.6816
65 | 0.0020897 | 0.00052351 | -0.0020896 | -0.00052369 | 1.0877e-07 | -1.8485e-07 | 0.0031425 | 0.0031426 | 0.0031426 | 0.98945 | -0.073873 | 0.98939 | -0.074249 | 1.1639
66 | -0.1542 | -0.038771 | 0.15439 | 0.038845 | 0.00019285 | 7.3868e-05 | 0.23027 | 0.23027 | 0.23027 | 0.99663 | -0.023446 | 0.99792 | -0.014482 | 42.6423
67 | -0.010788 | -0.0027026 | 0.01079 | 0.002703 | 1.3849e-06 | 4.2743e-07 | 0.016341 | 0.016341 | 0.016341 | 0.98236 | -0.12408 | 0.98249 | -0.12315 | 6.0523
68 | 0.0085862 | 0.0021506 | -0.0085834 | -0.0021499 | 2.7733e-06 | 7.3408e-07 | 0.013005 | 0.013005 | 0.013005 | 0.98236 | -0.12408 | 0.98203 | -0.12642 | 4.8168
69 | -0.014849 | -0.0037203 | 0.014858 | 0.0037234 | 9.0227e-06 | 3.108e-06 | 0.022489 | 0.022489 | 0.022489 | 0.98249 | -0.12315 | 0.9831 | -0.11876 | 8.3292
70 | 0.0085834 | 0.0021499 | -0.0085791 | -0.0021487 | 4.3408e-06 | 1.1495e-06 | 0.013005 | 0.013006 | 0.013006 | 0.98203 | -0.12642 | 0.98152 | -0.13008 | 4.8169
71 | -0.019236 | -0.0048208 | 0.019238 | 0.0048213 | 1.4193e-06 | 5.1185e-07 | 0.029116 | 0.029116 | 0.029116 | 0.9831 | -0.11876 | 0.98318 | -0.11823 | 10.7837
72 | 0.0038936 | 0.00097445 | -0.0038923 | -0.00097471 | 1.3298e-06 | -2.6139e-07 | 0.0059023 | 0.0059026 | 0.0059026 | 0.98152 | -0.13008 | 0.98117 | -0.13255 | 2.1861
73 | 0.0038923 | 0.00097471 | -0.0038921 | -0.00097473 | 1.0644e-07 | -2.0895e-08 | 0.0059026 | 0.0059026 | 0.0059026 | 0.98117 | -0.13255 | 0.98114 | -0.13275 | 2.1862
74 | 0.0038921 | 0.00097473 | -0.0038905 | -0.00097505 | 1.6378e-06 | -3.2101e-07 | 0.0059026 | 0.005903 | 0.005903 | 0.98114 | -0.13275 | 0.98072 | -0.13579 | 2.1863

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22246 | 0.055838

## res_load
| p_mw | q_mvar
0 | 0.0031892 | 0.00079928
1 | 0.0020051 | 0.00050254
2 | 0.0075574 | 0.0018941
3 | 0.0028296 | 0.00070916
4 | 0.0024428 | 0.00061223
5 | 0.0029601 | 0.00074186
6 | 0.0013052 | 0.00032711
7 | 0.00088364 | 0.00022146
8 | 0.0041625 | 0.0010432
9 | 0.0041723 | 0.0010457
10 | 0.0022789 | 0.00057114
11 | 0.0031239 | 0.00078292
12 | 0.0016929 | 0.00042427
13 | 0.0031369 | 0.00078618
14 | 0.0022183 | 0.00055596
15 | 0.0020409 | 0.00051151
16 | 0.0011253 | 0.00028202
17 | 0.0013609 | 0.00034107
18 | 0.0050178 | 0.0012576
19 | 0.010075 | 0.002525
20 | 0.0092025 | 0.0023064
21 | 0.0090266 | 0.0022623
22 | 0.0032344 | 0.00081061
23 | 0.0030613 | 0.00076722
24 | 0.0066818 | 0.0016746
25 | 0.0028307 | 0.00070944
26 | 0.0022444 | 0.00056249
27 | 0.0014438 | 0.00036185
28 | 0.010448 | 0.0026186
29 | 0.0049272 | 0.0012349
30 | 0.0047493 | 0.0011903
31 | 0.0062042 | 0.0015549
32 | 0.0048414 | 0.0012134
33 | 0.0049762 | 0.0012471
34 | 0.0047853 | 0.0011993
35 | 0.0088277 | 0.0022124
36 | 0.0051865 | 0.0012999
37 | 0.0058859 | 0.0014752
38 | 0.0038019 | 0.00095286
39 | 0.0036245 | 0.00090839
40 | 0.0020896 | 0.00052369
41 | 0.0060152 | 0.0015076
42 | 0.007905 | 0.0019812
43 | 0.0033061 | 0.0008286
44 | 0.0077688 | 0.0019471
45 | 0.0022023 | 0.00055195
46 | 0.004059 | 0.0010173
47 | 0.0043785 | 0.0010974
48 | 0.0046855 | 0.0011743
49 | 0.0033859 | 0.00084858
50 | 0.0038905 | 0.00097505

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1