## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-38_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-38_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-38_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-38_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-38_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-38_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1631-38_0_4_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1631-38_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1631-38_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1631-38_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1631-38_0_4_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1631-38_0_4_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_1631-38_0_4_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_1631-38_0_4_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_1631-38_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1631-38_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1631-38_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1631-38_0_4_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_1631-38_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1631-38_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1631-38_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1631-38_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1631-38_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1631-38_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1631-38_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1631-38_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1631-38_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1631-38_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1631-38_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_MV_13_0_node_128 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-38_0_4_load_0 | 0 | 0.046255 | 0.011593 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-38_0_4_load_1 | 1 | 0.029966 | 0.0075103 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-38_0_4_load_19 | 6 | 0.041059 | 0.01029 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-38_0_4_load_6 | 7 | 0.0051325 | 0.0012863 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-38_0_4_load_24 | 11 | 0.0096585 | 0.0024206 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-38_0_4_load_29 | 12 | 0.0042712 | 0.0010705 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-38_0_4_load_30 | 13 | 0.0037521 | 0.00094037 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-38_0_4_load_28 | 17 | 0.0042782 | 0.0010722 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-38_0_4_load_26 | 18 | 0.0055277 | 0.0013854 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-38_0_4_load_8 | 19 | 0.024471 | 0.0061331 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-38_0_4_load_16 | 20 | 0.0062153 | 0.0015577 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-38_0_4_load_14 | 21 | 0.0062701 | 0.0015714 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-38_0_4_load_17 | 24 | 0.0087568 | 0.0021947 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-38_0_4_load_18 | 25 | 0.007669 | 0.001922 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-38_0_4_load_21 | 27 | 0.013871 | 0.0034763 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-38_0_4_load_27 | 28 | 0.0091278 | 0.0022876 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-38_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-38_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.019301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-38_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.036765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-38_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.017089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-38_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.022455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-38_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.026357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-38_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.045013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-38_0_4_line_7 | NAYY 4x150 SE | 6 | 14 | 0.01502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1631-38_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.035407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-38_0_4_line_9 | NAYY 4x150 SE | 8 | 10 | 0.26973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-38_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.078285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-38_0_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.038472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-38_0_4_line_12 | NAYY 4x150 SE | 9 | 13 | 0.0097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-38_0_4_line_13 | NAYY 4x150 SE | 10 | 17 | 0.063753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-38_0_4_line_14 | NAYY 4x150 SE | 10 | 18 | 0.055697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-38_0_4_line_15 | NAYY 4x150 SE | 11 | 22 | 0.022274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-38_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.069045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1631-38_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.018517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-38_0_4_line_18 | NAYY 4x150 SE | 15 | 20 | 0.014017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-38_0_4_line_19 | NAYY 4x150 SE | 15 | 21 | 0.010951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-38_0_4_line_20 | NAYY 4x150 SE | 16 | 19 | 0.022666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-38_0_4_line_21 | NAYY 4x150 SE | 18 | 28 | 0.025694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-38_0_4_line_22 | NAYY 4x150 SE | 21 | 23 | 0.0048817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-38_0_4_line_23 | NAYY 4x150 SE | 22 | 27 | 0.052134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-38_0_4_line_24 | NAYY 4x150 SE | 23 | 24 | 0.01566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-38_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.030562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-38_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.013235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-38_0_4_line_27 | NAYY 4x150 SE | 26 | 27 | 0.011091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-38_0_4_trafo_12 | 0.25 MVA 20/0.4 kV | 29 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30
0 | 2718789.4861 | 1199874.9897 | 2718774.1907 | 1199858.4857
1 | 2718802.606 | 1199889.1462 | 2718789.4861 | 1199874.9897
2 | 2718749.2001 | 1199831.5205 | 2718774.1907 | 1199858.4857
3 | 2718802.606 | 1199889.1462 | 2718807.4637 | 1199894.947 | 2718808.3435 | 1199897.811 | 2718808.0306 | 1199901.2851 | 2718806.629 | 1199903.9815
4 | 2718749.2001 | 1199831.5205 | 2718745.3928 | 1199827.2751 | 2718762.0902 | 1199828.6301
5 | 2718806.629 | 1199903.9815 | 2718803.8107 | 1199906.3049 | 2718800.6855 | 1199907.2101 | 2718797.7738 | 1199906.9521 | 2718795.358 | 1199905.8811 | 2718793.4943 | 1199904.2428 | 2718785.4795 | 1199896.1304
6 | 2718762.0902 | 1199828.6301 | 2718766.6043 | 1199829.1201 | 2718770.9709 | 1199830.1299 | 2718802.7216 | 1199847.0769
7 | 2718774.9201 | 1199885.4488 | 2718776.4731 | 1199887.0142 | 2718785.4795 | 1199896.1304
8 | 2718735.1865 | 1199965.24 | 2718741.2675 | 1199962.759 | 2718751.7631 | 1199961.5444 | 2718767.0094 | 1199962.3257 | 2718765.0673 | 1199960.0298
9 | 2718710.0478 | 1200084.3723 | 2718723.1204 | 1200089.5135 | 2718741.6053 | 1200094.7734 | 2718751.1379 | 1200098.321 | 2718766.0848 | 1200106.8575 | 2718765.0666 | 1200096.4074 | 2718763.4549 | 1200082.4763 | 2718764.5637 | 1200080.7193 | 2718766.1649 | 1200079.4724 | 2718774.9774 | 1200077.8686 | 2718780.6319 | 1200076.1464 | 2718781.4864 | 1200074.5399 | 2718781.9663 | 1200073.382 | 2718781.2801 | 1200071.8895 | 2718780.1494 | 1200069.7765 | 2718773.2796 | 1200057.5533 | 2718771.0794 | 1200053.3065 | 2718770.8382 | 1200046.2854 | 2718770.4659 | 1200039.3507 | 2718770.4639 | 1200029.8771 | 2718772.9034 | 1200024.3882 | 2718771.963 | 1200019.2102 | 2718756.6251 | 1200000.0692 | 2718737.833 | 1199981.9047 | 2718735.7922 | 1199978.0614 | 2718737.2564 | 1199976.0446 | 2718751.3511 | 1199978.4374 | 2718755.5854 | 1199977.2874 | 2718758.128 | 1199973.891 | 2718743.0014 | 1199968.2419 | 2718735.1865 | 1199965.24
10 | 2718735.1865 | 1199965.24 | 2718716.671 | 1199961.5028 | 2718703.874 | 1199958.1906 | 2718680.9656 | 1199949.7851 | 2718672.6701 | 1199945.6729 | 2718664.3009 | 1199939.1353 | 2718663.0103 | 1199937.7457
11 | 2718765.0673 | 1199960.0298 | 2718757.5702 | 1199957.1343 | 2718749.1106 | 1199956.2989 | 2718736.1455 | 1199953.3948 | 2718728.8858 | 1199948.5137
12 | 2718757.7903 | 1199953.7251 | 2718762.6805 | 1199957.1247 | 2718765.0673 | 1199960.0298
13 | 2718710.0478 | 1200084.3723 | 2718693.5203 | 1200078.3396 | 2718674.2307 | 1200072.5634 | 2718653.9833 | 1200069.0033 | 2718648.5957 | 1200068.0844
14 | 2718710.0478 | 1200084.3723 | 2718702.6872 | 1200077.2987 | 2718696.7792 | 1200073.7676 | 2718689.9656 | 1200069.8183 | 2718682.5474 | 1200062.9549 | 2718669.8786 | 1200052.8181 | 2718667.0175 | 1200049.4773
15 | 2718649.5866 | 1199920.007 | 2718659.9241 | 1199934.4228 | 2718663.0103 | 1199937.7457
16 | 2718743.7861 | 1199908.0912 | 2718752.266 | 1199905.6134 | 2718758.3817 | 1199905.9797 | 2718763.8183 | 1199907.5666 | 2718769.6359 | 1199910.2842 | 2718775.4005 | 1199911.0771 | 2718762.415 | 1199898.8546 | 2718770.3082 | 1199889.8826 | 2718772.4056 | 1199887.8117 | 2718774.9201 | 1199885.4488
17 | 2718759.0421 | 1199880.4296 | 2718762.0704 | 1199879.0332 | 2718764.9171 | 1199878.734 | 2718769.1416 | 1199879.9967 | 2718771.7325 | 1199882.2164 | 2718774.9201 | 1199885.4488
18 | 2718743.7861 | 1199908.0912 | 2718748.4922 | 1199912.7103 | 2718755.3812 | 1199915.5493
19 | 2718743.7861 | 1199908.0912 | 2718733.0933 | 1199910.4538
20 | 2718759.0421 | 1199880.4296 | 2718751.6479 | 1199876.1796 | 2718737.5237 | 1199876.7854
21 | 2718655.4616 | 1200026.7906 | 2718657.5085 | 1200032.6244 | 2718660.5844 | 1200037.2667 | 2718664.3858 | 1200046.4044 | 2718667.0175 | 1200049.4773
22 | 2718728.3478 | 1199911.5982 | 2718732.1974 | 1199910.6518 | 2718733.0933 | 1199910.4538
23 | 2718649.5866 | 1199920.007 | 2718652.159 | 1199918.9462 | 2718658.3122 | 1199920.4917 | 2718666.0797 | 1199920.1345 | 2718669.5683 | 1199919.3365 | 2718677.8768 | 1199920.1132 | 2718685.4698 | 1199920.8756 | 2718699.4451 | 1199927.978
24 | 2718728.3478 | 1199911.5982 | 2718725.1445 | 1199913.3692 | 2718722.5417 | 1199915.9638 | 2718717.4411 | 1199922.5432
25 | 2718699.8588 | 1199900.8022 | 2718704.8641 | 1199903.3924 | 2718708.7212 | 1199904.7478 | 2718717.0432 | 1199907.1482 | 2718724.274 | 1199910.8056 | 2718728.3478 | 1199911.5982
26 | 2718709.3324 | 1199933.0028 | 2718717.4411 | 1199922.5432
27 | 2718709.3324 | 1199933.0028 | 2718699.4451 | 1199927.978

## bus_geodata
| x | y | coords
0 | 2718789.4861 | 1199874.9897
1 | 2718774.1907 | 1199858.4857
2 | 2718802.606 | 1199889.1462
3 | 2718749.2001 | 1199831.5205
4 | 2718806.629 | 1199903.9815
5 | 2718762.0902 | 1199828.6301
6 | 2718785.4795 | 1199896.1304
7 | 2718802.7216 | 1199847.0769
8 | 2718735.1865 | 1199965.24
9 | 2718765.0673 | 1199960.0298
10 | 2718710.0478 | 1200084.3722
11 | 2718663.0103 | 1199937.7457
12 | 2718728.8858 | 1199948.5137
13 | 2718757.7903 | 1199953.7251
14 | 2718774.9201 | 1199885.4488
15 | 2718743.7861 | 1199908.0912
16 | 2718759.0421 | 1199880.4296
17 | 2718648.5957 | 1200068.0844
18 | 2718667.0175 | 1200049.4773
19 | 2718737.5237 | 1199876.7854
20 | 2718755.3812 | 1199915.5493
21 | 2718733.0933 | 1199910.4538
22 | 2718649.5866 | 1199920.007
23 | 2718728.3478 | 1199911.5982
24 | 2718717.4411 | 1199922.5432
25 | 2718699.8588 | 1199900.8022
26 | 2718709.3324 | 1199933.0028
27 | 2718699.4451 | 1199927.978
28 | 2718655.4616 | 1200026.7906
29 | 2718755.3812 | 1199915.5493

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98395 | -0.11256 | 0.046255 | 0.011593
1 | 0.9828 | -0.12071 | 0.029966 | 0.0075103
2 | 0.98622 | -0.096406 | 0 | 0
3 | 0.98253 | -0.12266 | 0 | 0
4 | 0.98824 | -0.082166 | 0 | 0
5 | 0.98236 | -0.12386 | 0 | 0
6 | 0.99135 | -0.060318 | 0.041059 | 0.01029
7 | 0.98203 | -0.12625 | 0.0051325 | 0.0012863
8 | 0.98826 | -0.08211 | 0 | 0
9 | 0.98785 | -0.085016 | 0 | 0
10 | 0.98083 | -0.13477 | 0 | 0
11 | 0.99132 | -0.060571 | 0.0096585 | 0.0024206
12 | 0.98761 | -0.086698 | 0.0042712 | 0.0010705
13 | 0.9878 | -0.085389 | 0.0037521 | 0.00094037
14 | 0.99268 | -0.050993 | 0 | 0
15 | 1 | 0 | -0.22964 | -0.057681
16 | 0.99202 | -0.055586 | 0 | 0
17 | 0.98043 | -0.1376 | 0.0042782 | 0.0010722
18 | 0.97964 | -0.14325 | 0.0055277 | 0.0013854
19 | 0.99123 | -0.061216 | 0.024471 | 0.0061331
20 | 0.99988 | -0.00086968 | 0.0062153 | 0.0015577
21 | 0.99885 | -0.008015 | 0.0062701 | 0.0015714
22 | 0.9925 | -0.052285 | 0 | 0
23 | 0.99838 | -0.011288 | 0 | 0
24 | 0.99704 | -0.0206 | 0.0087568 | 0.0021947
25 | 0.99804 | -0.013636 | 0.007669 | 0.001922
26 | 0.99607 | -0.027323 | 0 | 0
27 | 0.99527 | -0.032967 | 0.013871 | 0.0034763
28 | 0.9793 | -0.14569 | 0.0091278 | 0.0022876
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.035143 | 0.0088118 | -0.035103 | -0.0087968 | 3.9661e-05 | 1.4969e-05 | 0.053147 | 0.053147 | 0.053147 | 0.98395 | -0.11256 | 0.9828 | -0.12071 | 19.6842
1 | -0.081398 | -0.020404 | 0.08158 | 0.020474 | 0.00018251 | 6.9949e-05 | 0.1231 | 0.1231 | 0.1231 | 0.98395 | -0.11256 | 0.98622 | -0.096406 | 45.5921
2 | 0.0051365 | 0.0012865 | -0.0051351 | -0.0012865 | 1.3874e-06 | 6.7872e-08 | 0.0077766 | 0.0077768 | 0.0077768 | 0.9828 | -0.12071 | 0.98253 | -0.12266 | 2.8803
3 | -0.08158 | -0.020474 | 0.081742 | 0.020536 | 0.00016159 | 6.1931e-05 | 0.1231 | 0.1231 | 0.1231 | 0.98622 | -0.096406 | 0.98824 | -0.082166 | 45.5921
4 | 0.0051351 | 0.0012865 | -0.0051342 | -0.0012864 | 8.4742e-07 | 4.1593e-08 | 0.0077768 | 0.0077769 | 0.0077769 | 0.98253 | -0.12266 | 0.98236 | -0.12386 | 2.8803
5 | -0.081742 | -0.020536 | 0.081991 | 0.020632 | 0.00024922 | 9.5516e-05 | 0.1231 | 0.1231 | 0.1231 | 0.98824 | -0.082166 | 0.99135 | -0.060318 | 45.592
6 | 0.0051342 | 0.0012864 | -0.0051325 | -0.0012863 | 1.6988e-06 | 8.3695e-08 | 0.0077769 | 0.0077771 | 0.0077771 | 0.98236 | -0.12386 | 0.98203 | -0.12625 | 2.8804
7 | -0.12305 | -0.030922 | 0.12321 | 0.030983 | 0.00015991 | 6.1117e-05 | 0.18473 | 0.18473 | 0.18473 | 0.99135 | -0.060318 | 0.99268 | -0.050993 | 34.2088
8 | 0.0080277 | 0.0020115 | -0.0080245 | -0.0020107 | 3.2279e-06 | 7.8803e-07 | 0.012087 | 0.012087 | 0.012087 | 0.98826 | -0.08211 | 0.98785 | -0.085016 | 4.4768
9 | 0.019095 | 0.004802 | -0.018956 | -0.0047519 | 0.00013919 | 5.0106e-05 | 0.028757 | 0.028758 | 0.028758 | 0.98826 | -0.08211 | 0.98083 | -0.13477 | 10.6512
10 | -0.027123 | -0.0068134 | 0.027204 | 0.0068438 | 8.1493e-05 | 3.0337e-05 | 0.040844 | 0.040844 | 0.040844 | 0.98826 | -0.08211 | 0.99132 | -0.060571 | 15.1275
11 | 0.0042722 | 0.0010704 | -0.0042712 | -0.0010705 | 9.9416e-07 | -1.1004e-07 | 0.0064351 | 0.0064353 | 0.0064353 | 0.98785 | -0.085016 | 0.98761 | -0.086698 | 2.3835
12 | 0.0037523 | 0.00094032 | -0.0037521 | -0.00094037 | 1.9337e-07 | -4.9804e-08 | 0.0056522 | 0.0056522 | 0.0056522 | 0.98785 | -0.085016 | 0.9878 | -0.085389 | 2.0934
13 | 0.0042799 | 0.0010721 | -0.0042782 | -0.0010722 | 1.6772e-06 | -1.5924e-07 | 0.0064929 | 0.0064931 | 0.0064931 | 0.98083 | -0.13477 | 0.98043 | -0.1376 | 2.4049
14 | 0.014676 | 0.0036798 | -0.014659 | -0.0036739 | 1.723e-05 | 5.9247e-06 | 0.022265 | 0.022266 | 0.022266 | 0.98083 | -0.13477 | 0.97964 | -0.14325 | 8.2465
15 | -0.036863 | -0.0092644 | 0.036905 | 0.0092805 | 4.2568e-05 | 1.6085e-05 | 0.055342 | 0.055341 | 0.055342 | 0.99132 | -0.060571 | 0.9925 | -0.052285 | 20.4969
16 | -0.14772 | -0.037129 | 0.14877 | 0.037534 | 0.0010566 | 0.00040457 | 0.22146 | 0.22146 | 0.22146 | 0.99268 | -0.050993 | 1 | 0 | 41.0117
17 | 0.024506 | 0.0061459 | -0.02449 | -0.0061401 | 1.5593e-05 | 5.7582e-06 | 0.036736 | 0.036736 | 0.036736 | 0.99268 | -0.050993 | 0.99202 | -0.055586 | 13.6059
18 | 0.006216 | 0.0015578 | -0.0062153 | -0.0015577 | 7.483e-07 | 1.0394e-07 | 0.0092495 | 0.0092496 | 0.0092496 | 1 | 0 | 0.99988 | -0.00086968 | 3.4258
19 | 0.073853 | 0.01859 | -0.07377 | -0.018558 | 8.2566e-05 | 3.1613e-05 | 0.10992 | 0.10992 | 0.10992 | 1 | 0 | 0.99885 | -0.008015 | 40.7121
20 | 0.02449 | 0.0061401 | -0.024471 | -0.0061331 | 1.9087e-05 | 7.0487e-06 | 0.036736 | 0.036736 | 0.036736 | 0.99202 | -0.055586 | 0.99123 | -0.061216 | 13.6059
21 | 0.0091309 | 0.0022885 | -0.0091278 | -0.0022876 | 3.0841e-06 | 8.6281e-07 | 0.013869 | 0.013869 | 0.013869 | 0.97964 | -0.14325 | 0.9793 | -0.14569 | 5.1368
22 | 0.0675 | 0.016987 | -0.067469 | -0.016975 | 3.0817e-05 | 1.1789e-05 | 0.10058 | 0.10058 | 0.10058 | 0.99885 | -0.008015 | 0.99838 | -0.011288 | 37.2526
23 | -0.036905 | -0.0092805 | 0.037005 | 0.0093182 | 9.9633e-05 | 3.7645e-05 | 0.055341 | 0.055341 | 0.055341 | 0.9925 | -0.052285 | 0.99527 | -0.032967 | 20.4968
24 | 0.059798 | 0.015052 | -0.05972 | -0.015023 | 7.7663e-05 | 2.9666e-05 | 0.089148 | 0.089148 | 0.089148 | 0.99838 | -0.011288 | 0.99704 | -0.0206 | 33.0178
25 | 0.0076715 | 0.0019226 | -0.007669 | -0.001922 | 2.4932e-06 | 5.594e-07 | 0.011434 | 0.011434 | 0.011434 | 0.99838 | -0.011288 | 0.99804 | -0.013636 | 4.2348
26 | 0.050963 | 0.012828 | -0.050916 | -0.01281 | 4.78e-05 | 1.8212e-05 | 0.076079 | 0.076079 | 0.076079 | 0.99704 | -0.0206 | 0.99607 | -0.027323 | 28.1775
27 | 0.050916 | 0.01281 | -0.050876 | -0.012794 | 4.0058e-05 | 1.5262e-05 | 0.076079 | 0.076079 | 0.076079 | 0.99607 | -0.027323 | 0.99527 | -0.032967 | 28.1775

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22964 | 0.057681

## res_load
| p_mw | q_mvar
0 | 0.046255 | 0.011593
1 | 0.029966 | 0.0075103
2 | 0.041059 | 0.01029
3 | 0.0051325 | 0.0012863
4 | 0.0096585 | 0.0024206
5 | 0.0042712 | 0.0010705
6 | 0.0037521 | 0.00094037
7 | 0.0042782 | 0.0010722
8 | 0.0055277 | 0.0013854
9 | 0.024471 | 0.0061331
10 | 0.0062153 | 0.0015577
11 | 0.0062701 | 0.0015714
12 | 0.0087568 | 0.0021947
13 | 0.007669 | 0.001922
14 | 0.013871 | 0.0034763
15 | 0.0091278 | 0.0022876

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1