## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-3_0_3_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_1631-3_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1631-3_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1631-3_0_3_node_149 | 0.4 | n |  | TRUE
7 | bus_LV_1631-3_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1631-3_0_3_node_148 | 0.4 | n |  | TRUE
9 | bus_LV_1631-3_0_3_node_146 | 0.4 | n |  | TRUE
10 | bus_LV_1631-3_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1631-3_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1631-3_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1631-3_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-3_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1631-3_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1631-3_0_3_node_151 | 0.4 | n |  | TRUE
17 | bus_LV_1631-3_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1631-3_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1631-3_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1631-3_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1631-3_0_3_node_155 | 0.4 | n |  | TRUE
22 | bus_LV_1631-3_0_3_node_145 | 0.4 | n |  | TRUE
23 | bus_LV_1631-3_0_3_node_147 | 0.4 | n |  | TRUE
24 | bus_LV_1631-3_0_3_node_171 | 0.4 | n |  | TRUE
25 | bus_LV_1631-3_0_3_node_150 | 0.4 | n |  | TRUE
26 | bus_LV_1631-3_0_3_node_152 | 0.4 | n |  | TRUE
27 | bus_LV_1631-3_0_3_node_153 | 0.4 | n |  | TRUE
28 | bus_LV_1631-3_0_3_node_154 | 0.4 | n |  | TRUE
29 | bus_LV_1631-3_0_3_node_169 | 0.4 | n |  | TRUE
30 | bus_LV_1631-3_0_3_node_170 | 0.4 | n |  | TRUE
31 | bus_LV_1631-3_0_3_node_172 | 0.4 | n |  | TRUE
32 | bus_MV_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-3_0_3_load_0 | 0 | 0.00059126 | 0.00014818 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-3_0_3_load_2 | 2 | 0.00039775 | 9.9687e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-3_0_3_load_4 | 5 | 0.0010143 | 0.0002542 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-3_0_3_load_148 | 8 | 0.0011627 | 0.0002914 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-3_0_3_load_146 | 9 | 0.0049554 | 0.001242 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-3_0_3_load_6 | 10 | 0.00036187 | 9.0693e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-3_0_3_load_7 | 11 | 0.00051635 | 0.00012941 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-3_0_3_load_9 | 13 | 0.002444 | 0.00061252 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-3_0_3_load_151 | 16 | 0.00048981 | 0.00012276 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-3_0_3_load_13 | 17 | 0.0010849 | 0.0002719 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-3_0_3_load_14 | 18 | 0.00049918 | 0.00012511 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-3_0_3_load_15 | 19 | 0.00071946 | 0.00018031 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-3_0_3_load_145 | 22 | 0.00091076 | 0.00022826 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-3_0_3_load_171 | 24 | 0.0004566 | 0.00011443 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-3_0_3_load_150 | 25 | 0.00021801 | 5.4638e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-3_0_3_load_152 | 26 | 0.00031951 | 8.0077e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-3_0_3_load_154 | 28 | 0.0002852 | 7.1478e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-3_0_3_load_172 | 31 | 0.00049242 | 0.00012341 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.32305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.011761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-3_0_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.38197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-3_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.13332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-3_0_3_line_4 | NAYY 4x150 SE | 3 | 13 | 0.039837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-3_0_3_line_5 | NAYY 4x150 SE | 4 | 5 | 0.014462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-3_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.022151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-3_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0098159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-3_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.045942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-3_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.0044983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-3_0_3_line_10 | NAYY 4x150 SE | 9 | 22 | 0.012857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-3_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.19647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-3_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.012074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-3_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.0085688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-3_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.039352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-3_0_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.036731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-3_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.43157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-3_0_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.025763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-3_0_3_line_18 | NAYY 4x150 SE | 14 | 18 | 0.0026821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-3_0_3_line_19 | NAYY 4x150 SE | 15 | 19 | 0.00038671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-3_0_3_line_20 | NAYY 4x150 SE | 17 | 20 | 0.1941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-3_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.80938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-3_0_3_line_22 | NAYY 4x150 SE | 21 | 28 | 0.098104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-3_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.025481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-3_0_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.36729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-3_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 1.0242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-3_0_3_line_26 | NAYY 4x150 SE | 24 | 29 | 0.36027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-3_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.031819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-3_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.058246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-3_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.016229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-3_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.07772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-3_0_3_trafo_0 | 0.25 MVA 20/0.4 kV | 32 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30
0 | 2729946.829 | 1198220.4528 | 2729938.3625 | 1198218.812 | 2729932.6725 | 1198217.365 | 2729925.7117 | 1198213.0438 | 2729919.2276 | 1198206.0753 | 2729904.9153 | 1198187.728 | 2729886.7833 | 1198166.351 | 2729849.8053 | 1198137.8481 | 2729837.3968 | 1198121.277 | 2729828.8483 | 1198114.9865 | 2729813.3839 | 1198107.2114 | 2729803.2955 | 1198105.8692 | 2729786.4492 | 1198107.6937 | 2729762.5099 | 1198106.7178 | 2729737.5958 | 1198106.0766 | 2729720.0861 | 1198107.9314 | 2729699.1076 | 1198114.1032 | 2729682.5601 | 1198119.0147 | 2729676.3333 | 1198122.9827 | 2729673.6727 | 1198126.1158
1 | 2729666.06 | 1198135.0803 | 2729673.6727 | 1198126.1158
2 | 2729771.6696 | 1197756.9263 | 2729673.6727 | 1198126.1158
3 | 2729829.189 | 1198213.5918 | 2729832.052 | 1198212.9646 | 2729835.4877 | 1198212.9725 | 2729841.1677 | 1198213.8299 | 2729847.1837 | 1198216.7517 | 2729855.4374 | 1198223.2804 | 2729870.9159 | 1198237.0494 | 2729875.2137 | 1198239.4557 | 2729879.5146 | 1198240.3165 | 2729883.99 | 1198239.1128 | 2729888.1183 | 1198236.7006 | 2729896.6404 | 1198227.0228 | 2729904.4548 | 1198222.5669 | 2729908.7158 | 1198221.4142 | 2729913.3204 | 1198221.2697 | 2729927.2468 | 1198223.0292 | 2729936.9456 | 1198223.0067 | 2729946.829 | 1198220.4528
4 | 2729771.6696 | 1197756.9263 | 2729761.2926 | 1197744.2914 | 2729746.2989 | 1197726.2131
5 | 2729829.189 | 1198213.5918 | 2729821.3653 | 1198225.7553
6 | 2729809.3823 | 1198244.3853 | 2729821.3653 | 1198225.7553
7 | 2729809.3823 | 1198244.3853 | 2729800.3645 | 1198240.5082
8 | 2729764.7901 | 1198215.6953 | 2729766.5902 | 1198222.2616 | 2729773.0578 | 1198227.8952 | 2729783.2277 | 1198234.9436 | 2729787.9796 | 1198237.1373 | 2729794.7544 | 1198238.0963 | 2729800.3645 | 1198240.5082
9 | 2729764.7901 | 1198215.6953 | 2729760.3017 | 1198215.3976
10 | 2729747.8003 | 1198218.2921 | 2729753.6414 | 1198216.5317 | 2729760.3017 | 1198215.3976 | 2729760.3017 | 1198215.3976
11 | 2729584.6689 | 1197607.3731 | 2729586.6199 | 1197609.3108 | 2729591.6301 | 1197611.9214 | 2729595.4074 | 1197613.0597 | 2729602.4778 | 1197616.5823 | 2729615.6468 | 1197620.6598 | 2729619.4081 | 1197622.8875 | 2729633.2913 | 1197634.4306 | 2729638.8651 | 1197637.3982 | 2729641.3223 | 1197640.0313 | 2729642.8274 | 1197642.9995 | 2729647.9235 | 1197646.913 | 2729658.7571 | 1197653.275 | 2729669.5917 | 1197662.3948 | 2729677.6795 | 1197671.3437 | 2729684.5595 | 1197679.4213 | 2729694.7732 | 1197688.3608 | 2729701.8262 | 1197699.7003 | 2729706.8352 | 1197704.1123 | 2729714.8025 | 1197709.1334 | 2729731.7523 | 1197715.5728 | 2729736.4068 | 1197717.364 | 2729738.8737 | 1197718.8409 | 2729740.3988 | 1197720.0281
12 | 2729578.2474 | 1197597.3202 | 2729581.8241 | 1197604.5477 | 2729584.6689 | 1197607.3731
13 | 2729746.2989 | 1197726.2131 | 2729744.9138 | 1197724.543 | 2729741.5186 | 1197720.8999 | 2729740.3988 | 1197720.0281
14 | 2729578.2474 | 1197597.3202 | 2729580.571 | 1197596.9814 | 2729582.3128 | 1197594.6618 | 2729582.7656 | 1197589.9458 | 2729581.7588 | 1197584.0195 | 2729578.7266 | 1197576.9817 | 2729573.0565 | 1197568.9638 | 2729572.8841 | 1197566.0245 | 2729574.3189 | 1197563.4536
15 | 2729551.6924 | 1197577.0293 | 2729560.227 | 1197578.0372 | 2729566.5175 | 1197580.9869 | 2729570.6417 | 1197586.158 | 2729574.0167 | 1197595.3048 | 2729576.1346 | 1197597.0742 | 2729578.2474 | 1197597.3202
16 | 2729746.2989 | 1197726.2131 | 2730082.271 | 1197455.3273
17 | 2729574.3189 | 1197563.4536 | 2729551.9516 | 1197550.6703
18 | 2729574.3189 | 1197563.4536 | 2729576.9966 | 1197563.3004
19 | 2729551.3069 | 1197576.9988 | 2729551.6924 | 1197577.0293
20 | 2729432.4369 | 1197403.2248 | 2729435.56 | 1197407.4845 | 2729439.0111 | 1197411.0286 | 2729446.3381 | 1197415.7353 | 2729455.8171 | 1197422.0453 | 2729470.2939 | 1197431.1991 | 2729479.6359 | 1197439.9636 | 2729485.6615 | 1197448.1115 | 2729493.7409 | 1197461.341 | 2729500.7332 | 1197475.1585 | 2729503.0906 | 1197478.5344 | 2729513.695 | 1197487.4042 | 2729517.1785 | 1197491.2048 | 2729536.9742 | 1197524.915 | 2729543.0749 | 1197533.109 | 2729547.4005 | 1197538.1287 | 2729548.4622 | 1197541.521 | 2729548.6872 | 1197545.5512 | 2729549.8556 | 1197547.8894 | 2729551.9516 | 1197550.6703
21 | 2729432.4369 | 1197403.2248 | 2728653.7094 | 1197182.5731
22 | 2728653.7094 | 1197182.5731 | 2728661.9277 | 1197162.9127 | 2728677.2329 | 1197139.691 | 2728679.2958 | 1197129.8835 | 2728684.1054 | 1197120.2575 | 2728689.9558 | 1197111.4878 | 2728703.0281 | 1197099.6157
23 | 2729722.9433 | 1198223.3486 | 2729735.2289 | 1198222.0809 | 2729747.8003 | 1198218.2921
24 | 2729722.9433 | 1198223.3486 | 2729572.3813 | 1198558.3626
25 | 2729572.3813 | 1198558.3626 | 2729858.4169 | 1199541.8138
26 | 2729572.3813 | 1198558.3626 | 2729549.0016 | 1198534.1262 | 2729539.5626 | 1198530.9748 | 2729528.1235 | 1198530.8269 | 2729518.0518 | 1198533.6664 | 2729481.6563 | 1198548.9675 | 2729464.4545 | 1198555.311 | 2729449.0689 | 1198558.3468 | 2729441.3393 | 1198558.9243 | 2729434.0113 | 1198559.9553 | 2729424.0587 | 1198561.8746 | 2729394.8176 | 1198563.0759 | 2729385.7371 | 1198562.3677 | 2729379.1863 | 1198563.0376 | 2729373.0059 | 1198565.25 | 2729366.6738 | 1198569.8943 | 2729362.7486 | 1198571.7441 | 2729353.4851 | 1198574.9127 | 2729337.991 | 1198578.0355 | 2729330.2813 | 1198580.515 | 2729318.3979 | 1198581.8923 | 2729308.8072 | 1198581.1732 | 2729301.9165 | 1198583.4704 | 2729283.4194 | 1198597.937 | 2729275.3005 | 1198604.889 | 2729266.2404 | 1198612.7435 | 2729262.4703 | 1198616.9319 | 2729258.261 | 1198627.3377 | 2729256.2775 | 1198629.2296 | 2729254.3293 | 1198629.4877 | 2729251.6578 | 1198628.6737
27 | 2728748.3985 | 1197063.0979 | 2728767.8987 | 1197037.9542
28 | 2728748.3985 | 1197063.0979 | 2728738.7973 | 1197071.2418 | 2728703.0281 | 1197099.6157
29 | 2729253.6593 | 1198612.5713 | 2729251.6578 | 1198628.6737
30 | 2729253.6593 | 1198612.5713 | 2729244.8247 | 1198615.6382 | 2729235.0865 | 1198617.1622 | 2729213.0916 | 1198618.3099 | 2729199.4529 | 1198616.6694 | 2729194.9903 | 1198615.1941 | 2729189.5024 | 1198613.2184 | 2729186.9594 | 1198607.8705 | 2729186.1843 | 1198601.4377

## bus_geodata
| x | y | coords
0 | 2729673.6727 | 1198126.1158
1 | 2729946.829 | 1198220.4528
2 | 2729666.06 | 1198135.0803
3 | 2729771.6696 | 1197756.9262
4 | 2729829.189 | 1198213.5918
5 | 2729821.3653 | 1198225.7553
6 | 2729809.3823 | 1198244.3853
7 | 2729764.7901 | 1198215.6953
8 | 2729800.3645 | 1198240.5082
9 | 2729760.3017 | 1198215.3976
10 | 2729584.6689 | 1197607.3731
11 | 2729740.3988 | 1197720.0281
12 | 2729578.2474 | 1197597.3202
13 | 2729746.2989 | 1197726.2131
14 | 2729574.3189 | 1197563.4536
15 | 2729551.6924 | 1197577.0293
16 | 2730082.271 | 1197455.3273
17 | 2729551.9516 | 1197550.6703
18 | 2729576.9966 | 1197563.3004
19 | 2729551.3069 | 1197576.9988
20 | 2729432.4369 | 1197403.2248
21 | 2728653.7094 | 1197182.5731
22 | 2729747.8003 | 1198218.2921
23 | 2729722.9433 | 1198223.3486
24 | 2729572.3813 | 1198558.3626
25 | 2729858.4169 | 1199541.8138
26 | 2728767.8987 | 1197037.9542
27 | 2728748.3985 | 1197063.0979
28 | 2728703.0281 | 1197099.6157
29 | 2729251.6578 | 1198628.6737
30 | 2729253.6593 | 1198612.5713
31 | 2729186.1843 | 1198601.4377
32 | 2729673.6727 | 1198126.1158

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.017223 | -0.0040661
1 | 0.99573 | -0.030534 | 0 | 0
2 | 0.99999 | -4.6755e-05 | 0.00039775 | 9.9687e-05
3 | 0.99633 | -0.02652 | 0 | 0
4 | 0.99397 | -0.043181 | 0 | 0
5 | 0.99378 | -0.044555 | 0.0010143 | 0.0002542
6 | 0.99352 | -0.046432 | 0 | 0
7 | 0.99294 | -0.050619 | 0 | 0
8 | 0.99341 | -0.047264 | 0.0011627 | 0.0002914
9 | 0.9929 | -0.050948 | 0.0049554 | 0.001242
10 | 0.99498 | -0.036369 | 0.00036187 | 9.0693e-05
11 | 0.9959 | -0.029628 | 0.00051635 | 0.00012941
12 | 0.99493 | -0.036738 | 0 | 0
13 | 0.99595 | -0.029289 | 0.002444 | 0.00061252
14 | 0.99481 | -0.037654 | 0 | 0
15 | 0.99489 | -0.037005 | 0 | 0
16 | 0.99564 | -0.031508 | 0.00048981 | 0.00012276
17 | 0.99475 | -0.038124 | 0.0010849 | 0.0002719
18 | 0.99481 | -0.037668 | 0.00049918 | 0.00012511
19 | 0.99489 | -0.037008 | 0.00071946 | 0.00018031
20 | 0.99458 | -0.039515 | 0 | 0
21 | 0.99388 | -0.044925 | 0 | 0
22 | 0.99286 | -0.051242 | 0.00091076 | 0.00022826
23 | 0.99282 | -0.051589 | 0 | 0
24 | 0.9922 | -0.056528 | 0.0004566 | 0.00011443
25 | 0.99189 | -0.059305 | 0.00021801 | 5.4638e-05
26 | 0.99375 | -0.045833 | 0.00031951 | 8.0077e-05
27 | 0.99377 | -0.04573 | 0 | 0
28 | 0.99379 | -0.045538 | 0.0002852 | 7.1478e-05
29 | 0.99195 | -0.058423 | 0 | 0
30 | 0.99194 | -0.058506 | 0 | 0
31 | 0.99188 | -0.058897 | 0.00049242 | 0.00012341
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0092737 | 0.0023012 | -0.0092353 | -0.0022906 | 3.8346e-05 | 1.0528e-05 | 0.013791 | 0.013793 | 0.013793 | 1 | 0 | 0.99573 | -0.030534 | 5.1084
1 | 0.00039776 | 9.9533e-05 | -0.00039775 | -9.9687e-05 | 2.5706e-09 | -1.533e-07 | 0.00059182 | 0.00059187 | 0.00059187 | 1 | 0 | 0.99999 | -4.6755e-05 | 0.21921
2 | 0.0067511 | 0.0016654 | -0.0067271 | -0.0016611 | 2.4014e-05 | 4.2431e-06 | 0.010036 | 0.010038 | 0.010038 | 1 | 0 | 0.99633 | -0.02652 | 3.7179
3 | 0.0092353 | 0.0022906 | -0.0092195 | -0.0022863 | 1.5828e-05 | 4.3564e-06 | 0.013793 | 0.013793 | 0.013793 | 0.99573 | -0.030534 | 0.99397 | -0.043181 | 5.1087
4 | 0.0067271 | 0.0016611 | -0.0067246 | -0.0016607 | 2.5049e-06 | 4.4482e-07 | 0.010038 | 0.010038 | 0.010038 | 0.99633 | -0.02652 | 0.99595 | -0.029289 | 3.7179
5 | 0.0092195 | 0.0022863 | -0.0092178 | -0.0022858 | 1.717e-06 | 4.7296e-07 | 0.013793 | 0.013793 | 0.013793 | 0.99397 | -0.043181 | 0.99378 | -0.044555 | 5.1087
6 | 0.0082035 | 0.0020316 | -0.0082014 | -0.0020311 | 2.0826e-06 | 5.1408e-07 | 0.012275 | 0.012275 | 0.012275 | 0.99378 | -0.044555 | 0.99352 | -0.046432 | 4.5462
7 | 0.0082014 | 0.0020311 | -0.0082005 | -0.0020309 | 9.2289e-07 | 2.2786e-07 | 0.012275 | 0.012275 | 0.012275 | 0.99352 | -0.046432 | 0.99341 | -0.047264 | 4.5463
8 | -0.0070346 | -0.0017388 | 0.0070378 | 0.0017395 | 3.1808e-06 | 6.2884e-07 | 0.010533 | 0.010533 | 0.010533 | 0.99294 | -0.050619 | 0.99341 | -0.047264 | 3.9013
9 | 0.0070346 | 0.0017388 | -0.0070343 | -0.0017388 | 3.1144e-07 | 6.1604e-08 | 0.010533 | 0.010534 | 0.010534 | 0.99294 | -0.050619 | 0.9929 | -0.050948 | 3.9013
10 | 0.0020788 | 0.00049681 | -0.0020788 | -0.00049695 | 7.7452e-08 | -1.3649e-07 | 0.0031071 | 0.0031072 | 0.0031072 | 0.9929 | -0.050948 | 0.99286 | -0.051242 | 1.1508
11 | -0.0032712 | -0.00080302 | 0.0032741 | 0.00080159 | 2.9266e-06 | -1.4285e-06 | 0.0048863 | 0.0048854 | 0.0048863 | 0.99498 | -0.036369 | 0.9959 | -0.029628 | 1.8097
12 | 0.0029094 | 0.00071233 | -0.0029092 | -0.00071243 | 1.4224e-07 | -1.0209e-07 | 0.0043451 | 0.0043452 | 0.0043452 | 0.99498 | -0.036369 | 0.99493 | -0.036738 | 1.6093
13 | -0.0037905 | -0.000931 | 0.0037907 | 0.00093096 | 1.711e-07 | -4.5692e-08 | 0.0056569 | 0.0056569 | 0.0056569 | 0.9959 | -0.029628 | 0.99595 | -0.029289 | 2.0952
14 | 0.0021897 | 0.00053259 | -0.0021895 | -0.000533 | 2.6247e-07 | -4.1003e-07 | 0.0032693 | 0.0032695 | 0.0032695 | 0.99493 | -0.036738 | 0.99481 | -0.037654 | 1.2109
15 | 0.00071949 | 0.00017984 | -0.00071946 | -0.00018031 | 2.6535e-08 | -4.6679e-07 | 0.0010759 | 0.0010761 | 0.0010761 | 0.99493 | -0.036738 | 0.99489 | -0.037005 | 0.39854
16 | 0.00048995 | 0.0001172 | -0.00048981 | -0.00012276 | 1.4392e-07 | -5.5591e-06 | 0.00073009 | 0.00073203 | 0.00073203 | 0.99595 | -0.029289 | 0.99564 | -0.031508 | 0.27112
17 | 0.0016903 | 0.00040792 | -0.0016902 | -0.00040822 | 1.0232e-07 | -2.9511e-07 | 0.0025228 | 0.002523 | 0.002523 | 0.99481 | -0.037654 | 0.99475 | -0.038124 | 0.93443
18 | 0.00049918 | 0.00012507 | -0.00049918 | -0.00012511 | 9.3307e-10 | -3.4463e-08 | 0.00074666 | 0.00074667 | 0.00074667 | 0.99481 | -0.037654 | 0.99481 | -0.037668 | 0.27655
19 | 0.00071946 | 0.00018031 | -0.00071946 | -0.00018031 | 2.7979e-10 | -4.9142e-09 | 0.0010761 | 0.0010761 | 0.0010761 | 0.99489 | -0.037005 | 0.99489 | -0.037008 | 0.39854
20 | 0.00060528 | 0.00013632 | -0.00060519 | -0.0001388 | 9.8254e-08 | -2.4816e-06 | 0.00090027 | 0.00090108 | 0.00090108 | 0.99475 | -0.038124 | 0.99458 | -0.039515 | 0.33373
21 | 0.00060519 | 0.0001388 | -0.00060477 | -0.00014914 | 4.1165e-07 | -1.0338e-05 | 0.00090108 | 0.0009046 | 0.0009046 | 0.99458 | -0.039515 | 0.99388 | -0.044925 | 0.33504
22 | 0.00060477 | 0.00014914 | -0.00060472 | -0.00015039 | 5.0119e-08 | -1.252e-06 | 0.0009046 | 0.00090505 | 0.00090505 | 0.99388 | -0.044925 | 0.99379 | -0.045538 | 0.3352
23 | 0.001168 | 0.00026869 | -0.0011679 | -0.000269 | 4.8271e-08 | -3.1095e-07 | 0.0017423 | 0.0017424 | 0.0017424 | 0.99286 | -0.051242 | 0.99282 | -0.051589 | 0.64535
24 | 0.0011679 | 0.000269 | -0.0011673 | -0.00027348 | 6.9646e-07 | -4.4788e-06 | 0.0017424 | 0.001744 | 0.001744 | 0.99282 | -0.051589 | 0.9922 | -0.056528 | 0.64593
25 | 0.00021808 | 4.144e-05 | -0.00021801 | -5.4638e-05 | 6.7442e-08 | -1.3198e-05 | 0.00032291 | 0.00032705 | 0.00032705 | 0.9922 | -0.056528 | 0.99189 | -0.059305 | 0.12113
26 | 0.00049258 | 0.00011761 | -0.00049246 | -0.00012221 | 1.2227e-07 | -4.6048e-06 | 0.0007367 | 0.0007383 | 0.0007383 | 0.9922 | -0.056528 | 0.99195 | -0.058423 | 0.27345
27 | -0.00031951 | -8.0077e-05 | 0.00031951 | 7.9666e-05 | 4.5433e-09 | -4.105e-07 | 0.00047842 | 0.00047828 | 0.00047842 | 0.99375 | -0.045833 | 0.99377 | -0.04573 | 0.17719
28 | -0.00031951 | -7.9666e-05 | 0.00031952 | 7.8915e-05 | 8.3095e-09 | -7.5148e-07 | 0.00047828 | 0.00047801 | 0.00047828 | 0.99377 | -0.04573 | 0.99379 | -0.045538 | 0.17714
29 | 0.00049246 | 0.00012221 | -0.00049245 | -0.00012242 | 5.5206e-09 | -2.0737e-07 | 0.0007383 | 0.00073838 | 0.00073838 | 0.99195 | -0.058423 | 0.99194 | -0.058506 | 0.27347
30 | 0.00049245 | 0.00012242 | -0.00049242 | -0.00012341 | 2.6453e-08 | -9.9303e-07 | 0.00073838 | 0.00073873 | 0.00073873 | 0.99194 | -0.058506 | 0.99188 | -0.058897 | 0.2736

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.017814 | 0.0042143

## res_load
| p_mw | q_mvar
0 | 0.00059126 | 0.00014818
1 | 0.00039775 | 9.9687e-05
2 | 0.0010143 | 0.0002542
3 | 0.0011627 | 0.0002914
4 | 0.0049554 | 0.001242
5 | 0.00036187 | 9.0693e-05
6 | 0.00051635 | 0.00012941
7 | 0.002444 | 0.00061252
8 | 0.00048981 | 0.00012276
9 | 0.0010849 | 0.0002719
10 | 0.00049918 | 0.00012511
11 | 0.00071946 | 0.00018031
12 | 0.00091076 | 0.00022826
13 | 0.0004566 | 0.00011443
14 | 0.00021801 | 5.4638e-05
15 | 0.00031951 | 8.0077e-05
16 | 0.0002852 | 7.1478e-05
17 | 0.00049242 | 0.00012341

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1