## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-41_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-41_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-41_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-41_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-41_0_2_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1631-41_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1631-41_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1631-41_0_2_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1631-41_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1631-41_0_2_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_1631-41_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1631-41_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1631-41_0_2_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1631-41_0_2_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1631-41_0_2_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1631-41_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1631-41_0_2_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1631-41_0_2_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1631-41_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1631-41_0_2_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1631-41_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1631-41_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1631-41_0_2_node_18 | 0.4 | n |  | TRUE
23 | bus_MV_13_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-41_0_2_load_0 | 0 | 0.011312 | 0.002835 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-41_0_2_load_7 | 4 | 0.011184 | 0.0028029 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-41_0_2_load_8 | 6 | 0.012555 | 0.0031465 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-41_0_2_load_20 | 7 | 0.016031 | 0.0040177 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-41_0_2_load_22 | 9 | 0.0050127 | 0.0012563 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-41_0_2_load_9 | 11 | 0.0050126 | 0.0012563 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-41_0_2_load_13 | 14 | 0.015699 | 0.0039344 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-41_0_2_load_10 | 16 | 0.0024529 | 0.00061476 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-41_0_2_load_15 | 19 | 0.0016193 | 0.00040583 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-41_0_2_load_21 | 20 | 0.013757 | 0.0034477 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-41_0_2_load_16 | 21 | 0.0080053 | 0.0020063 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-41_0_2_load_18 | 22 | 0.014872 | 0.0037273 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-41_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-41_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.029779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-41_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.035798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-41_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.050517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-41_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.012521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-41_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0078928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-41_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.015225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-41_0_2_line_7 | NAYY 4x150 SE | 6 | 10 | 0.021345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-41_0_2_line_8 | NAYY 4x150 SE | 7 | 17 | 0.0076534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-41_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.021121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-41_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.18743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-41_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.016183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-41_0_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.022337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-41_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.040347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-41_0_2_line_14 | NAYY 4x150 SE | 13 | 20 | 0.020084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-41_0_2_line_15 | NAYY 4x150 SE | 13 | 17 | 0.025633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-41_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.025322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-41_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.010585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-41_0_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.061909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-41_0_2_line_19 | NAYY 4x150 SE | 17 | 21 | 0.015529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-41_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.0093161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-41_0_2_line_21 | NAYY 4x150 SE | 21 | 22 | 0.013943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-41_0_2_trafo_16 | 0.25 MVA 20/0.4 kV | 23 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2718840.9633 | 1199962.0288 | 2718834.3492 | 1199955.3257 | 2718824.1289 | 1199943.0802 | 2718822.4374 | 1199939.802
1 | 2718810.7163 | 1199912.5245 | 2718815.7676 | 1199921.9874 | 2718820.8364 | 1199936.699 | 2718822.4374 | 1199939.802
2 | 2718814.4058 | 1199977.8123 | 2718827.4603 | 1199973.5354 | 2718833.6554 | 1199972.5912 | 2718837.5469 | 1199972.2127 | 2718840.4274 | 1199970.5911 | 2718840.9633 | 1199962.0288
3 | 2718810.7163 | 1199912.5245 | 2718826.7922 | 1199922.5181 | 2718839.1216 | 1199931.7255 | 2718840.9511 | 1199936.9991 | 2718840.9345 | 1199940.5125 | 2718841.2016 | 1199942.3969 | 2718845.0212 | 1199945.9269
4 | 2718808.0306 | 1199901.2851 | 2718806.629 | 1199903.9815 | 2718807.9863 | 1199907.3443 | 2718810.7163 | 1199912.5245
5 | 2718814.4058 | 1199977.8123 | 2718809.7158 | 1199977.3632 | 2718806.6803 | 1199976.4109
6 | 2718808.0306 | 1199901.2851 | 2718814.3331 | 1199909.4942 | 2718818.8208 | 1199911.4009
7 | 2718786.7901 | 1199968.6901 | 2718803.4719 | 1199975.4043 | 2718806.6803 | 1199976.4109
8 | 2718825.8648 | 1199914.3937 | 2718818.8208 | 1199911.4009
9 | 2718754.9047 | 1200037.9516 | 2718745.5517 | 1200032.6397 | 2718739.5056 | 1200024.18
10 | 2718754.9047 | 1200037.9516 | 2718760.7848 | 1200036.7565 | 2718766.1097 | 1200033.9936 | 2718770.4639 | 1200029.8771 | 2718772.9034 | 1200024.3882 | 2718771.963 | 1200019.2102 | 2718756.6251 | 1200000.0692 | 2718737.833 | 1199981.9047 | 2718735.7922 | 1199978.0614 | 2718737.2564 | 1199976.0446 | 2718751.3511 | 1199978.4374 | 2718755.5854 | 1199977.2874 | 2718758.128 | 1199973.891 | 2718743.0014 | 1199968.2419 | 2718735.1865 | 1199965.24 | 2718741.2675 | 1199962.759 | 2718751.7631 | 1199961.5444 | 2718767.0094 | 1199962.3257 | 2718776.519 | 1199964.7386 | 2718786.7901 | 1199968.6901
11 | 2718786.7901 | 1199968.6901 | 2718783.5747 | 1199961.8767 | 2718782.1604 | 1199953.3424
12 | 2718825.1248 | 1199895.3206 | 2718835.1155 | 1199898.0546 | 2718843.2881 | 1199906.8124
13 | 2718825.1248 | 1199895.3206 | 2718827.3759 | 1199892.7968 | 2718827.4204 | 1199890.5628 | 2718821.9558 | 1199887.7076 | 2718826.3639 | 1199882.8027 | 2718827.0935 | 1199879.8151 | 2718826.7305 | 1199873.1808 | 2718829.8414 | 1199869.5511 | 2718833.4715 | 1199872.3586 | 2718835.6896 | 1199870.5203
14 | 2718843.2881 | 1199906.8124 | 2718853.5292 | 1199913.4208 | 2718860.3362 | 1199917.4229
15 | 2718825.8648 | 1199914.3937 | 2718830.5991 | 1199903.0462 | 2718835.0734 | 1199904.0025 | 2718837.699 | 1199905.6226 | 2718843.2881 | 1199906.8124
16 | 2718817.2559 | 1199854.8345 | 2718829.0733 | 1199863.7538 | 2718836.4063 | 1199869.9263 | 2718835.6896 | 1199870.5203
17 | 2718817.2559 | 1199854.8345 | 2718822.7362 | 1199854.2208 | 2718827.7835 | 1199854.7059
18 | 2718876.5818 | 1199886.6486 | 2718868.3401 | 1199882.515 | 2718855.4394 | 1199868.715 | 2718846.0797 | 1199856.4643 | 2718827.7835 | 1199854.7059
19 | 2718825.8648 | 1199914.3937 | 2718839.3187 | 1199922.1485
20 | 2718876.5818 | 1199886.6486 | 2718883.4477 | 1199892.9453
21 | 2718849.3881 | 1199931.3183 | 2718845.3659 | 1199925.6341 | 2718839.3187 | 1199922.1485

## bus_geodata
| x | y | coords
0 | 2718822.4374 | 1199939.802
1 | 2718840.9633 | 1199962.0288
2 | 2718810.7163 | 1199912.5245
3 | 2718814.4058 | 1199977.8123
4 | 2718845.0212 | 1199945.9269
5 | 2718808.0306 | 1199901.2851
6 | 2718806.6803 | 1199976.4109
7 | 2718818.8208 | 1199911.4009
8 | 2718754.9047 | 1200037.9516
9 | 2718739.5056 | 1200024.18
10 | 2718786.7901 | 1199968.6901
11 | 2718782.1604 | 1199953.3424
12 | 2718825.1248 | 1199895.3206
13 | 2718843.2881 | 1199906.8124
14 | 2718835.6896 | 1199870.5203
15 | 2718817.2559 | 1199854.8345
16 | 2718827.7835 | 1199854.7059
17 | 2718825.8648 | 1199914.3937
18 | 2718876.5818 | 1199886.6486
19 | 2718883.4477 | 1199892.9453
20 | 2718860.3362 | 1199917.4229
21 | 2718839.3187 | 1199922.1485
22 | 2718849.3881 | 1199931.3183
23 | 2718849.3881 | 1199931.3183

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99398 | -0.042176 | 0.011312 | 0.002835
1 | 0.99303 | -0.048819 | 0 | 0
2 | 0.99543 | -0.031987 | 0 | 0
3 | 0.99187 | -0.057019 | 0 | 0
4 | 0.99462 | -0.037683 | 0.011184 | 0.0028029
5 | 0.99624 | -0.026302 | 0 | 0
6 | 0.99162 | -0.058829 | 0.012555 | 0.0031465
7 | 0.99722 | -0.019401 | 0.016031 | 0.0040177
8 | 0.98995 | -0.070583 | 0 | 0
9 | 0.9898 | -0.071662 | 0.0050127 | 0.0012563
10 | 0.99131 | -0.061007 | 0 | 0
11 | 0.99119 | -0.061831 | 0.0050126 | 0.0012563
12 | 0.99603 | -0.02778 | 0 | 0
13 | 0.99666 | -0.023337 | 0 | 0
14 | 0.99489 | -0.035819 | 0.015699 | 0.0039344
15 | 0.99474 | -0.036861 | 0 | 0
16 | 0.99468 | -0.037297 | 0.0024529 | 0.00061476
17 | 0.99789 | -0.014707 | 0 | 0
18 | 0.99453 | -0.03831 | 0 | 0
19 | 0.99451 | -0.038463 | 0.0016193 | 0.00040583
20 | 0.99627 | -0.026114 | 0.013757 | 0.0034477
21 | 1 | 0 | -0.11082 | -0.027635
22 | 0.9997 | -0.0020703 | 0.014872 | 0.0037273
23 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.022643 | 0.0056793 | -0.022622 | -0.0056717 | 2.0835e-05 | 7.6374e-06 | 0.033899 | 0.033899 | 0.033899 | 0.99398 | -0.042176 | 0.99303 | -0.048819 | 12.5554
1 | -0.033955 | -0.0085143 | 0.034003 | 0.0085324 | 4.8016e-05 | 1.8081e-05 | 0.050833 | 0.050833 | 0.050833 | 0.99398 | -0.042176 | 0.99543 | -0.031987 | 18.8272
2 | 0.022622 | 0.0056717 | -0.022597 | -0.0056622 | 2.5671e-05 | 9.4107e-06 | 0.033899 | 0.0339 | 0.0339 | 0.99303 | -0.048819 | 0.99187 | -0.057019 | 12.5554
3 | 0.011193 | 0.0028057 | -0.011184 | -0.0028029 | 8.8246e-06 | 2.7379e-06 | 0.016731 | 0.016732 | 0.016732 | 0.99543 | -0.031987 | 0.99462 | -0.037683 | 6.1969
4 | -0.045196 | -0.011338 | 0.045231 | 0.011352 | 3.5666e-05 | 1.3555e-05 | 0.067565 | 0.067565 | 0.067565 | 0.99543 | -0.031987 | 0.99624 | -0.026302 | 25.024
5 | 0.022597 | 0.0056622 | -0.022591 | -0.0056602 | 5.6598e-06 | 2.075e-06 | 0.0339 | 0.0339 | 0.0339 | 0.99187 | -0.057019 | 0.99162 | -0.058829 | 12.5554
6 | -0.045231 | -0.011352 | 0.045275 | 0.011368 | 4.337e-05 | 1.6482e-05 | 0.067565 | 0.067565 | 0.067565 | 0.99624 | -0.026302 | 0.99722 | -0.019401 | 25.0239
7 | 0.010036 | 0.0025136 | -0.010033 | -0.0025127 | 3.0208e-06 | 8.8658e-07 | 0.01506 | 0.01506 | 0.01506 | 0.99162 | -0.058829 | 0.99131 | -0.061007 | 5.5778
8 | -0.061305 | -0.015386 | 0.061345 | 0.015401 | 3.9971e-05 | 1.5273e-05 | 0.091485 | 0.091485 | 0.091485 | 0.99722 | -0.019401 | 0.99789 | -0.014707 | 33.8833
9 | 0.0050134 | 0.0012563 | -0.0050127 | -0.0012563 | 7.4844e-07 | 1.6348e-08 | 0.0075357 | 0.0075358 | 0.0075358 | 0.98995 | -0.070583 | 0.9898 | -0.071662 | 2.791
10 | -0.0050134 | -0.0012563 | 0.0050201 | 0.0012565 | 6.6408e-06 | 1.4109e-07 | 0.0075357 | 0.0075349 | 0.0075357 | 0.98995 | -0.070583 | 0.99131 | -0.061007 | 2.791
11 | 0.0050132 | 0.0012563 | -0.0050126 | -0.0012563 | 5.7184e-07 | 1.1328e-08 | 0.0075251 | 0.0075252 | 0.0075252 | 0.99131 | -0.061007 | 0.99119 | -0.061831 | 2.7871
12 | -0.019794 | -0.004962 | 0.019806 | 0.0049664 | 1.2189e-05 | 4.397e-06 | 0.029571 | 0.029571 | 0.029571 | 0.99603 | -0.02778 | 0.99666 | -0.023337 | 10.9524
13 | 0.019794 | 0.004962 | -0.019772 | -0.0049541 | 2.2016e-05 | 7.9432e-06 | 0.029571 | 0.029572 | 0.029572 | 0.99603 | -0.02778 | 0.99489 | -0.035819 | 10.9525
14 | 0.013762 | 0.0034495 | -0.013757 | -0.0034477 | 5.2909e-06 | 1.7733e-06 | 0.020547 | 0.020547 | 0.020547 | 0.99666 | -0.023337 | 0.99627 | -0.026114 | 7.6099
15 | -0.033568 | -0.0084159 | 0.033608 | 0.008431 | 4.0176e-05 | 1.5118e-05 | 0.050118 | 0.050118 | 0.050118 | 0.99666 | -0.023337 | 0.99789 | -0.014707 | 18.5622
16 | 0.0040733 | 0.0010196 | -0.0040727 | -0.0010197 | 5.8638e-07 | -1.0323e-07 | 0.0060919 | 0.006092 | 0.006092 | 0.99489 | -0.035819 | 0.99474 | -0.036861 | 2.2563
17 | 0.0040727 | 0.0010197 | -0.0040725 | -0.0010198 | 2.4513e-07 | -4.3122e-08 | 0.006092 | 0.006092 | 0.006092 | 0.99474 | -0.036861 | 0.99468 | -0.037297 | 2.2563
18 | 0.0016196 | 0.00040501 | -0.0016193 | -0.00040572 | 2.2673e-07 | -7.1625e-07 | 0.0024225 | 0.0024228 | 0.0024228 | 0.99468 | -0.037297 | 0.99453 | -0.03831 | 0.89733
19 | -0.094954 | -0.023832 | 0.095148 | 0.023907 | 0.0001943 | 7.4526e-05 | 0.1416 | 0.1416 | 0.1416 | 0.99789 | -0.014707 | 1 | 0 | 52.4455
20 | 0.0016193 | 0.00040572 | -0.0016193 | -0.00040583 | 3.4124e-08 | -1.0776e-07 | 0.0024228 | 0.0024228 | 0.0024228 | 0.99453 | -0.03831 | 0.99451 | -0.038463 | 0.89734
21 | 0.014877 | 0.0037288 | -0.014872 | -0.0037273 | 4.2635e-06 | 1.4569e-06 | 0.022137 | 0.022137 | 0.022137 | 1 | 0 | 0.9997 | -0.0020703 | 8.1988

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11883 | 0.029642

## res_load
| p_mw | q_mvar
0 | 0.011312 | 0.002835
1 | 0.011184 | 0.0028029
2 | 0.012555 | 0.0031465
3 | 0.016031 | 0.0040177
4 | 0.0050127 | 0.0012563
5 | 0.0050126 | 0.0012563
6 | 0.015699 | 0.0039344
7 | 0.0024529 | 0.00061476
8 | 0.0016193 | 0.00040583
9 | 0.013757 | 0.0034477
10 | 0.0080053 | 0.0020063
11 | 0.014872 | 0.0037273

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1