## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-58_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-58_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-58_0_2_node_40 | 0.4 | n |  | TRUE
3 | bus_LV_1631-58_0_2_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1631-58_0_2_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_1631-58_0_2_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_1631-58_0_2_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1631-58_0_2_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_1631-58_0_2_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1631-58_0_2_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_1631-58_0_2_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1631-58_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1631-58_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1631-58_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-58_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1631-58_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1631-58_0_2_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_1631-58_0_2_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1631-58_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1631-58_0_2_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1631-58_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1631-58_0_2_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1631-58_0_2_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1631-58_0_2_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1631-58_0_2_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1631-58_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1631-58_0_2_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1631-58_0_2_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1631-58_0_2_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1631-58_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1631-58_0_2_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1631-58_0_2_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1631-58_0_2_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1631-58_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1631-58_0_2_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1631-58_0_2_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1631-58_0_2_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1631-58_0_2_node_35 | 0.4 | n |  | TRUE
38 | bus_MV_13_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-58_0_2_load_0 | 0 | 0.013594 | 0.003407 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-58_0_2_load_1 | 1 | 0.0061069 | 0.0015305 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-58_0_2_load_40 | 2 | 0.0056658 | 0.00142 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-58_0_2_load_28 | 4 | 0.0021165 | 0.00053045 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-58_0_2_load_29 | 5 | 0.002776 | 0.00069573 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-58_0_2_load_30 | 7 | 0.0020286 | 0.00050842 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-58_0_2_load_18 | 8 | 0.021359 | 0.0053532 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-58_0_2_load_3 | 9 | 0.0019455 | 0.00048758 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-58_0_2_load_4 | 10 | 0.0043981 | 0.0011023 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-58_0_2_load_7 | 12 | 0.048263 | 0.012096 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-58_0_2_load_13 | 15 | 0.0016909 | 0.00042377 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-58_0_2_load_10 | 17 | 0.0036534 | 0.00091563 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-58_0_2_load_11 | 18 | 0.0042688 | 0.0010699 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-58_0_2_load_12 | 19 | 0.0091237 | 0.0022866 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-58_0_2_load_15 | 21 | 0.020785 | 0.0052093 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-58_0_2_load_16 | 23 | 0.0016834 | 0.00042191 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-58_0_2_load_23 | 25 | 0.0038604 | 0.00096752 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-58_0_2_load_14 | 26 | 0.0056632 | 0.0014193 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-58_0_2_load_17 | 27 | 0.0041083 | 0.0010296 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-58_0_2_load_26 | 28 | 0.0016546 | 0.00041468 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-58_0_2_load_27 | 29 | 0.0043862 | 0.0010993 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-58_0_2_load_37 | 30 | 0.00091273 | 0.00022875 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-58_0_2_load_22 | 31 | 0.0044663 | 0.0011193 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-58_0_2_load_38 | 32 | 0.0029179 | 0.00073129 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-58_0_2_load_33 | 35 | 0.00088575 | 0.00022199 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-58_0_2_load_34 | 36 | 0.0052582 | 0.0013178 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-58_0_2_load_35 | 37 | 0.00089173 | 0.00022349 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-58_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.032921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-58_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.25831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-58_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.049284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-58_0_2_line_3 | NAYY 4x150 SE | 3 | 6 | 0.030483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-58_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.10276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-58_0_2_line_5 | NAYY 4x150 SE | 5 | 7 | 0.055842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-58_0_2_line_6 | NAYY 4x150 SE | 6 | 8 | 0.038626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-58_0_2_line_7 | NAYY 4x150 SE | 7 | 24 | 0.10256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-58_0_2_line_8 | NAYY 4x150 SE | 8 | 16 | 0.045058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-58_0_2_line_9 | NAYY 4x150 SE | 9 | 10 | 0.0060402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-58_0_2_line_10 | NAYY 4x150 SE | 10 | 11 | 0.019853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-58_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.038295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-58_0_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.032924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-58_0_2_line_13 | NAYY 4x150 SE | 13 | 17 | 0.0096287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-58_0_2_line_14 | NAYY 4x150 SE | 13 | 18 | 0.038909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-58_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.019643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1631-58_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.016525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1631-58_0_2_line_17 | NAYY 4x150 SE | 15 | 19 | 0.010568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1631-58_0_2_line_18 | NAYY 4x150 SE | 16 | 20 | 0.020438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1631-58_0_2_line_19 | NAYY 4x150 SE | 17 | 21 | 0.015832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-58_0_2_line_20 | NAYY 4x150 SE | 18 | 22 | 0.027389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1631-58_0_2_line_21 | NAYY 4x150 SE | 19 | 26 | 0.0049964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1631-58_0_2_line_22 | NAYY 4x150 SE | 20 | 25 | 0.0017367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1631-58_0_2_line_23 | NAYY 4x150 SE | 20 | 31 | 0.022953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-58_0_2_line_24 | NAYY 4x150 SE | 21 | 23 | 2.2306e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-58_0_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.025978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-58_0_2_line_26 | NAYY 4x150 SE | 22 | 25 | 0.059572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1631-58_0_2_line_27 | NAYY 4x150 SE | 23 | 27 | 0.0052052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-58_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.019312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-58_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.021181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-58_0_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.11313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-58_0_2_line_31 | NAYY 4x150 SE | 29 | 32 | 0.049614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-58_0_2_line_32 | NAYY 4x150 SE | 30 | 33 | 0.085312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-58_0_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.04441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-58_0_2_line_34 | NAYY 4x150 SE | 33 | 35 | 0.020516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-58_0_2_line_35 | NAYY 4x150 SE | 34 | 36 | 0.016714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-58_0_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.023859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-58_0_2_trafo_14 | 0.25 MVA 20/0.4 kV | 38 | 26 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2719401.2897 | 1199091.624 | 2719415.3362 | 1199100.3783 | 2719424.0259 | 1199100.0517 | 2719431.2075 | 1199097.3476
1 | 2719401.2897 | 1199091.624 | 2719297.6594 | 1198855.0157
2 | 2719473.6622 | 1199072.3677 | 2719432.7749 | 1199096.7574 | 2719431.2075 | 1199097.3476
3 | 2719473.6622 | 1199072.3677 | 2719481.732 | 1199072.1844 | 2719504.1848 | 1199070.7433
4 | 2719324.6308 | 1199180.6137 | 2719329.4289 | 1199185.2805 | 2719341.6584 | 1199193.4307 | 2719347.5858 | 1199196.0176 | 2719355.5496 | 1199197.322 | 2719393.6956 | 1199200.2859 | 2719403.5144 | 1199201.7609 | 2719411.1055 | 1199203.8029 | 2719416.1109 | 1199206.0268 | 2719420.4209 | 1199209.1221
5 | 2719420.4209 | 1199209.1221 | 2719422.0353 | 1199210.2816 | 2719427.9643 | 1199215.8374 | 2719435.9249 | 1199224.9143 | 2719441.8538 | 1199230.4701 | 2719447.961 | 1199234.7286 | 2719461.6668 | 1199241.0293 | 2719464.2964 | 1199242.4743
6 | 2719504.1848 | 1199070.7433 | 2719510.3148 | 1199070.8214 | 2719542.3218 | 1199076.4332
7 | 2719545.1896 | 1199179.4206 | 2719464.2964 | 1199242.4743
8 | 2719586.7024 | 1199084.2145 | 2719542.3218 | 1199076.4332
9 | 2719680.9568 | 1199107.0795 | 2719674.9572 | 1199106.3808
10 | 2719655.1983 | 1199104.4778 | 2719667.7447 | 1199105.5408 | 2719674.9572 | 1199106.3808
11 | 2719655.1983 | 1199104.4778 | 2719650.5938 | 1199120.2639 | 2719637.4565 | 1199137.7247
12 | 2719617.5458 | 1199163.9456 | 2719631.1956 | 1199146.039 | 2719635.2723 | 1199140.6277 | 2719637.4565 | 1199137.7247
13 | 2719617.5458 | 1199163.9456 | 2719625.4574 | 1199169.4336
14 | 2719617.5458 | 1199163.9456 | 2719588.822 | 1199158.3001 | 2719584.6469 | 1199159.1172 | 2719582.5779 | 1199160.499 | 2719580.7011 | 1199162.7008
15 | 2719603.2289 | 1199085.4571 | 2719592.639 | 1199102.0015
16 | 2719586.7024 | 1199084.2145 | 2719603.2289 | 1199085.4571
17 | 2719592.639 | 1199102.0015 | 2719586.9419 | 1199110.9021
18 | 2719586.7024 | 1199084.2145 | 2719571.969 | 1199098.4191
19 | 2719625.4574 | 1199169.4336 | 2719638.4661 | 1199178.4572
20 | 2719557.1223 | 1199156.3423 | 2719570.0329 | 1199164.3175 | 2719572.6716 | 1199165.2933 | 2719576.5415 | 1199166.0268 | 2719578.6546 | 1199165.1017 | 2719580.7011 | 1199162.7008
21 | 2719584.2483 | 1199115.1103 | 2719586.9419 | 1199110.9021
22 | 2719571.969 | 1199098.4191 | 2719570.8602 | 1199099.7557
23 | 2719571.969 | 1199098.4191 | 2719549.3638 | 1199094.4396
24 | 2719638.4679 | 1199178.4585 | 2719638.4661 | 1199178.4572
25 | 2719545.1896 | 1199179.4206 | 2719546.4722 | 1199176.9889 | 2719555.6491 | 1199158.7813 | 2719557.1223 | 1199156.3423
26 | 2719557.1223 | 1199156.3423 | 2719559.3516 | 1199146.9467 | 2719562.4979 | 1199114.5748 | 2719564.4839 | 1199107.4426 | 2719570.8602 | 1199099.7557
27 | 2719642.7449 | 1199181.4253 | 2719638.4679 | 1199178.4585
28 | 2719642.7449 | 1199181.4253 | 2719658.6134 | 1199192.4326
29 | 2719658.6134 | 1199192.4326 | 2719676.0169 | 1199204.5048
30 | 2719658.6134 | 1199192.4326 | 2719592.9422 | 1199284.5565
31 | 2719716.783 | 1199232.7828 | 2719676.0169 | 1199204.5048
32 | 2719579.6488 | 1199368.8265 | 2719592.9422 | 1199284.5565
33 | 2719622.2468 | 1199381.7995 | 2719579.6488 | 1199368.8265
34 | 2719579.6488 | 1199368.8265 | 2719577.5558 | 1199379.4035 | 2719581.6281 | 1199388.2444
35 | 2719622.2468 | 1199381.7995 | 2719617.8413 | 1199397.9229
36 | 2719617.8413 | 1199397.9229 | 2719613.765 | 1199412.8414 | 2719607.8071 | 1199414.8348 | 2719605.7137 | 1199415.1101

## bus_geodata
| x | y | coords
0 | 2719401.2897 | 1199091.624
1 | 2719431.2074 | 1199097.3476
2 | 2719297.6594 | 1198855.0157
3 | 2719473.6622 | 1199072.3677
4 | 2719324.6308 | 1199180.6137
5 | 2719420.4209 | 1199209.1221
6 | 2719504.1848 | 1199070.7433
7 | 2719464.2964 | 1199242.4743
8 | 2719542.3218 | 1199076.4332
9 | 2719680.9568 | 1199107.0795
10 | 2719674.9572 | 1199106.3808
11 | 2719655.1983 | 1199104.4778
12 | 2719637.4565 | 1199137.7247
13 | 2719617.5458 | 1199163.9456
14 | 2719603.2289 | 1199085.4571
15 | 2719592.639 | 1199102.0015
16 | 2719586.7024 | 1199084.2145
17 | 2719625.4574 | 1199169.4336
18 | 2719580.7011 | 1199162.7008
19 | 2719586.9419 | 1199110.9021
20 | 2719571.969 | 1199098.4191
21 | 2719638.4661 | 1199178.4572
22 | 2719557.1223 | 1199156.3423
23 | 2719638.4679 | 1199178.4585
24 | 2719545.1896 | 1199179.4206
25 | 2719570.8602 | 1199099.7557
26 | 2719584.2483 | 1199115.1103
27 | 2719642.7449 | 1199181.4253
28 | 2719658.6134 | 1199192.4326
29 | 2719676.0169 | 1199204.5048
30 | 2719592.9422 | 1199284.5565
31 | 2719549.3638 | 1199094.4396
32 | 2719716.783 | 1199232.7828
33 | 2719579.6488 | 1199368.8265
34 | 2719622.2468 | 1199381.7995
35 | 2719581.6281 | 1199388.2444
36 | 2719617.8413 | 1199397.9229
37 | 2719605.7137 | 1199415.1101
38 | 2719603.2289 | 1199085.4571

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98533 | -0.10265 | 0.013594 | 0.003407
1 | 0.98625 | -0.096131 | 0.0061069 | 0.0015305
2 | 0.98321 | -0.11776 | 0.0056658 | 0.00142
3 | 0.98806 | -0.083312 | 0 | 0
4 | 0.98477 | -0.10619 | 0.0021165 | 0.00053045
5 | 0.98509 | -0.10394 | 0.002776 | 0.00069573
6 | 0.98918 | -0.075405 | 0 | 0
7 | 0.98549 | -0.10113 | 0.0020286 | 0.00050842
8 | 0.99059 | -0.065411 | 0.021359 | 0.0053532
9 | 0.97569 | -0.17067 | 0.0019455 | 0.00048758
10 | 0.97571 | -0.17055 | 0.0043981 | 0.0011023
11 | 0.97589 | -0.16923 | 0 | 0
12 | 0.97625 | -0.16668 | 0.048263 | 0.012096
13 | 0.97887 | -0.1479 | 0 | 0
14 | 0.99565 | -0.03003 | 0 | 0
15 | 0.99805 | -0.013444 | 0.0016909 | 0.00042377
16 | 0.99363 | -0.044044 | 0 | 0
17 | 0.97821 | -0.15264 | 0.0036534 | 0.00091563
18 | 0.98465 | -0.10689 | 0.0042688 | 0.0010699
19 | 0.99935 | -0.0044648 | 0.0091237 | 0.0022866
20 | 0.99183 | -0.056604 | 0 | 0
21 | 0.97721 | -0.15983 | 0.020785 | 0.0052093
22 | 0.98677 | -0.091969 | 0 | 0
23 | 0.97721 | -0.15983 | 0.0016834 | 0.00042191
24 | 0.98651 | -0.093819 | 0 | 0
25 | 0.99168 | -0.057634 | 0.0038604 | 0.00096752
26 | 1 | 0 | -0.1828 | -0.046021
27 | 0.97705 | -0.16097 | 0.0041083 | 0.0010296
28 | 0.97657 | -0.1644 | 0.0016546 | 0.00041468
29 | 0.97634 | -0.16602 | 0.0043862 | 0.0010993
30 | 0.97525 | -0.17385 | 0.00091273 | 0.00022875
31 | 0.99168 | -0.057644 | 0.0044663 | 0.0011193
32 | 0.97613 | -0.16754 | 0.0029179 | 0.00073129
33 | 0.97438 | -0.18016 | 0 | 0
34 | 0.97398 | -0.18304 | 0 | 0
35 | 0.97435 | -0.18036 | 0.00088575 | 0.00022199
36 | 0.97383 | -0.18412 | 0.0052582 | 0.0013178
37 | 0.97379 | -0.18435 | 0.00089173 | 0.00022349
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.019272 | -0.0048282 | 0.019289 | 0.0048345 | 1.7399e-05 | 6.2722e-06 | 0.029103 | 0.029103 | 0.029103 | 0.98533 | -0.10265 | 0.98625 | -0.096131 | 10.7788
1 | 0.0056777 | 0.0014213 | -0.0056658 | -0.00142 | 1.185e-05 | 1.2746e-06 | 0.0085736 | 0.0085748 | 0.0085748 | 0.98533 | -0.10265 | 0.98321 | -0.11776 | 3.1759
2 | -0.025396 | -0.006365 | 0.025441 | 0.0063818 | 4.515e-05 | 1.6735e-05 | 0.038316 | 0.038316 | 0.038316 | 0.98625 | -0.096131 | 0.98806 | -0.083312 | 14.1913
3 | -0.025441 | -0.0063818 | 0.025469 | 0.0063921 | 2.7926e-05 | 1.035e-05 | 0.038316 | 0.038316 | 0.038316 | 0.98806 | -0.083312 | 0.98918 | -0.075405 | 14.1912
4 | -0.0021165 | -0.00053045 | 0.0021172 | 0.00052939 | 6.5575e-07 | -1.0556e-06 | 0.0031981 | 0.0031976 | 0.0031981 | 0.98477 | -0.10619 | 0.98509 | -0.10394 | 1.1845
5 | -0.0048932 | -0.0012251 | 0.0048951 | 0.0012251 | 1.9034e-06 | 2.0864e-08 | 0.0073909 | 0.0073907 | 0.0073909 | 0.98509 | -0.10394 | 0.98549 | -0.10113 | 2.7374
6 | -0.025469 | -0.0063921 | 0.025504 | 0.0064052 | 3.5385e-05 | 1.3113e-05 | 0.038316 | 0.038316 | 0.038316 | 0.98918 | -0.075405 | 0.99059 | -0.065411 | 14.1912
7 | -0.0069237 | -0.0017336 | 0.0069307 | 0.001735 | 6.9937e-06 | 1.3817e-06 | 0.010454 | 0.010453 | 0.010454 | 0.98549 | -0.10113 | 0.98651 | -0.093819 | 3.8718
8 | -0.046864 | -0.011758 | 0.047003 | 0.011811 | 0.00013935 | 5.3014e-05 | 0.070401 | 0.070401 | 0.070401 | 0.99059 | -0.065411 | 0.99363 | -0.044044 | 26.0743
9 | -0.0019455 | -0.00048758 | 0.0019455 | 0.00048752 | 3.318e-08 | -6.2677e-08 | 0.002967 | 0.002967 | 0.002967 | 0.97569 | -0.17067 | 0.97571 | -0.17055 | 1.0989
10 | -0.0063436 | -0.0015898 | 0.0063447 | 0.00159 | 1.1594e-06 | 1.9793e-07 | 0.0096743 | 0.0096742 | 0.0096743 | 0.97571 | -0.17055 | 0.97589 | -0.16923 | 3.5831
11 | -0.0063447 | -0.00159 | 0.006347 | 0.0015904 | 2.2364e-06 | 3.815e-07 | 0.0096742 | 0.009674 | 0.0096742 | 0.97589 | -0.16923 | 0.97625 | -0.16668 | 3.583
12 | -0.05461 | -0.013686 | 0.054752 | 0.01374 | 0.00014234 | 5.4333e-05 | 0.083237 | 0.083237 | 0.083237 | 0.97625 | -0.16668 | 0.97887 | -0.1479 | 30.8285
13 | 0.047245 | 0.01185 | -0.047214 | -0.011838 | 3.0994e-05 | 1.18e-05 | 0.071823 | 0.071823 | 0.071823 | 0.97887 | -0.1479 | 0.97821 | -0.15264 | 26.601
14 | -0.102 | -0.02559 | 0.10258 | 0.025814 | 0.00058375 | 0.00022403 | 0.15506 | 0.15506 | 0.15506 | 0.97887 | -0.1479 | 0.98465 | -0.10689 | 57.4294
15 | -0.17045 | -0.043031 | 0.17085 | 0.043183 | 0.00039807 | 0.00015259 | 0.25486 | 0.25486 | 0.25486 | 0.99565 | -0.03003 | 0.99805 | -0.013444 | 47.1957
16 | 0.17045 | 0.043031 | -0.17012 | -0.042902 | 0.00033488 | 0.00012837 | 0.25486 | 0.25486 | 0.25486 | 0.99565 | -0.03003 | 0.99363 | -0.044044 | 47.1957
17 | -0.17254 | -0.043607 | 0.17276 | 0.043691 | 0.00021841 | 8.3728e-05 | 0.25738 | 0.25738 | 0.25738 | 0.99805 | -0.013444 | 0.99935 | -0.0044648 | 47.6625
18 | 0.12312 | 0.031091 | -0.1229 | -0.031008 | 0.00021696 | 8.2918e-05 | 0.18446 | 0.18446 | 0.18446 | 0.99363 | -0.044044 | 0.99183 | -0.056604 | 34.1587
19 | 0.043561 | 0.010923 | -0.043518 | -0.010906 | 4.338e-05 | 1.6486e-05 | 0.066265 | 0.066265 | 0.066265 | 0.97821 | -0.15264 | 0.97721 | -0.15983 | 24.5427
20 | -0.10685 | -0.026884 | 0.10707 | 0.026969 | 0.00022291 | 8.5036e-05 | 0.16151 | 0.16151 | 0.16151 | 0.98465 | -0.10689 | 0.98677 | -0.091969 | 29.9093
21 | -0.18189 | -0.045977 | 0.182 | 0.046021 | 0.00011445 | 4.389e-05 | 0.27096 | 0.27096 | 0.27096 | 0.99935 | -0.0044648 | 1 | 0 | 50.1783
22 | 0.11843 | 0.029889 | -0.11842 | -0.029882 | 1.7121e-05 | 6.54e-06 | 0.17776 | 0.17776 | 0.17776 | 0.99183 | -0.056604 | 0.99168 | -0.057634 | 32.9176
23 | 0.0044669 | 0.0011193 | -0.0044663 | -0.0011193 | 6.4324e-07 | -4.8778e-08 | 0.0067015 | 0.0067016 | 0.0067016 | 0.99183 | -0.056604 | 0.99168 | -0.057644 | 2.4821
24 | 0.022732 | 0.0056968 | -0.022732 | -0.0056968 | 1.6677e-09 | 6.13e-10 | 0.034615 | 0.034615 | 0.034615 | 0.97721 | -0.15983 | 0.97721 | -0.15983 | 12.8203
25 | 0.0069325 | 0.0017353 | -0.0069307 | -0.001735 | 1.7713e-06 | 3.495e-07 | 0.010453 | 0.010453 | 0.010453 | 0.98677 | -0.091969 | 0.98651 | -0.093819 | 3.8716
26 | -0.11401 | -0.028705 | 0.11456 | 0.028915 | 0.00054962 | 0.00020986 | 0.17196 | 0.17196 | 0.17196 | 0.98677 | -0.091969 | 0.99168 | -0.057634 | 31.845
27 | 0.021049 | 0.0052749 | -0.021046 | -0.0052736 | 3.3367e-06 | 1.2181e-06 | 0.032051 | 0.032051 | 0.032051 | 0.97721 | -0.15983 | 0.97705 | -0.16097 | 11.8709
28 | 0.016937 | 0.004244 | -0.016929 | -0.0042412 | 8.0183e-06 | 2.8422e-06 | 0.025795 | 0.025795 | 0.025795 | 0.97705 | -0.16097 | 0.97657 | -0.1644 | 9.5536
29 | 0.0073063 | 0.0018305 | -0.0073046 | -0.0018302 | 1.638e-06 | 3.6505e-07 | 0.011133 | 0.011133 | 0.011133 | 0.97657 | -0.1644 | 0.97634 | -0.16602 | 4.1232
30 | 0.0079684 | 0.0019959 | -0.007958 | -0.0019934 | 1.0407e-05 | 2.589e-06 | 0.012141 | 0.012142 | 0.012142 | 0.97657 | -0.1644 | 0.97525 | -0.17385 | 4.4969
31 | 0.0029185 | 0.0007309 | -0.0029179 | -0.00073129 | 6.1248e-07 | -3.8476e-07 | 0.0044478 | 0.004448 | 0.004448 | 0.97634 | -0.16602 | 0.97613 | -0.16754 | 1.6474
32 | 0.0070452 | 0.0017646 | -0.0070391 | -0.0017633 | 6.151e-06 | 1.3022e-06 | 0.010749 | 0.010749 | 0.010749 | 0.97525 | -0.17385 | 0.97438 | -0.18016 | 3.9813
33 | 0.0061533 | 0.0015416 | -0.0061509 | -0.0015412 | 2.447e-06 | 3.8823e-07 | 0.0093968 | 0.009397 | 0.009397 | 0.97438 | -0.18016 | 0.97398 | -0.18304 | 3.4804
34 | 0.00088577 | 0.00022174 | -0.00088575 | -0.00022199 | 2.3423e-08 | -2.4652e-07 | 0.0013526 | 0.0013527 | 0.0013527 | 0.97438 | -0.18016 | 0.97435 | -0.18036 | 0.501
35 | 0.0061509 | 0.0015412 | -0.0061499 | -0.001541 | 9.21e-07 | 1.4624e-07 | 0.009397 | 0.0093971 | 0.0093971 | 0.97398 | -0.18304 | 0.97383 | -0.18412 | 3.4804
36 | 0.00089175 | 0.0002232 | -0.00089173 | -0.00022349 | 2.7641e-08 | -2.862e-07 | 0.0013625 | 0.0013626 | 0.0013626 | 0.97383 | -0.18412 | 0.97379 | -0.18435 | 0.50467

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18846 | 0.047441

## res_load
| p_mw | q_mvar
0 | 0.013594 | 0.003407
1 | 0.0061069 | 0.0015305
2 | 0.0056658 | 0.00142
3 | 0.0021165 | 0.00053045
4 | 0.002776 | 0.00069573
5 | 0.0020286 | 0.00050842
6 | 0.021359 | 0.0053532
7 | 0.0019455 | 0.00048758
8 | 0.0043981 | 0.0011023
9 | 0.048263 | 0.012096
10 | 0.0016909 | 0.00042377
11 | 0.0036534 | 0.00091563
12 | 0.0042688 | 0.0010699
13 | 0.0091237 | 0.0022866
14 | 0.020785 | 0.0052093
15 | 0.0016834 | 0.00042191
16 | 0.0038604 | 0.00096752
17 | 0.0056632 | 0.0014193
18 | 0.0041083 | 0.0010296
19 | 0.0016546 | 0.00041468
20 | 0.0043862 | 0.0010993
21 | 0.00091273 | 0.00022875
22 | 0.0044663 | 0.0011193
23 | 0.0029179 | 0.00073129
24 | 0.00088575 | 0.00022199
25 | 0.0052582 | 0.0013178
26 | 0.00089173 | 0.00022349

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1