## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-61_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-61_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-61_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-61_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-61_0_2_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_1631-61_0_2_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1631-61_0_2_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1631-61_0_2_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_1631-61_0_2_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1631-61_0_2_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1631-61_0_2_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1631-61_0_2_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1631-61_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1631-61_0_2_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1631-61_0_2_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1631-61_0_2_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1631-61_0_2_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1631-61_0_2_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1631-61_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1631-61_0_2_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1631-61_0_2_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1631-61_0_2_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_1631-61_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1631-61_0_2_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1631-61_0_2_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1631-61_0_2_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1631-61_0_2_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1631-61_0_2_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1631-61_0_2_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1631-61_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1631-61_0_2_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1631-61_0_2_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_1631-61_0_2_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1631-61_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1631-61_0_2_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1631-61_0_2_node_33 | 0.4 | n |  | TRUE
36 | bus_MV_13_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-61_0_2_load_0 | 0 | 0.0057482 | 0.0014406 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-61_0_2_load_2 | 2 | 0.0052463 | 0.0013149 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-61_0_2_load_14 | 4 | 0.0074339 | 0.0018631 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-61_0_2_load_19 | 5 | 0.0029724 | 0.00074495 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-61_0_2_load_18 | 6 | 0.0047791 | 0.0011978 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-61_0_2_load_20 | 9 | 0.0071445 | 0.0017906 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-61_0_2_load_4 | 10 | 0.0081639 | 0.0020461 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-61_0_2_load_5 | 11 | 0.044582 | 0.011173 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-61_0_2_load_26 | 14 | 0.0029071 | 0.00072858 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-61_0_2_load_29 | 15 | 0.009032 | 0.0022636 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-61_0_2_load_9 | 16 | 0.0030086 | 0.00075404 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-61_0_2_load_12 | 19 | 0.0070759 | 0.0017734 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-61_0_2_load_39 | 21 | 0.008498 | 0.0021298 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-61_0_2_load_16 | 22 | 0.0088108 | 0.0022082 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-61_0_2_load_24 | 23 | 0.015181 | 0.0038048 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-61_0_2_load_38 | 24 | 0.0081381 | 0.0020396 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-61_0_2_load_15 | 25 | 0.0050135 | 0.0012565 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-61_0_2_load_25 | 26 | 0.0071568 | 0.0017937 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-61_0_2_load_30 | 27 | 0.0082958 | 0.0020791 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-61_0_2_load_17 | 28 | 0.0044769 | 0.001122 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-61_0_2_load_27 | 29 | 0.0025908 | 0.00064932 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-61_0_2_load_28 | 30 | 0.0029123 | 0.00072989 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-61_0_2_load_36 | 31 | 0.010482 | 0.0026269 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-61_0_2_load_37 | 32 | 0.0081404 | 0.0020402 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-61_0_2_load_31 | 33 | 0.0064272 | 0.0016108 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-61_0_2_load_32 | 34 | 0.0050586 | 0.0012678 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-61_0_2_load_33 | 35 | 0.0039633 | 0.00099331 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-61_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.018145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-61_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.015436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-61_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.021414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-61_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.054974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-61_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.013062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-61_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0098918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-61_0_2_line_6 | NAYY 4x150 SE | 6 | 28 | 0.010438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-61_0_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.013136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-61_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.016024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-61_0_2_line_9 | NAYY 4x150 SE | 8 | 23 | 0.014241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-61_0_2_line_10 | NAYY 4x150 SE | 10 | 11 | 0.030056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-61_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.023709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-61_0_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.005299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-61_0_2_line_13 | NAYY 4x150 SE | 13 | 14 | 0.041124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-61_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.019494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-61_0_2_line_15 | NAYY 4x150 SE | 14 | 26 | 0.0010973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-61_0_2_line_16 | NAYY 4x150 SE | 15 | 27 | 0.022502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-61_0_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.043938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-61_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.030382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-61_0_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.019332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-61_0_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.004753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-61_0_2_line_21 | NAYY 4x150 SE | 18 | 21 | 0.01389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-61_0_2_line_22 | NAYY 4x150 SE | 19 | 22 | 0.00017557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-61_0_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.0053672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-61_0_2_line_24 | NAYY 4x150 SE | 21 | 24 | 0.005985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-61_0_2_line_25 | NAYY 4x150 SE | 22 | 25 | 0.027276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-61_0_2_line_26 | NAYY 4x150 SE | 24 | 32 | 0.0056027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-61_0_2_line_27 | NAYY 4x150 SE | 25 | 28 | 0.025106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-61_0_2_line_28 | NAYY 4x150 SE | 26 | 29 | 0.012329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-61_0_2_line_29 | NAYY 4x150 SE | 27 | 33 | 0.014445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-61_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.0060033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-61_0_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.0069415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-61_0_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.0063907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-61_0_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.0010874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-61_0_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.027729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-61_0_2_trafo_36 | 0.25 MVA 20/0.4 kV | 36 | 31 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2718650.4762 | 1198055.2413 | 2718657.1618 | 1198072.11
1 | 2718650.4762 | 1198055.2413 | 2718635.7878 | 1198059.9877
2 | 2718642.5909 | 1198035.3259 | 2718650.4762 | 1198055.2413
3 | 2718607.0191 | 1198103.07 | 2718617.334 | 1198074.6089 | 2718622.3474 | 1198066.5136 | 2718624.6404 | 1198064.2129 | 2718631.2851 | 1198061.4428 | 2718635.7878 | 1198059.9877
4 | 2718642.5909 | 1198035.3259 | 2718630.2199 | 1198039.5178
5 | 2718630.2199 | 1198039.5178 | 2718620.8514 | 1198042.6923
6 | 2718620.8514 | 1198042.6923 | 2718611.3138 | 1198045.9241 | 2718610.9893 | 1198046.0962
7 | 2718630.135 | 1198003.878 | 2718625.2963 | 1197991.662
8 | 2718630.135 | 1198003.878 | 2718615.0911 | 1198009.395
9 | 2718625.2963 | 1197991.662 | 2718611.6127 | 1197995.6058
10 | 2718639.7884 | 1197899.5081 | 2718641.1656 | 1197903.3904 | 2718640.7344 | 1197906.3062 | 2718639.6238 | 1197908.9082 | 2718620.8896 | 1197916.3542
11 | 2718598.8568 | 1197925.1112 | 2718620.8896 | 1197916.3542
12 | 2718598.8568 | 1197925.1112 | 2718596.8592 | 1197920.2014
13 | 2718596.8592 | 1197920.2014 | 2718573.5691 | 1197929.8576 | 2718580.1086 | 1197944.3627
14 | 2718596.8592 | 1197920.2014 | 2718589.4642 | 1197902.1642
15 | 2718580.5596 | 1197945.3631 | 2718580.5596 | 1197945.3631 | 2718580.1086 | 1197944.3627
16 | 2718589.4642 | 1197902.1642 | 2718580.9281 | 1197881.3437
17 | 2718572.5478 | 1198006.6488 | 2718530.2591 | 1198018.5745
18 | 2718572.5478 | 1198006.6488 | 2718601.8666 | 1197998.3798
19 | 2718572.5478 | 1198006.6488 | 2718580.4774 | 1198024.2798
20 | 2718606.4554 | 1197997.0922 | 2718601.8666 | 1197998.3798
21 | 2718601.8666 | 1197998.3798 | 2718596.8616 | 1197985.423
22 | 2718580.4774 | 1198024.2798 | 2718580.5495 | 1198024.4399
23 | 2718606.4554 | 1197997.0922 | 2718611.6127 | 1197995.6058
24 | 2718596.8616 | 1197985.423 | 2718594.705 | 1197979.8401
25 | 2718591.7375 | 1198049.3159 | 2718580.5495 | 1198024.4399
26 | 2718592.6861 | 1197974.6138 | 2718592.6861 | 1197974.6138 | 2718594.705 | 1197979.8401
27 | 2718591.7375 | 1198049.3159 | 2718594.2757 | 1198054.9594 | 2718610.9893 | 1198046.0962
28 | 2718580.5596 | 1197945.3631 | 2718585.2813 | 1197956.7523
29 | 2718580.9281 | 1197881.3437 | 2718575.4485 | 1197867.9785
30 | 2718585.2813 | 1197956.7523 | 2718587.5803 | 1197962.298
31 | 2718590.2387 | 1197968.7103 | 2718587.5803 | 1197962.298
32 | 2718590.2387 | 1197968.7103 | 2718592.6861 | 1197974.6138
33 | 2718575.4485 | 1197867.9785 | 2718575.036 | 1197866.9724
34 | 2718562.5995 | 1197842.2695 | 2718563.6543 | 1197843.6538 | 2718570.8451 | 1197856.7503 | 2718575.036 | 1197866.9724

## bus_geodata
| x | y | coords
0 | 2718657.1618 | 1198072.11
1 | 2718650.4762 | 1198055.2413
2 | 2718635.7878 | 1198059.9877
3 | 2718642.5909 | 1198035.3259
4 | 2718607.0191 | 1198103.07
5 | 2718630.2199 | 1198039.5178
6 | 2718620.8514 | 1198042.6923
7 | 2718630.135 | 1198003.878
8 | 2718625.2963 | 1197991.662
9 | 2718615.0911 | 1198009.395
10 | 2718639.7884 | 1197899.5081
11 | 2718620.8896 | 1197916.3542
12 | 2718598.8568 | 1197925.1112
13 | 2718596.8592 | 1197920.2014
14 | 2718580.1086 | 1197944.3627
15 | 2718589.4642 | 1197902.1642
16 | 2718530.2591 | 1198018.5745
17 | 2718572.5478 | 1198006.6488
18 | 2718601.8666 | 1197998.3798
19 | 2718580.4774 | 1198024.2798
20 | 2718606.4554 | 1197997.0922
21 | 2718596.8616 | 1197985.423
22 | 2718580.5495 | 1198024.4399
23 | 2718611.6127 | 1197995.6058
24 | 2718594.705 | 1197979.8401
25 | 2718591.7375 | 1198049.3159
26 | 2718580.5596 | 1197945.3631
27 | 2718580.9281 | 1197881.3437
28 | 2718610.9893 | 1198046.0962
29 | 2718585.2813 | 1197956.7523
30 | 2718587.5803 | 1197962.298
31 | 2718590.2387 | 1197968.7103
32 | 2718592.6861 | 1197974.6138
33 | 2718575.4485 | 1197867.9785
34 | 2718575.036 | 1197866.9724
35 | 2718562.5995 | 1197842.2695
36 | 2718601.8666 | 1197998.3798

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98793 | -0.084717 | 0.0057482 | 0.0014406
1 | 0.98808 | -0.083651 | 0 | 0
2 | 0.9878 | -0.085653 | 0.0052463 | 0.0013149
3 | 0.98865 | -0.079617 | 0 | 0
4 | 0.98721 | -0.089837 | 0.0074339 | 0.0018631
5 | 0.989 | -0.077159 | 0.0029724 | 0.00074495
6 | 0.98931 | -0.074998 | 0.0047791 | 0.0011978
7 | 0.99544 | -0.031838 | 0 | 0
8 | 0.99558 | -0.030893 | 0 | 0
9 | 0.99528 | -0.032992 | 0.0071445 | 0.0017906
10 | 0.98868 | -0.079348 | 0.0081639 | 0.0020461
11 | 0.98903 | -0.076843 | 0.044582 | 0.011173
12 | 0.99083 | -0.064106 | 0 | 0
13 | 0.99124 | -0.061265 | 0 | 0
14 | 0.9963 | -0.025716 | 0.0029071 | 0.00072858
15 | 0.99032 | -0.067763 | 0.009032 | 0.0022636
16 | 0.99347 | -0.045657 | 0.0030086 | 0.00075404
17 | 0.99366 | -0.044319 | 0 | 0
18 | 0.99605 | -0.027594 | 0 | 0
19 | 0.99222 | -0.054413 | 0.0070759 | 0.0017734
20 | 0.99589 | -0.028662 | 0 | 0
21 | 0.99758 | -0.016862 | 0.008498 | 0.0021298
22 | 0.99221 | -0.054492 | 0.0088108 | 0.0022082
23 | 0.99572 | -0.029868 | 0.015181 | 0.0038048
24 | 0.99832 | -0.011738 | 0.0081381 | 0.0020396
25 | 0.99081 | -0.064374 | 0.0050135 | 0.0012565
26 | 0.99644 | -0.02474 | 0.0071568 | 0.0017937
27 | 0.98955 | -0.073206 | 0.0082958 | 0.0020791
28 | 0.9897 | -0.072211 | 0.0044769 | 0.001122
29 | 0.99814 | -0.012912 | 0.0025908 | 0.00064932
30 | 0.99899 | -0.0070118 | 0.0029123 | 0.00072989
31 | 1 | 0 | -0.20518 | -0.051432
32 | 0.99907 | -0.0064929 | 0.0081404 | 0.0020402
33 | 0.98923 | -0.075482 | 0.0064272 | 0.0016108
34 | 0.98921 | -0.075582 | 0.0050586 | 0.0012678
35 | 0.98905 | -0.076703 | 0.0039633 | 0.00099331
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0057482 | -0.0014406 | 0.005749 | 0.0014407 | 8.4872e-07 | 9.4054e-08 | 0.0086579 | 0.0086578 | 0.0086579 | 0.98793 | -0.084717 | 0.98808 | -0.083651 | 3.2066
1 | 0.012688 | 0.0031801 | -0.012685 | -0.0031789 | 3.5169e-06 | 1.155e-06 | 0.019108 | 0.019108 | 0.019108 | 0.98808 | -0.083651 | 0.9878 | -0.085653 | 7.077
2 | -0.018437 | -0.0046208 | 0.018447 | 0.0046245 | 1.0301e-05 | 3.6876e-06 | 0.027766 | 0.027766 | 0.027766 | 0.98808 | -0.083651 | 0.98865 | -0.079617 | 10.2836
3 | 0.0074383 | 0.0018641 | -0.0074339 | -0.0018631 | 4.3069e-06 | 9.532e-07 | 0.011205 | 0.011205 | 0.011205 | 0.9878 | -0.085653 | 0.98721 | -0.089837 | 4.1501
4 | -0.018447 | -0.0046245 | 0.018454 | 0.0046267 | 6.2835e-06 | 2.2492e-06 | 0.027766 | 0.027765 | 0.027766 | 0.98865 | -0.079617 | 0.989 | -0.077159 | 10.2835
5 | -0.021426 | -0.0053717 | 0.021433 | 0.005374 | 6.4148e-06 | 2.3403e-06 | 0.032238 | 0.032238 | 0.032238 | 0.989 | -0.077159 | 0.98931 | -0.074998 | 11.9399
6 | -0.026212 | -0.0065718 | 0.026222 | 0.0065756 | 1.0124e-05 | 3.7597e-06 | 0.039426 | 0.039426 | 0.039426 | 0.98931 | -0.074998 | 0.9897 | -0.072211 | 14.6022
7 | -0.0071457 | -0.0017908 | 0.0071466 | 0.001791 | 9.3522e-07 | 1.8891e-07 | 0.010682 | 0.010681 | 0.010682 | 0.99544 | -0.031838 | 0.99558 | -0.030893 | 3.9561
8 | 0.0071457 | 0.0017908 | -0.0071445 | -0.0017906 | 1.1408e-06 | 2.305e-07 | 0.010682 | 0.010682 | 0.010682 | 0.99544 | -0.031838 | 0.99528 | -0.032992 | 3.9562
9 | -0.0071466 | -0.001791 | 0.0071476 | 0.0017912 | 1.0138e-06 | 2.0474e-07 | 0.010681 | 0.010681 | 0.010681 | 0.99558 | -0.030893 | 0.99572 | -0.029868 | 3.9561
10 | -0.0081639 | -0.0020461 | 0.0081667 | 0.0020468 | 2.8314e-06 | 7.0343e-07 | 0.012287 | 0.012287 | 0.012287 | 0.98868 | -0.079348 | 0.98903 | -0.076843 | 4.5508
11 | -0.052749 | -0.01322 | 0.052842 | 0.013256 | 9.318e-05 | 3.5533e-05 | 0.079361 | 0.079361 | 0.079361 | 0.98903 | -0.076843 | 0.99083 | -0.064106 | 29.3931
12 | -0.052842 | -0.013256 | 0.052863 | 0.013264 | 2.0826e-05 | 7.9415e-06 | 0.079361 | 0.079361 | 0.079361 | 0.99083 | -0.064106 | 0.99124 | -0.061265 | 29.3931
13 | -0.085693 | -0.021498 | 0.086117 | 0.02166 | 0.00042469 | 0.00016281 | 0.12865 | 0.12865 | 0.12865 | 0.99124 | -0.061265 | 0.9963 | -0.025716 | 47.647
14 | 0.03283 | 0.008234 | -0.032801 | -0.0082229 | 2.9548e-05 | 1.1114e-05 | 0.049286 | 0.049286 | 0.049286 | 0.99124 | -0.061265 | 0.99032 | -0.067763 | 18.254
15 | -0.089025 | -0.022389 | 0.089037 | 0.022394 | 1.211e-05 | 4.6433e-06 | 0.13299 | 0.13299 | 0.13299 | 0.9963 | -0.025716 | 0.99644 | -0.02474 | 49.255
16 | 0.023769 | 0.0059593 | -0.023751 | -0.0059527 | 1.791e-05 | 6.5993e-06 | 0.035715 | 0.035715 | 0.035715 | 0.99032 | -0.067763 | 0.98955 | -0.073206 | 13.2277
17 | -0.0030086 | -0.00075404 | 0.0030092 | 0.00075368 | 5.5674e-07 | -3.5491e-07 | 0.0045063 | 0.0045061 | 0.0045063 | 0.99347 | -0.045657 | 0.99366 | -0.044319 | 1.669
18 | -0.054763 | -0.013748 | 0.054891 | 0.013797 | 0.00012753 | 4.8655e-05 | 0.082017 | 0.082017 | 0.082017 | 0.99366 | -0.044319 | 0.99605 | -0.027594 | 30.3767
19 | 0.051754 | 0.012995 | -0.051682 | -0.012967 | 7.2476e-05 | 2.7625e-05 | 0.077511 | 0.077511 | 0.077511 | 0.99366 | -0.044319 | 0.99222 | -0.054413 | 28.7078
20 | 0.022336 | 0.0055986 | -0.022333 | -0.0055974 | 3.3024e-06 | 1.2083e-06 | 0.033369 | 0.033369 | 0.033369 | 0.99605 | -0.027594 | 0.99589 | -0.028662 | 12.3587
21 | -0.077227 | -0.019395 | 0.077342 | 0.01944 | 0.0001154 | 4.4202e-05 | 0.11539 | 0.11539 | 0.11539 | 0.99605 | -0.027594 | 0.99758 | -0.016862 | 42.7354
22 | 0.044606 | 0.011194 | -0.044605 | -0.011193 | 4.9031e-07 | 1.8631e-07 | 0.0669 | 0.0669 | 0.0669 | 0.99222 | -0.054413 | 0.99221 | -0.054492 | 24.7776
23 | 0.022333 | 0.0055974 | -0.022329 | -0.005596 | 3.7291e-06 | 1.3645e-06 | 0.033369 | 0.033369 | 0.033369 | 0.99589 | -0.028662 | 0.99572 | -0.029868 | 12.3587
24 | -0.08584 | -0.021569 | 0.085902 | 0.021593 | 6.1247e-05 | 2.3478e-05 | 0.12806 | 0.12806 | 0.12806 | 0.99758 | -0.016862 | 0.99832 | -0.011738 | 47.4301
25 | 0.035795 | 0.0089851 | -0.035746 | -0.0089666 | 4.9056e-05 | 1.8516e-05 | 0.053686 | 0.053686 | 0.053686 | 0.99221 | -0.054492 | 0.99081 | -0.064374 | 19.8838
26 | -0.09404 | -0.023633 | 0.094108 | 0.023659 | 6.871e-05 | 2.6354e-05 | 0.14019 | 0.14019 | 0.14019 | 0.99832 | -0.011738 | 0.99907 | -0.0064929 | 51.9227
27 | 0.030732 | 0.0077101 | -0.030699 | -0.0076976 | 3.3376e-05 | 1.2514e-05 | 0.046157 | 0.046157 | 0.046157 | 0.99081 | -0.064374 | 0.9897 | -0.072211 | 17.0952
28 | -0.096193 | -0.024187 | 0.096352 | 0.024248 | 0.00015881 | 6.0921e-05 | 0.14368 | 0.14368 | 0.14368 | 0.99644 | -0.02474 | 0.99814 | -0.012912 | 53.2133
29 | 0.015455 | 0.0038735 | -0.01545 | -0.0038719 | 4.8683e-06 | 1.6869e-06 | 0.02324 | 0.02324 | 0.02324 | 0.98955 | -0.073206 | 0.98923 | -0.075482 | 8.6074
30 | -0.098943 | -0.024897 | 0.099025 | 0.024929 | 8.1543e-05 | 3.1284e-05 | 0.14754 | 0.14754 | 0.14754 | 0.99814 | -0.012912 | 0.99899 | -0.0070118 | 54.6438
31 | -0.10194 | -0.025659 | 0.10204 | 0.025697 | 9.9912e-05 | 3.8337e-05 | 0.15188 | 0.15188 | 0.15188 | 0.99899 | -0.0070118 | 1 | 0 | 56.2504
32 | 0.10234 | 0.025735 | -0.10225 | -0.025699 | 9.2517e-05 | 3.55e-05 | 0.15232 | 0.15232 | 0.15232 | 1 | 0 | 0.99907 | -0.0064929 | 56.4132
33 | 0.0090227 | 0.002261 | -0.0090226 | -0.002261 | 1.2498e-07 | 3.4111e-08 | 0.013572 | 0.013572 | 0.013572 | 0.98923 | -0.075482 | 0.98921 | -0.075582 | 5.0267
34 | 0.003964 | 0.00099319 | -0.0039633 | -0.00099331 | 6.1519e-07 | -1.1931e-07 | 0.0059627 | 0.0059628 | 0.0059628 | 0.98921 | -0.075582 | 0.98905 | -0.076703 | 2.2084

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21566 | 0.054059

## res_load
| p_mw | q_mvar
0 | 0.0057482 | 0.0014406
1 | 0.0052463 | 0.0013149
2 | 0.0074339 | 0.0018631
3 | 0.0029724 | 0.00074495
4 | 0.0047791 | 0.0011978
5 | 0.0071445 | 0.0017906
6 | 0.0081639 | 0.0020461
7 | 0.044582 | 0.011173
8 | 0.0029071 | 0.00072858
9 | 0.009032 | 0.0022636
10 | 0.0030086 | 0.00075404
11 | 0.0070759 | 0.0017734
12 | 0.008498 | 0.0021298
13 | 0.0088108 | 0.0022082
14 | 0.015181 | 0.0038048
15 | 0.0081381 | 0.0020396
16 | 0.0050135 | 0.0012565
17 | 0.0071568 | 0.0017937
18 | 0.0082958 | 0.0020791
19 | 0.0044769 | 0.001122
20 | 0.0025908 | 0.00064932
21 | 0.0029123 | 0.00072989
22 | 0.010482 | 0.0026269
23 | 0.0081404 | 0.0020402
24 | 0.0064272 | 0.0016108
25 | 0.0050586 | 0.0012678
26 | 0.0039633 | 0.00099331

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1