## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-70_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-70_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-70_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1631-70_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1631-70_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1631-70_0_4_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_1631-70_0_4_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_1631-70_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_1631-70_0_4_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1631-70_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1631-70_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1631-70_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1631-70_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1631-70_0_4_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1631-70_0_4_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_1631-70_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1631-70_0_4_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1631-70_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1631-70_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1631-70_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1631-70_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1631-70_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1631-70_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1631-70_0_4_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1631-70_0_4_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_1631-70_0_4_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_1631-70_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1631-70_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1631-70_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1631-70_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1631-70_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1631-70_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1631-70_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1631-70_0_4_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1631-70_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_1631-70_0_4_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_1631-70_0_4_node_40 | 0.4 | n |  | TRUE
37 | bus_MV_145_1_node_281 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-70_0_4_load_0 | 0 | 0.006907 | 0.0017311 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-70_0_4_load_41 | 5 | 0.0004606 | 0.00011544 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-70_0_4_load_42 | 6 | 0.0015484 | 0.00038807 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-70_0_4_load_23 | 7 | 0.0040736 | 0.0010209 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-70_0_4_load_22 | 8 | 0.0010226 | 0.00025629 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-70_0_4_load_12 | 10 | 0.0049969 | 0.0012523 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-70_0_4_load_14 | 12 | 0.0060198 | 0.0015087 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-70_0_4_load_43 | 13 | 0.0076005 | 0.0019049 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-70_0_4_load_38 | 14 | 0.0011321 | 0.00028372 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-70_0_4_load_10 | 15 | 0.00070041 | 0.00017554 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-70_0_4_load_21 | 16 | 0.0041618 | 0.001043 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-70_0_4_load_17 | 17 | 0.003572 | 0.00089523 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-70_0_4_load_15 | 18 | 0.01171 | 0.0029348 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-70_0_4_load_8 | 19 | 0.01166 | 0.0029222 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-70_0_4_load_11 | 21 | 0.00080995 | 0.00020299 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-70_0_4_load_30 | 22 | 0.0010843 | 0.00027176 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-70_0_4_load_31 | 23 | 0.0013348 | 0.00033452 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-70_0_4_load_32 | 25 | 0.0028369 | 0.00071099 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-70_0_4_load_19 | 27 | 0.0049534 | 0.0012414 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-70_0_4_load_24 | 28 | 0.010629 | 0.0026639 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-70_0_4_load_25 | 29 | 0.0016743 | 0.00041963 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-70_0_4_load_28 | 31 | 0.0029332 | 0.00073514 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-70_0_4_load_39 | 34 | 0.00067595 | 0.00016941 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-70_0_4_load_36 | 35 | 0.00098888 | 0.00024784 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-70_0_4_load_40 | 36 | 0.0018112 | 0.00045393 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-70_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.031236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-70_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.054638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-70_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.070091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-70_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.28211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-70_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.003211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-70_0_4_line_5 | NAYY 4x150 SE | 2 | 6 | 0.004418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-70_0_4_line_6 | NAYY 4x150 SE | 3 | 7 | 0.008427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-70_0_4_line_7 | NAYY 4x150 SE | 3 | 8 | 0.0079915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-70_0_4_line_8 | NAYY 4x150 SE | 4 | 11 | 0.039491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-70_0_4_line_9 | NAYY 4x150 SE | 4 | 12 | 0.022515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-70_0_4_line_10 | NAYY 4x150 SE | 4 | 9 | 0.1523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-70_0_4_line_11 | NAYY 4x150 SE | 5 | 13 | 0.038849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-70_0_4_line_12 | NAYY 4x150 SE | 7 | 14 | 0.07823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-70_0_4_line_13 | NAYY 4x150 SE | 8 | 15 | 0.011548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-70_0_4_line_14 | NAYY 4x150 SE | 9 | 10 | 0.027757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-70_0_4_line_15 | NAYY 4x150 SE | 11 | 16 | 0.016773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-70_0_4_line_16 | NAYY 4x150 SE | 11 | 17 | 0.0075029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-70_0_4_line_17 | NAYY 4x150 SE | 12 | 18 | 0.0082554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-70_0_4_line_18 | NAYY 4x150 SE | 15 | 20 | 0.022478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-70_0_4_line_19 | NAYY 4x150 SE | 17 | 26 | 0.049712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-70_0_4_line_20 | NAYY 4x150 SE | 18 | 24 | 0.14004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-70_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.086532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-70_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.020344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-70_0_4_line_23 | NAYY 4x150 SE | 21 | 22 | 0.013287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-70_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.025222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-70_0_4_line_25 | NAYY 4x150 SE | 23 | 31 | 0.027023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-70_0_4_line_26 | NAYY 4x150 SE | 24 | 25 | 0.041042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-70_0_4_line_27 | NAYY 4x150 SE | 26 | 27 | 0.012397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-70_0_4_line_28 | NAYY 4x150 SE | 28 | 29 | 0.053746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-70_0_4_line_29 | NAYY 4x150 SE | 28 | 30 | 0.036857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-70_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.022333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-70_0_4_line_31 | NAYY 4x150 SE | 30 | 32 | 0.035527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-70_0_4_line_32 | NAYY 4x150 SE | 32 | 33 | 0.1111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-70_0_4_line_33 | NAYY 4x150 SE | 32 | 34 | 0.0164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-70_0_4_line_34 | NAYY 4x150 SE | 33 | 35 | 0.02197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-70_0_4_line_35 | NAYY 4x150 SE | 34 | 36 | 0.010048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-70_0_4_trafo_1 | 0.25 MVA 20/0.4 kV | 37 | 1 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2731792.1076 | 1202783.1954 | 2731761.1193 | 1202787.1243
1 | 2731792.1076 | 1202783.1954 | 2731793.0924 | 1202799.2742 | 2731799.404 | 1202803.728 | 2731813.7589 | 1202824.1941 | 2731813.67 | 1202825.8045 | 2731813.4481 | 1202829.9917
2 | 2731792.1076 | 1202783.1954 | 2731793.0924 | 1202799.2742 | 2731794.535 | 1202853.2371
3 | 2731792.1076 | 1202783.1954 | 2731791.3734 | 1202773.3493 | 2731791.9815 | 1202757.8729 | 2731791.4495 | 1202744.0392 | 2731790.5321 | 1202720.078 | 2731790.9359 | 1202699.3707 | 2731793.9061 | 1202678.6311 | 2731798.5173 | 1202641.8374 | 2731802.4775 | 1202607.2867 | 2731802.6761 | 1202605.5341 | 2731807.0711 | 1202567.1567 | 2731814.5798 | 1202502.583
4 | 2731816.6653 | 1202830.1295 | 2731813.4481 | 1202829.9917
5 | 2731813.1681 | 1202834.4001 | 2731813.4481 | 1202829.9917
6 | 2731787.5707 | 1202858.0094 | 2731794.535 | 1202853.2371
7 | 2731794.535 | 1202853.2371 | 2731794.751 | 1202861.2257
8 | 2731819.1457 | 1202463.3642 | 2731814.5798 | 1202502.583
9 | 2731814.5798 | 1202502.583 | 2731792.2293 | 1202499.8683
10 | 2731814.5798 | 1202502.583 | 2731807.0711 | 1202567.1567 | 2731810.9288 | 1202565.1847 | 2731815.5412 | 1202560.0602 | 2731836.6188 | 1202505.7273 | 2731843.6185 | 1202489.3801
11 | 2731841.026 | 1202845.6348 | 2731826.8839 | 1202844.8443 | 2731823.9731 | 1202844.6243 | 2731815.8538 | 1202843.7778 | 2731816.556 | 1202831.973 | 2731816.6653 | 1202830.1295
12 | 2731787.5707 | 1202858.0094 | 2731776.5808 | 1202882.7085 | 2731776.5607 | 1202888.1012 | 2731778.6146 | 1202913.6887 | 2731778.0342 | 1202925.841 | 2731776.2441 | 1202933.6044
13 | 2731795.0632 | 1202872.7699 | 2731794.751 | 1202861.2257
14 | 2731843.6185 | 1202489.3801 | 2731853.6762 | 1202465.9059 | 2731854.9119 | 1202464.0624
15 | 2731819.1457 | 1202463.3642 | 2731827.25 | 1202460.4296 | 2731832.9451 | 1202454.5507
16 | 2731819.1457 | 1202463.3642 | 2731820.0121 | 1202455.9115
17 | 2731784.0341 | 1202498.8729 | 2731792.2293 | 1202499.8683
18 | 2731795.6707 | 1202895.2394 | 2731795.0632 | 1202872.7699
19 | 2731825.7528 | 1202406.5322 | 2731820.0121 | 1202455.9115
20 | 2731784.0341 | 1202498.8729 | 2731648.6481 | 1202463.0601
21 | 2731795.6707 | 1202895.2394 | 2731811.2763 | 1202897.3187 | 2731833.9575 | 1202873.3894 | 2731871.2326 | 1202879.7743
22 | 2731795.6707 | 1202895.2394 | 2731796.2172 | 1202915.5759
23 | 2731796.5741 | 1202928.8582 | 2731796.2172 | 1202915.5759
24 | 2731799.9123 | 1202953.7569 | 2731799.8006 | 1202949.8844 | 2731796.7531 | 1202935.517 | 2731796.5741 | 1202928.8582
25 | 2731799.9123 | 1202953.7569 | 2731800.6917 | 1202980.7691
26 | 2731648.6481 | 1202463.0601 | 2731646.4783 | 1202465.4808 | 2731643.4073 | 1202466.9921 | 2731638.0464 | 1202468.0859 | 2731609.2768 | 1202470.7986
27 | 2731825.7528 | 1202406.5322 | 2731816.5001 | 1202406.3057 | 2731813.4253 | 1202406.9494
28 | 2731783.6767 | 1203090.9534 | 2731792.234 | 1203072.9582 | 2731794.9086 | 1203062.8426 | 2731798.9091 | 1203039.831
29 | 2731801.3358 | 1203003.0932 | 2731800.9441 | 1203014.6269 | 2731799.8789 | 1203034.2521 | 2731798.9091 | 1203039.831
30 | 2731801.3358 | 1203003.0932 | 2731800.6917 | 1202980.7691
31 | 2731836.868 | 1203000.4641 | 2731801.3358 | 1203003.0932
32 | 2731873.4734 | 1203044.0173 | 2731872.9411 | 1203040.5472 | 2731874.7994 | 1203030.5137 | 2731885.7158 | 1203001.9101 | 2731886.8658 | 1202993.9626 | 2731885.054 | 1202989.4858 | 2731882.0934 | 1202986.3513 | 2731876.7997 | 1202984.0771 | 2731868.0763 | 1202985.7748 | 2731859.1318 | 1202990.9369 | 2731851.1359 | 1202996.9207 | 2731844.3462 | 1202999.306 | 2731836.868 | 1203000.4641
33 | 2731836.868 | 1203000.4641 | 2731837.1688 | 1202984.0668
34 | 2731873.4734 | 1203044.0173 | 2731868.3127 | 1203065.3723
35 | 2731837.3531 | 1202974.0208 | 2731837.1688 | 1202984.0668

## bus_geodata
| x | y | coords
0 | 2731761.1193 | 1202787.1243
1 | 2731792.1076 | 1202783.1954
2 | 2731813.4481 | 1202829.9917
3 | 2731794.535 | 1202853.2371
4 | 2731814.5798 | 1202502.583
5 | 2731816.6653 | 1202830.1295
6 | 2731813.1681 | 1202834.4001
7 | 2731787.5706 | 1202858.0094
8 | 2731794.751 | 1202861.2257
9 | 2731843.6185 | 1202489.3801
10 | 2731854.9119 | 1202464.0624
11 | 2731819.1457 | 1202463.3642
12 | 2731792.2293 | 1202499.8683
13 | 2731841.026 | 1202845.6348
14 | 2731776.2441 | 1202933.6044
15 | 2731795.0632 | 1202872.7699
16 | 2731832.9451 | 1202454.5507
17 | 2731820.0121 | 1202455.9115
18 | 2731784.0341 | 1202498.8729
19 | 2731871.2326 | 1202879.7743
20 | 2731795.6707 | 1202895.2394
21 | 2731796.2172 | 1202915.5759
22 | 2731796.5741 | 1202928.8582
23 | 2731799.9123 | 1202953.7569
24 | 2731648.6481 | 1202463.0601
25 | 2731609.2768 | 1202470.7986
26 | 2731825.7528 | 1202406.5322
27 | 2731813.4253 | 1202406.9494
28 | 2731798.9091 | 1203039.831
29 | 2731783.6767 | 1203090.9534
30 | 2731801.3358 | 1203003.0932
31 | 2731800.6917 | 1202980.7691
32 | 2731836.868 | 1203000.4641
33 | 2731873.4734 | 1203044.0173
34 | 2731837.1688 | 1202984.0668
35 | 2731868.3127 | 1203065.3723
36 | 2731837.3531 | 1202974.0208
37 | 2731793.0924 | 1202799.2742

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99969 | -0.0021544 | 0.006907 | 0.0017311
1 | 1 | 0 | -0.097051 | -0.02423
2 | 0.99925 | -0.005248 | 0 | 0
3 | 0.99592 | -0.028512 | 0 | 0
4 | 0.98436 | -0.10959 | 0 | 0
5 | 0.99921 | -0.0055068 | 0.0004606 | 0.00011544
6 | 0.99924 | -0.0053164 | 0.0015484 | 0.00038807
7 | 0.99586 | -0.028954 | 0.0040736 | 0.0010209
8 | 0.99551 | -0.031358 | 0.0010226 | 0.00025629
9 | 0.98326 | -0.11745 | 0 | 0
10 | 0.98305 | -0.11888 | 0.0049969 | 0.0012523
11 | 0.98363 | -0.11475 | 0 | 0
12 | 0.98369 | -0.11436 | 0.0060198 | 0.0015087
13 | 0.99879 | -0.0084603 | 0.0076005 | 0.0019049
14 | 0.99573 | -0.029848 | 0.0011321 | 0.00028372
15 | 0.99494 | -0.035355 | 0.00070041 | 0.00017554
16 | 0.98353 | -0.11547 | 0.0041618 | 0.001043
17 | 0.98354 | -0.11541 | 0.003572 | 0.00089523
18 | 0.98351 | -0.1156 | 0.01171 | 0.0029348
19 | 0.99241 | -0.053201 | 0.01166 | 0.0029222
20 | 0.99386 | -0.042989 | 0 | 0
21 | 0.99322 | -0.047509 | 0.00080995 | 0.00020299
22 | 0.99281 | -0.050356 | 0.0010843 | 0.00027176
23 | 0.99208 | -0.055488 | 0.0013348 | 0.00033452
24 | 0.98294 | -0.11972 | 0 | 0
25 | 0.98277 | -0.12092 | 0.0028369 | 0.00071099
26 | 0.98318 | -0.11796 | 0 | 0
27 | 0.98309 | -0.11859 | 0.0049534 | 0.0012414
28 | 0.9902 | -0.068831 | 0.010629 | 0.0026639
29 | 0.99007 | -0.069748 | 0.0016743 | 0.00041963
30 | 0.99085 | -0.064215 | 0 | 0
31 | 0.99136 | -0.060628 | 0.0029332 | 0.00073514
32 | 0.99067 | -0.065477 | 0 | 0
33 | 0.99051 | -0.066603 | 0 | 0
34 | 0.99061 | -0.065892 | 0.00067595 | 0.00016941
35 | 0.99048 | -0.066824 | 0.00098888 | 0.00024784
36 | 0.99059 | -0.066077 | 0.0018112 | 0.00045393
37 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.006907 | -0.0017311 | 0.0069091 | 0.0017314 | 2.0602e-06 | 3.827e-07 | 0.010281 | 0.010281 | 0.010281 | 0.99969 | -0.0021544 | 1 | 0 | 3.8077
1 | 0.0096199 | 0.002411 | -0.0096129 | -0.0024091 | 6.9862e-06 | 1.9707e-06 | 0.014315 | 0.014315 | 0.014315 | 1 | 0 | 0.99925 | -0.005248 | 5.3018
2 | 0.040844 | 0.01027 | -0.040682 | -0.010209 | 0.00016162 | 6.1245e-05 | 0.060788 | 0.060789 | 0.060789 | 1 | 0 | 0.99592 | -0.028512 | 22.5143
3 | 0.038878 | 0.0098174 | -0.038288 | -0.0095942 | 0.00058967 | 0.00022315 | 0.057876 | 0.057878 | 0.057878 | 1 | 0 | 0.98436 | -0.10959 | 21.4362
4 | 0.0080645 | 0.002021 | -0.0080642 | -0.002021 | 2.8896e-07 | 6.9078e-08 | 0.012009 | 0.012009 | 0.012009 | 0.99925 | -0.005248 | 0.99921 | -0.0055068 | 4.4478
5 | 0.0015484 | 0.00038802 | -0.0015484 | -0.00038807 | 1.4657e-08 | -5.2236e-08 | 0.0023058 | 0.0023058 | 0.0023058 | 0.99925 | -0.005248 | 0.99924 | -0.0053164 | 0.85401
6 | 0.0052061 | 0.0013037 | -0.0052058 | -0.0013037 | 3.1813e-07 | 1.2711e-08 | 0.0077781 | 0.0077782 | 0.0077782 | 0.99592 | -0.028512 | 0.99586 | -0.028954 | 2.8808
7 | 0.035476 | 0.0089048 | -0.035462 | -0.0088995 | 1.4013e-05 | 5.2857e-06 | 0.053011 | 0.053011 | 0.053011 | 0.99592 | -0.028512 | 0.99551 | -0.031358 | 19.6336
8 | 0.0127 | 0.0031829 | -0.012691 | -0.0031799 | 9.0819e-06 | 2.9914e-06 | 0.019198 | 0.019198 | 0.019198 | 0.98436 | -0.10959 | 0.98363 | -0.11475 | 7.1103
9 | 0.020585 | 0.0051588 | -0.020571 | -0.0051539 | 1.3604e-05 | 4.9462e-06 | 0.031117 | 0.031117 | 0.031117 | 0.98436 | -0.10959 | 0.98369 | -0.11436 | 11.5249
10 | 0.0050033 | 0.0012525 | -0.0049979 | -0.0012524 | 5.436e-06 | 1.5694e-07 | 0.0075628 | 0.0075635 | 0.0075635 | 0.98436 | -0.10959 | 0.98326 | -0.11745 | 2.8013
11 | 0.0076036 | 0.0019055 | -0.0076005 | -0.0019049 | 3.1082e-06 | 6.8679e-07 | 0.011323 | 0.011323 | 0.011323 | 0.99921 | -0.0055068 | 0.99879 | -0.0084603 | 4.1938
12 | 0.0011322 | 0.00028276 | -0.0011321 | -0.00028372 | 1.3968e-07 | -9.6397e-07 | 0.0016914 | 0.0016917 | 0.0016917 | 0.99586 | -0.028954 | 0.99573 | -0.029848 | 0.62657
13 | 0.03444 | 0.0086433 | -0.034421 | -0.0086361 | 1.9099e-05 | 7.1959e-06 | 0.051482 | 0.051482 | 0.051482 | 0.99551 | -0.031358 | 0.99494 | -0.035355 | 19.0675
14 | 0.0049979 | 0.0012524 | -0.0049969 | -0.0012523 | 9.9088e-07 | 2.9113e-08 | 0.0075635 | 0.0075636 | 0.0075636 | 0.98326 | -0.11745 | 0.98305 | -0.11888 | 2.8013
15 | 0.0041622 | 0.001043 | -0.0041618 | -0.001043 | 4.1494e-07 | -5.3291e-08 | 0.0062964 | 0.0062965 | 0.0062965 | 0.98363 | -0.11475 | 0.98353 | -0.11547 | 2.332
16 | 0.0085283 | 0.0021369 | -0.0085276 | -0.0021367 | 7.7926e-07 | 2.0449e-07 | 0.012901 | 0.012901 | 0.012901 | 0.98363 | -0.11475 | 0.98354 | -0.11541 | 4.7783
17 | 0.014551 | 0.0036452 | -0.014549 | -0.0036443 | 2.4958e-06 | 8.5515e-07 | 0.022011 | 0.022011 | 0.022011 | 0.98369 | -0.11436 | 0.98351 | -0.1156 | 8.1523
18 | 0.03372 | 0.0084605 | -0.033685 | -0.0084471 | 3.5678e-05 | 1.3431e-05 | 0.050435 | 0.050435 | 0.050435 | 0.99494 | -0.035355 | 0.99386 | -0.042989 | 18.6795
19 | 0.0049556 | 0.0012415 | -0.0049538 | -0.0012414 | 1.7436e-06 | 3.9968e-08 | 0.0074972 | 0.0074974 | 0.0074974 | 0.98354 | -0.11541 | 0.98318 | -0.11796 | 2.7768
20 | 0.002839 | 0.00070949 | -0.0028373 | -0.00071065 | 1.6119e-06 | -1.1562e-06 | 0.0042945 | 0.0042951 | 0.0042951 | 0.98351 | -0.1156 | 0.98294 | -0.11972 | 1.5908
21 | -0.01166 | -0.0029222 | 0.011676 | 0.0029274 | 1.6503e-05 | 5.2275e-06 | 0.017482 | 0.017482 | 0.017482 | 0.99241 | -0.053201 | 0.99386 | -0.042989 | 6.475
22 | 0.022008 | 0.0055197 | -0.021995 | -0.0055147 | 1.3785e-05 | 5.0384e-06 | 0.032953 | 0.032953 | 0.032953 | 0.99386 | -0.042989 | 0.99322 | -0.047509 | 12.2048
23 | 0.021185 | 0.0053117 | -0.021176 | -0.0053086 | 8.3524e-06 | 3.0406e-06 | 0.031739 | 0.031739 | 0.031739 | 0.99322 | -0.047509 | 0.99281 | -0.050356 | 11.7554
24 | 0.020092 | 0.0050369 | -0.020078 | -0.0050317 | 1.4273e-05 | 5.1637e-06 | 0.030114 | 0.030114 | 0.030114 | 0.99281 | -0.050356 | 0.99208 | -0.055488 | 11.1535
25 | 0.018743 | 0.0046972 | -0.01873 | -0.0046924 | 1.3327e-05 | 4.777e-06 | 0.028112 | 0.028113 | 0.028113 | 0.99208 | -0.055488 | 0.99136 | -0.060628 | 10.412
26 | 0.0028373 | 0.00071065 | -0.0028369 | -0.00071099 | 4.7248e-07 | -3.3841e-07 | 0.0042951 | 0.0042953 | 0.0042953 | 0.98294 | -0.11972 | 0.98277 | -0.12092 | 1.5909
27 | 0.0049538 | 0.0012414 | -0.0049534 | -0.0012414 | 4.3484e-07 | 1.0045e-08 | 0.0074974 | 0.0074975 | 0.0074975 | 0.98318 | -0.11796 | 0.98309 | -0.11859 | 2.7768
28 | 0.0016745 | 0.00041902 | -0.0016743 | -0.00041963 | 2.1235e-07 | -6.0959e-07 | 0.0025162 | 0.0025164 | 0.0025164 | 0.9902 | -0.068831 | 0.99007 | -0.069748 | 0.93201
29 | -0.012304 | -0.0030829 | 0.012312 | 0.0030855 | 7.8621e-06 | 2.5495e-06 | 0.018489 | 0.018489 | 0.018489 | 0.9902 | -0.068831 | 0.99085 | -0.064215 | 6.8479
30 | -0.015789 | -0.0039545 | 0.015796 | 0.0039573 | 7.8342e-06 | 2.7254e-06 | 0.02371 | 0.02371 | 0.02371 | 0.99085 | -0.064215 | 0.99136 | -0.060628 | 8.7814
31 | 0.003477 | 0.00086905 | -0.0034764 | -0.00086927 | 6.0428e-07 | -2.251e-07 | 0.0052208 | 0.005221 | 0.005221 | 0.99085 | -0.064215 | 0.99067 | -0.065477 | 1.9337
32 | 0.00098907 | 0.0002462 | -0.00098892 | -0.00024757 | 1.5294e-07 | -1.3715e-06 | 0.001485 | 0.0014855 | 0.0014855 | 0.99067 | -0.065477 | 0.99051 | -0.066603 | 0.55019
33 | 0.0024874 | 0.00062308 | -0.0024872 | -0.00062323 | 1.4284e-07 | -1.5621e-07 | 0.003736 | 0.0037361 | 0.0037361 | 0.99067 | -0.065477 | 0.99061 | -0.065892 | 1.3837
34 | 0.00098892 | 0.00024757 | -0.00098888 | -0.00024784 | 3.0255e-08 | -2.7114e-07 | 0.0014855 | 0.0014856 | 0.0014856 | 0.99051 | -0.066603 | 0.99048 | -0.066824 | 0.55023
35 | 0.0018113 | 0.00045382 | -0.0018112 | -0.00045393 | 4.641e-08 | -1.115e-07 | 0.0027207 | 0.0027207 | 0.0027207 | 0.99061 | -0.065892 | 0.99059 | -0.066077 | 1.0077

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.097051 | 0.02423

## res_load
| p_mw | q_mvar
0 | 0.006907 | 0.0017311
1 | 0.0004606 | 0.00011544
2 | 0.0015484 | 0.00038807
3 | 0.0040736 | 0.0010209
4 | 0.0010226 | 0.00025629
5 | 0.0049969 | 0.0012523
6 | 0.0060198 | 0.0015087
7 | 0.0076005 | 0.0019049
8 | 0.0011321 | 0.00028372
9 | 0.00070041 | 0.00017554
10 | 0.0041618 | 0.001043
11 | 0.003572 | 0.00089523
12 | 0.01171 | 0.0029348
13 | 0.01166 | 0.0029222
14 | 0.00080995 | 0.00020299
15 | 0.0010843 | 0.00027176
16 | 0.0013348 | 0.00033452
17 | 0.0028369 | 0.00071099
18 | 0.0049534 | 0.0012414
19 | 0.010629 | 0.0026639
20 | 0.0016743 | 0.00041963
21 | 0.0029332 | 0.00073514
22 | 0.00067595 | 0.00016941
23 | 0.00098888 | 0.00024784
24 | 0.0018112 | 0.00045393

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1