## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-72_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-72_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-72_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-72_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-72_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-72_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-72_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1631-72_0_3_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1631-72_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1631-72_0_3_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1631-72_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1631-72_0_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1631-72_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1631-72_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1631-72_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1631-72_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1631-72_0_3_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_1631-72_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1631-72_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1631-72_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1631-72_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1631-72_0_3_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1631-72_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1631-72_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1631-72_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1631-72_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1631-72_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1631-72_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1631-72_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_MV_145_1_node_196 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-72_0_3_load_0 | 0 | 0.0090612 | 0.002271 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-72_0_3_load_4 | 4 | 0.0094997 | 0.0023809 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-72_0_3_load_5 | 5 | 0.0066593 | 0.001669 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-72_0_3_load_6 | 6 | 0.0070986 | 0.0017791 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-72_0_3_load_28 | 7 | 0.0073198 | 0.0018345 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-72_0_3_load_12 | 8 | 0.0053798 | 0.0013483 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-72_0_3_load_13 | 9 | 0.004714 | 0.0011814 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-72_0_3_load_7 | 12 | 0.005447 | 0.0013651 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-72_0_3_load_8 | 13 | 0.0052319 | 0.0013112 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-72_0_3_load_10 | 15 | 0.0072022 | 0.001805 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-72_0_3_load_19 | 16 | 0.0040649 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-72_0_3_load_20 | 17 | 0.0047022 | 0.0011785 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-72_0_3_load_16 | 19 | 0.0069991 | 0.0017541 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-72_0_3_load_17 | 20 | 0.0041632 | 0.0010434 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-72_0_3_load_27 | 21 | 0.010745 | 0.002693 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-72_0_3_load_26 | 22 | 0.0050359 | 0.0012621 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-72_0_3_load_18 | 23 | 0.004014 | 0.001006 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-72_0_3_load_25 | 24 | 0.004797 | 0.0012022 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-72_0_3_load_24 | 25 | 0.005751 | 0.0014413 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-72_0_3_load_21 | 26 | 0.0033243 | 0.00083314 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-72_0_3_load_22 | 27 | 0.010355 | 0.0025952 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-72_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-72_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.033871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-72_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.002479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-72_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.023476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-72_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.014073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-72_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.00016769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-72_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.014289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-72_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-72_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.0076079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-72_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.041772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-72_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.011098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-72_0_3_line_11 | NAYY 4x150 SE | 10 | 14 | 0.021234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-72_0_3_line_12 | NAYY 4x150 SE | 11 | 18 | 0.023192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-72_0_3_line_13 | NAYY 4x150 SE | 11 | 19 | 0.010938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1631-72_0_3_line_14 | NAYY 4x150 SE | 11 | 20 | 0.016392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-72_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.0021257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-72_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.0046483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-72_0_3_line_17 | NAYY 4x150 SE | 14 | 15 | 0.015622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-72_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.0069207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-72_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.0029927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-72_0_3_line_20 | NAYY 4x150 SE | 17 | 26 | 0.0075857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-72_0_3_line_21 | NAYY 4x150 SE | 18 | 21 | 0.020357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-72_0_3_line_22 | NAYY 4x150 SE | 18 | 22 | 0.018377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-72_0_3_line_23 | NAYY 4x150 SE | 19 | 23 | 0.02306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-72_0_3_line_24 | NAYY 4x150 SE | 20 | 24 | 0.0054883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-72_0_3_line_25 | NAYY 4x150 SE | 22 | 25 | 0.014546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-72_0_3_line_26 | NAYY 4x150 SE | 25 | 28 | 0.0056462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-72_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.027621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-72_0_3_trafo_16 | 0.25 MVA 20/0.4 kV | 29 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2730160.6383 | 1205169.8283 | 2730152.9169 | 1205179.7209
1 | 2730138.1851 | 1205209.8257 | 2730139.8467 | 1205203.7683 | 2730146.6255 | 1205187.7814 | 2730152.9169 | 1205179.7209
2 | 2730160.6383 | 1205169.8283 | 2730163.0868 | 1205170.2598
3 | 2730160.6383 | 1205169.8283 | 2730137.9128 | 1205163.9411
4 | 2730138.1851 | 1205209.8257 | 2730124.4732 | 1205206.6578 | 2730124.4732 | 1205206.6578
5 | 2730138.1851 | 1205209.8257 | 2730138.1495 | 1205209.9896
6 | 2730163.0868 | 1205170.2598 | 2730167.9155 | 1205156.8101
7 | 2730114.3153 | 1205212.3425 | 2730120.0137 | 1205212.2539 | 2730121.0939 | 1205211.9216 | 2730122.1608 | 1205211.1553 | 2730124.4732 | 1205206.6578
8 | 2730138.1495 | 1205209.9896 | 2730136.9328 | 1205215.6029 | 2730136.8509 | 1205217.4654
9 | 2730075.7966 | 1205213.5582 | 2730086.9777 | 1205217.9719 | 2730091.7658 | 1205213.7062 | 2730093.0693 | 1205212.5559 | 2730096.8716 | 1205211.2711 | 2730102.1419 | 1205210.7188 | 2730113.7642 | 1205212.3511 | 2730114.3153 | 1205212.3425
10 | 2730137.214 | 1205228.5303 | 2730136.6312 | 1205222.4573 | 2730136.8509 | 1205217.4654
11 | 2730066.9155 | 1205232.7909 | 2730069.1313 | 1205229.2364 | 2730069.6991 | 1205227.97 | 2730074.0647 | 1205218.302 | 2730075.7966 | 1205213.5582
12 | 2730137.214 | 1205228.5303 | 2730140.1366 | 1205251.5341
13 | 2730137.214 | 1205228.5303 | 2730133.304 | 1205229.8683 | 2730132.0881 | 1205236.5638
14 | 2730137.214 | 1205228.5303 | 2730152.6364 | 1205234.0841
15 | 2730063.1203 | 1205238.398 | 2730064.3587 | 1205236.6703
16 | 2730066.9155 | 1205232.7909 | 2730065.3781 | 1205235.2482 | 2730064.3587 | 1205236.6703
17 | 2730066.9155 | 1205232.7909 | 2730078.9747 | 1205236.3675 | 2730081.937 | 1205237.0649
18 | 2730088.6735 | 1205238.6508 | 2730081.937 | 1205237.0649
19 | 2730088.6735 | 1205238.6508 | 2730091.5866 | 1205239.3366
20 | 2730098.9704 | 1205241.0749 | 2730091.5866 | 1205239.3366
21 | 2730140.1366 | 1205251.5341 | 2730159.4856 | 1205257.8591
22 | 2730140.1366 | 1205251.5341 | 2730140.5001 | 1205260.3378 | 2730138.8995 | 1205269.7687
23 | 2730127.9681 | 1205259.2527 | 2730132.0881 | 1205236.5638
24 | 2730157.8002 | 1205235.9436 | 2730152.6364 | 1205234.0841
25 | 2730138.8995 | 1205269.7687 | 2730138.2212 | 1205273.7653 | 2730138.2091 | 1205276.4115 | 2730139.8089 | 1205280.5163 | 2730141.2194 | 1205283.6548
26 | 2730142.8876 | 1205289.0344 | 2730141.7974 | 1205284.9408 | 2730141.2194 | 1205283.6548
27 | 2730142.8876 | 1205289.0344 | 2730142.245 | 1205292.6788 | 2730140.6886 | 1205296.0031 | 2730137.8332 | 1205298.5317 | 2730132.3954 | 1205299.792 | 2730121.5811 | 1205300.7232

## bus_geodata
| x | y | coords
0 | 2730152.9169 | 1205179.7209
1 | 2730160.6383 | 1205169.8283
2 | 2730138.1851 | 1205209.8257
3 | 2730163.0868 | 1205170.2598
4 | 2730137.9128 | 1205163.9411
5 | 2730124.4732 | 1205206.6578
6 | 2730138.1495 | 1205209.9896
7 | 2730167.9155 | 1205156.8101
8 | 2730114.3153 | 1205212.3425
9 | 2730136.8509 | 1205217.4654
10 | 2730075.7966 | 1205213.5582
11 | 2730137.214 | 1205228.5303
12 | 2730064.3587 | 1205236.6703
13 | 2730063.1203 | 1205238.398
14 | 2730066.9155 | 1205232.7909
15 | 2730081.937 | 1205237.0649
16 | 2730088.6735 | 1205238.6508
17 | 2730091.5866 | 1205239.3366
18 | 2730140.1366 | 1205251.5341
19 | 2730132.0881 | 1205236.5638
20 | 2730152.6364 | 1205234.0841
21 | 2730159.4856 | 1205257.8591
22 | 2730138.8995 | 1205269.7687
23 | 2730127.9681 | 1205259.2527
24 | 2730157.8002 | 1205235.9436
25 | 2730141.2194 | 1205283.6548
26 | 2730098.9704 | 1205241.0749
27 | 2730121.5811 | 1205300.7232
28 | 2730142.8876 | 1205289.0344
29 | 2730137.214 | 1205228.5303

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9957 | -0.030102 | 0.0090612 | 0.002271
1 | 0.9954 | -0.032228 | 0 | 0
2 | 0.99695 | -0.021286 | 0 | 0
3 | 0.99537 | -0.032411 | 0 | 0
4 | 0.99508 | -0.034475 | 0.0094997 | 0.0023809
5 | 0.99611 | -0.02723 | 0.0066593 | 0.001669
6 | 0.99697 | -0.021172 | 0.0070986 | 0.0017791
7 | 0.99522 | -0.033465 | 0.0073198 | 0.0018345
8 | 0.99544 | -0.031928 | 0.0053798 | 0.0013483
9 | 0.99779 | -0.015446 | 0.004714 | 0.0011814
10 | 0.99364 | -0.044565 | 0 | 0
11 | 0.99906 | -0.006588 | 0 | 0
12 | 0.99265 | -0.051508 | 0.005447 | 0.0013651
13 | 0.99264 | -0.051621 | 0.0052319 | 0.0013112
14 | 0.99272 | -0.051005 | 0 | 0
15 | 0.99229 | -0.054059 | 0.0072022 | 0.001805
16 | 0.99217 | -0.054908 | 0.0040649 | 0.0010188
17 | 0.99214 | -0.055151 | 0.0047022 | 0.0011785
18 | 0.998 | -0.013993 | 0 | 0
19 | 1 | 0 | -0.12589 | -0.031414
20 | 0.99885 | -0.0080572 | 0.0041632 | 0.0010434
21 | 0.99769 | -0.016185 | 0.010745 | 0.002693
22 | 0.99744 | -0.017889 | 0.0050359 | 0.0012621
23 | 0.99987 | -0.0009242 | 0.004014 | 0.001006
24 | 0.99881 | -0.0083206 | 0.004797 | 0.0012022
25 | 0.99711 | -0.020241 | 0.005751 | 0.0014413
26 | 0.9921 | -0.055407 | 0.0033243 | 0.00083314
27 | 0.99662 | -0.023701 | 0.010355 | 0.0025952
28 | 0.99703 | -0.020828 | 0 | 0
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.016829 | 0.0042182 | -0.016824 | -0.0042165 | 4.953e-06 | 1.7418e-06 | 0.02515 | 0.02515 | 0.02515 | 0.9957 | -0.030102 | 0.9954 | -0.032228 | 9.3147
1 | -0.02589 | -0.0064892 | 0.025922 | 0.0065009 | 3.164e-05 | 1.1728e-05 | 0.038691 | 0.038691 | 0.038691 | 0.9957 | -0.030102 | 0.99695 | -0.021286 | 14.3301
2 | 0.007321 | 0.0018348 | -0.0073208 | -0.0018347 | 1.8528e-07 | 3.9038e-08 | 0.010944 | 0.010944 | 0.010944 | 0.9954 | -0.032228 | 0.99537 | -0.032411 | 4.0534
3 | 0.0095027 | 0.0023817 | -0.0094997 | -0.0023809 | 2.9561e-06 | 8.3192e-07 | 0.014206 | 0.014206 | 0.014206 | 0.9954 | -0.032228 | 0.99508 | -0.034475 | 5.2614
4 | 0.04216 | 0.010584 | -0.042125 | -0.010571 | 3.4779e-05 | 1.3193e-05 | 0.062932 | 0.062932 | 0.062932 | 0.99695 | -0.021286 | 0.99611 | -0.02723 | 23.3083
5 | -0.068081 | -0.017085 | 0.068082 | 0.017086 | 1.0806e-06 | 4.1344e-07 | 0.10162 | 0.10162 | 0.10162 | 0.99695 | -0.021286 | 0.99697 | -0.021172 | 37.6383
6 | 0.0073208 | 0.0018347 | -0.0073198 | -0.0018345 | 1.068e-06 | 2.2505e-07 | 0.010944 | 0.010944 | 0.010944 | 0.99537 | -0.032411 | 0.99522 | -0.033465 | 4.0534
7 | 0.035466 | 0.0089022 | -0.035442 | -0.0088935 | 2.3124e-05 | 8.722e-06 | 0.052985 | 0.052985 | 0.052985 | 0.99611 | -0.02723 | 0.99544 | -0.031928 | 19.6239
8 | -0.075181 | -0.018865 | 0.075241 | 0.018888 | 5.9783e-05 | 2.2894e-05 | 0.11222 | 0.11222 | 0.11222 | 0.99697 | -0.021172 | 0.99779 | -0.015446 | 41.5624
9 | 0.030063 | 0.0075452 | -0.03001 | -0.0075255 | 5.2649e-05 | 1.9707e-05 | 0.044943 | 0.044943 | 0.044943 | 0.99544 | -0.031928 | 0.99364 | -0.044565 | 16.6455
10 | -0.079955 | -0.020069 | 0.080053 | 0.020107 | 9.8474e-05 | 3.7729e-05 | 0.11925 | 0.11925 | 0.11925 | 0.99779 | -0.015446 | 0.99906 | -0.006588 | 44.1661
11 | 0.03001 | 0.0075254 | -0.029983 | -0.0075154 | 2.6764e-05 | 1.0019e-05 | 0.044943 | 0.044943 | 0.044943 | 0.99364 | -0.044565 | 0.99272 | -0.051005 | 16.6455
12 | 0.031945 | 0.0080124 | -0.031912 | -0.0080001 | 3.2764e-05 | 1.2298e-05 | 0.047581 | 0.047581 | 0.047581 | 0.99906 | -0.006588 | 0.998 | -0.013993 | 17.6227
13 | -0.12096 | -0.030365 | 0.12107 | 0.030408 | 0.00011079 | 4.2323e-05 | 0.18018 | 0.18018 | 0.18018 | 0.99906 | -0.006588 | 1 | 0 | 33.3663
14 | 0.0089621 | 0.0022461 | -0.0089603 | -0.0022456 | 1.8225e-06 | 4.8638e-07 | 0.013348 | 0.013348 | 0.013348 | 0.99906 | -0.006588 | 0.99885 | -0.0080572 | 4.9439
15 | 0.005232 | 0.0013113 | -0.0052319 | -0.0013112 | 8.159e-08 | 3.9025e-09 | 0.007843 | 0.007843 | 0.007843 | 0.99265 | -0.051508 | 0.99264 | -0.051621 | 2.9048
16 | -0.010679 | -0.0026764 | 0.01068 | 0.0026766 | 7.433e-07 | 2.2579e-07 | 0.016008 | 0.016008 | 0.016008 | 0.99265 | -0.051508 | 0.99272 | -0.051005 | 5.9289
17 | 0.019304 | 0.0048388 | -0.019295 | -0.0048359 | 8.1612e-06 | 2.937e-06 | 0.028935 | 0.028935 | 0.028935 | 0.99272 | -0.051005 | 0.99229 | -0.054059 | 10.7166
18 | 0.012093 | 0.0030308 | -0.012092 | -0.0030304 | 1.4202e-06 | 4.5685e-07 | 0.018135 | 0.018135 | 0.018135 | 0.99229 | -0.054059 | 0.99217 | -0.054908 | 6.7165
19 | 0.0080268 | 0.0020116 | -0.0080266 | -0.0020116 | 2.7063e-07 | 6.5441e-08 | 0.012038 | 0.012038 | 0.012038 | 0.99217 | -0.054908 | 0.99214 | -0.055151 | 4.4586
20 | 0.0033244 | 0.00083308 | -0.0033243 | -0.00083313 | 1.1767e-07 | -5.2698e-08 | 0.0049859 | 0.0049859 | 0.0049859 | 0.99214 | -0.055151 | 0.9921 | -0.055407 | 1.8466
21 | 0.010748 | 0.002694 | -0.010745 | -0.002693 | 3.2624e-06 | 9.8884e-07 | 0.016026 | 0.016026 | 0.016026 | 0.998 | -0.013993 | 0.99769 | -0.016185 | 5.9355
22 | 0.021163 | 0.0053061 | -0.021152 | -0.005302 | 1.1418e-05 | 4.1517e-06 | 0.031555 | 0.031556 | 0.031556 | 0.998 | -0.013993 | 0.99744 | -0.017889 | 11.6872
23 | 0.0040145 | 0.0010059 | -0.004014 | -0.001006 | 5.1349e-07 | -1.05e-07 | 0.0059736 | 0.0059737 | 0.0059737 | 1 | 0 | 0.99987 | -0.0009242 | 2.2125
24 | 0.0047971 | 0.0012022 | -0.0047969 | -0.0012022 | 1.7491e-07 | -4.5629e-09 | 0.0071464 | 0.0071465 | 0.0071465 | 0.99885 | -0.0080572 | 0.99881 | -0.0083206 | 2.6468
25 | 0.016116 | 0.0040398 | -0.016111 | -0.004038 | 5.2471e-06 | 1.8283e-06 | 0.024043 | 0.024043 | 0.024043 | 0.99744 | -0.017889 | 0.99711 | -0.020241 | 8.9048
26 | 0.01036 | 0.0025967 | -0.010359 | -0.0025964 | 8.4216e-07 | 2.5027e-07 | 0.015461 | 0.015461 | 0.015461 | 0.99711 | -0.020241 | 0.99703 | -0.020828 | 5.7262
27 | -0.010355 | -0.0025952 | 0.010359 | 0.0025964 | 4.1199e-06 | 1.2245e-06 | 0.015461 | 0.015461 | 0.015461 | 0.99662 | -0.023701 | 0.99703 | -0.020828 | 5.7262

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13288 | 0.033168

## res_load
| p_mw | q_mvar
0 | 0.0090612 | 0.002271
1 | 0.0094997 | 0.0023809
2 | 0.0066593 | 0.001669
3 | 0.0070986 | 0.0017791
4 | 0.0073198 | 0.0018345
5 | 0.0053798 | 0.0013483
6 | 0.004714 | 0.0011814
7 | 0.005447 | 0.0013651
8 | 0.0052319 | 0.0013112
9 | 0.0072022 | 0.001805
10 | 0.0040649 | 0.0010188
11 | 0.0047022 | 0.0011785
12 | 0.0069991 | 0.0017541
13 | 0.0041632 | 0.0010434
14 | 0.010745 | 0.002693
15 | 0.0050359 | 0.0012621
16 | 0.004014 | 0.001006
17 | 0.004797 | 0.0012022
18 | 0.005751 | 0.0014413
19 | 0.0033243 | 0.00083314
20 | 0.010355 | 0.0025952

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1