## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-80_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-80_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-80_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-80_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-80_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-80_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-80_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1631-80_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1631-80_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1631-80_0_3_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_1631-80_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1631-80_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1631-80_0_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1631-80_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1631-80_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1631-80_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1631-80_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1631-80_0_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1631-80_0_3_node_147 | 0.4 | n |  | TRUE
19 | bus_LV_1631-80_0_3_node_128 | 0.4 | n |  | TRUE
20 | bus_LV_1631-80_0_3_node_69 | 0.4 | n |  | TRUE
21 | bus_LV_1631-80_0_3_node_129 | 0.4 | n |  | TRUE
22 | bus_LV_1631-80_0_3_node_145 | 0.4 | n |  | TRUE
23 | bus_LV_1631-80_0_3_node_71 | 0.4 | n |  | TRUE
24 | bus_LV_1631-80_0_3_node_70 | 0.4 | n |  | TRUE
25 | bus_LV_1631-80_0_3_node_127 | 0.4 | n |  | TRUE
26 | bus_MV_145_1_node_269 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-80_0_3_load_0 | 0 | 0.0095795 | 0.0024008 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-80_0_3_load_1 | 1 | 0.0064008 | 0.0016042 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-80_0_3_load_2 | 2 | 0.0053343 | 0.0013369 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-80_0_3_load_4 | 4 | 0.0050566 | 0.0012673 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-80_0_3_load_6 | 6 | 0.011818 | 0.0029619 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-80_0_3_load_7 | 7 | 0.0051395 | 0.0012881 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-80_0_3_load_13 | 10 | 0.013486 | 0.0033799 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-80_0_3_load_17 | 12 | 0.005641 | 0.0014138 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-80_0_3_load_8 | 13 | 0.01434 | 0.003594 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-80_0_3_load_9 | 14 | 0.0062536 | 0.0015673 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-80_0_3_load_10 | 15 | 0.0079001 | 0.0019799 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-80_0_3_load_12 | 16 | 0.005971 | 0.0014965 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-80_0_3_load_18 | 17 | 0.0047405 | 0.0011881 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-80_0_3_load_147 | 18 | 0.001272 | 0.00031879 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-80_0_3_load_128 | 19 | 0.0064521 | 0.001617 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-80_0_3_load_129 | 21 | 0.0028894 | 0.00072416 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-80_0_3_load_145 | 22 | 0.00085867 | 0.0002152 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-80_0_3_load_127 | 25 | 0.00083245 | 0.00020863 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-80_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0041538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-80_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0020799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-80_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.00838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-80_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.005382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-80_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.026402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-80_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.010384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-80_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0052825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-80_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.38015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-80_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.37494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-80_0_3_line_9 | NAYY 4x150 SE | 5 | 10 | 0.024659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-80_0_3_line_10 | NAYY 4x150 SE | 6 | 11 | 0.019859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-80_0_3_line_11 | NAYY 4x150 SE | 7 | 12 | 0.0055854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-80_0_3_line_12 | NAYY 4x150 SE | 8 | 18 | 0.11621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-80_0_3_line_13 | NAYY 4x150 SE | 9 | 19 | 0.13456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-80_0_3_line_14 | NAYY 4x150 SE | 9 | 20 | 0.26496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-80_0_3_line_15 | NAYY 4x150 SE | 11 | 16 | 0.024415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-80_0_3_line_16 | NAYY 4x150 SE | 11 | 15 | 0.0072731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-80_0_3_line_17 | NAYY 4x150 SE | 13 | 14 | 0.028041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-80_0_3_line_18 | NAYY 4x150 SE | 13 | 15 | 0.010276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-80_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.0058204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-80_0_3_line_20 | NAYY 4x150 SE | 19 | 21 | 0.0045806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-80_0_3_line_21 | NAYY 4x150 SE | 20 | 24 | 0.05527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-80_0_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.008306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-80_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.1406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-80_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.024299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-80_0_3_trafo_3 | 0.25 MVA 20/0.4 kV | 26 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2731860.0839 | 1202319.7384 | 2731856.3717 | 1202317.8747
1 | 2731860.0839 | 1202319.7384 | 2731861.9427 | 1202320.6716
2 | 2731848.8825 | 1202314.1148 | 2731856.3717 | 1202317.8747
3 | 2731866.7526 | 1202323.0863 | 2731861.9427 | 1202320.6716
4 | 2731856.7934 | 1202288.9253 | 2731848.8825 | 1202314.1148
5 | 2731848.8825 | 1202314.1148 | 2731845.4534 | 1202323.9164
6 | 2731866.7526 | 1202323.0863 | 2731871.4735 | 1202325.4564
7 | 2731856.7934 | 1202288.9253 | 2731874.6559 | 1202234.0545 | 2731876.3142 | 1202228.9537 | 2731880.9049 | 1202214.8329 | 2731882.4403 | 1202210.1187 | 2731899.7385 | 1202159.4498 | 2731905.225 | 1202143.3806 | 2731906.666 | 1202139.1536 | 2731912.2378 | 1202124.3984 | 2731926.1331 | 1202090.9569 | 2731928.6747 | 1202082.4063 | 2731929.4871 | 1202073.8954 | 2731927.8198 | 1202048.7389 | 2731925.5037 | 1202022.2782 | 2731922.2737 | 1202016.1577 | 2731917.3088 | 1202011.0218 | 2731907.1568 | 1202005.9826 | 2731912.0877 | 1201994.3936 | 2731915.0304 | 1201982.1601 | 2731915.917 | 1201969.6032 | 2731914.7093 | 1201957.0667 | 2731911.4528 | 1201944.9076 | 2731906.4883 | 1201933.1999
8 | 2731856.7934 | 1202288.9253 | 2731874.6559 | 1202234.0545 | 2731876.3142 | 1202228.9537 | 2731880.9049 | 1202214.8329 | 2731882.4403 | 1202210.1187 | 2731899.7385 | 1202159.4498 | 2731905.225 | 1202143.3806 | 2731896.6319 | 1202132.2378 | 2731872.446 | 1202094.5523 | 2731864.1529 | 1202084.2945 | 2731851.1311 | 1202075.1 | 2731843.2386 | 1202071.8677 | 2731837.7847 | 1202071.2914 | 2731831.845 | 1202072.0276 | 2731807.7324 | 1202086.8627 | 2731781.5864 | 1202105.5228 | 2731775.3279 | 1202111.3893 | 2731772.4465 | 1202114.9952 | 2731758.6928 | 1202134.1291 | 2731755.5405 | 1202138.285 | 2731751.5463 | 1202141.2548 | 2731746.1721 | 1202144.3165
9 | 2731856.7934 | 1202288.9253 | 2731835.0206 | 1202277.3495
10 | 2731838.8953 | 1202342.6612 | 2731845.4534 | 1202323.9164
11 | 2731876.4652 | 1202327.9624 | 2731871.4735 | 1202325.4564
12 | 2731906.4883 | 1201933.1999 | 2732017.3276 | 1201968.1196
13 | 2731746.1721 | 1202144.3165 | 2731741.5921 | 1202152.7888 | 2731727.0545 | 1202184.682 | 2731723.3814 | 1202193.8082 | 2731719.7742 | 1202205.8158 | 2731719.5725 | 1202209.0917 | 2731720.0969 | 1202212.9285 | 2731721.6091 | 1202216.1643 | 2731724.3553 | 1202219.0271 | 2731742.5435 | 1202227.6682 | 2731745.9586 | 1202230.2344 | 2731746.6087 | 1202233.2066 | 2731745.771 | 1202238.7369 | 2731742.9319 | 1202244.5678 | 2731740.0833 | 1202251.1768 | 2731735.3674 | 1202255.0146
14 | 2731746.1721 | 1202144.3165 | 2731592.8701 | 1201928.214
15 | 2731838.8953 | 1202342.6612 | 2731861.5015 | 1202351.8824
16 | 2731838.8953 | 1202342.6612 | 2731836.4944 | 1202349.5266
17 | 2731833.1024 | 1202359.2263 | 2731831.9146 | 1202362.6228 | 2731829.5569 | 1202374.5801 | 2731828.0827 | 1202386.5235 | 2731828.0571 | 1202386.7435
18 | 2731833.1024 | 1202359.2263 | 2731836.4944 | 1202349.5266
19 | 2731866.8908 | 1202354.0807 | 2731861.5015 | 1202351.8824
20 | 2731735.3674 | 1202255.0146 | 2731731.8145 | 1202257.9058
21 | 2731539.07 | 1201916.8427 | 2731546.264 | 1201916.2005 | 2731576.1442 | 1201922.6079 | 2731592.8701 | 1201928.214
22 | 2731487.3621 | 1201955.6681 | 2731485.7191 | 1201947.5263
23 | 2731539.07 | 1201916.8427 | 2731538.8236 | 1201921.1183 | 2731539.9458 | 1201923.7451 | 2731542.2048 | 1201927.3087 | 2731550.3195 | 1201934.6375 | 2731552.1547 | 1201937.0465 | 2731552.2749 | 1201941.2635 | 2731550.7493 | 1201943.1203 | 2731549.1561 | 1201943.8969 | 2731546.5069 | 1201944.2277 | 2731517.6559 | 1201938.7995 | 2731513.3088 | 1201939.1263 | 2731512.131 | 1201939.7119 | 2731510.4385 | 1201941.198 | 2731508.9048 | 1201943.7663 | 2731503.3416 | 1201964.738 | 2731500.4549 | 1201972.3915 | 2731497.7231 | 1201976.1232 | 2731494.6368 | 1201978.3236 | 2731492.1407 | 1201977.924 | 2731490.8621 | 1201976.5169 | 2731489.936 | 1201974.3171 | 2731487.9593 | 1201958.628 | 2731487.3621 | 1201955.6681
24 | 2731539.07 | 1201916.8427 | 2731530.2219 | 1201916.5365 | 2731515.0642 | 1201913.5695

## bus_geodata
| x | y | coords
0 | 2731860.0839 | 1202319.7384
1 | 2731856.3717 | 1202317.8747
2 | 2731861.9427 | 1202320.6716
3 | 2731848.8825 | 1202314.1148
4 | 2731866.7526 | 1202323.0863
5 | 2731856.7934 | 1202288.9253
6 | 2731845.4534 | 1202323.9164
7 | 2731871.4735 | 1202325.4564
8 | 2731906.4883 | 1201933.1999
9 | 2731746.1721 | 1202144.3165
10 | 2731835.0206 | 1202277.3496
11 | 2731838.8953 | 1202342.6612
12 | 2731876.4652 | 1202327.9624
13 | 2731833.1024 | 1202359.2263
14 | 2731828.0571 | 1202386.7435
15 | 2731836.4944 | 1202349.5266
16 | 2731861.5015 | 1202351.8824
17 | 2731866.8908 | 1202354.0807
18 | 2732017.3276 | 1201968.1196
19 | 2731735.3674 | 1202255.0146
20 | 2731592.8701 | 1201928.214
21 | 2731731.8146 | 1202257.9058
22 | 2731485.7191 | 1201947.5263
23 | 2731487.3621 | 1201955.6681
24 | 2731539.07 | 1201916.8427
25 | 2731515.0642 | 1201913.5695
26 | 2731856.7934 | 1202288.9253

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99937 | -0.004385 | 0.0095795 | 0.0024008
1 | 0.99956 | -0.0031088 | 0.0064008 | 0.0016042
2 | 0.99931 | -0.0048251 | 0.0053343 | 0.0013369
3 | 1 | 0 | -0.11501 | -0.028633
4 | 0.99919 | -0.0056772 | 0.0050566 | 0.0012673
5 | 0.99903 | -0.0068419 | 0 | 0
6 | 0.99924 | -0.0052929 | 0.011818 | 0.0029619
7 | 0.99911 | -0.0062465 | 0.0051395 | 0.0012881
8 | 0.99834 | -0.011794 | 0 | 0
9 | 0.99308 | -0.048753 | 0 | 0
10 | 0.99855 | -0.010169 | 0.013486 | 0.0033799
11 | 0.99813 | -0.013085 | 0 | 0
12 | 0.99906 | -0.0065616 | 0.005641 | 0.0014138
13 | 0.99753 | -0.017285 | 0.01434 | 0.003594
14 | 0.99728 | -0.019044 | 0.0062536 | 0.0015673
15 | 0.99783 | -0.015162 | 0.0079001 | 0.0019799
16 | 0.99776 | -0.015707 | 0.005971 | 0.0014965
17 | 0.99772 | -0.015983 | 0.0047405 | 0.0011881
18 | 0.99812 | -0.013281 | 0.001272 | 0.00031879
19 | 0.99127 | -0.061506 | 0.0064521 | 0.001617
20 | 0.99244 | -0.053384 | 0 | 0
21 | 0.99125 | -0.061641 | 0.0028894 | 0.00072416
22 | 0.99212 | -0.055649 | 0.00085867 | 0.0002152
23 | 0.99213 | -0.055577 | 0 | 0
24 | 0.9923 | -0.054342 | 0 | 0
25 | 0.99227 | -0.054547 | 0.00083245 | 0.00020863
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.030755 | -0.0077083 | 0.030761 | 0.0077103 | 5.4353e-06 | 2.0361e-06 | 0.045793 | 0.045793 | 0.045793 | 0.99937 | -0.004385 | 0.99956 | -0.0031088 | 16.9604
1 | 0.021176 | 0.0053075 | -0.021174 | -0.005307 | 1.2902e-06 | 4.6899e-07 | 0.03153 | 0.03153 | 0.03153 | 0.99937 | -0.004385 | 0.99931 | -0.0048251 | 11.6776
2 | -0.037161 | -0.0093145 | 0.037177 | 0.0093206 | 1.6004e-05 | 6.0454e-06 | 0.055322 | 0.055322 | 0.055322 | 0.99956 | -0.0031088 | 1 | 0 | 20.4896
3 | 0.01584 | 0.0039701 | -0.015838 | -0.0039694 | 1.8683e-06 | 6.4809e-07 | 0.023587 | 0.023587 | 0.023587 | 0.99931 | -0.0048251 | 0.99919 | -0.0056772 | 8.7358
4 | 0.025905 | 0.0064873 | -0.02588 | -0.0064783 | 2.4477e-05 | 9.0681e-06 | 0.038545 | 0.038545 | 0.038545 | 1 | 0 | 0.99903 | -0.0068419 | 14.2759
5 | 0.051123 | 0.012825 | -0.051086 | -0.01281 | 3.7502e-05 | 1.4288e-05 | 0.076076 | 0.076076 | 0.076076 | 1 | 0 | 0.99924 | -0.0052929 | 28.1764
6 | 0.010782 | 0.0027021 | -0.010781 | -0.0027019 | 8.4979e-07 | 2.5766e-07 | 0.016056 | 0.016056 | 0.016056 | 0.99919 | -0.0056772 | 0.99911 | -0.0062465 | 5.9467
7 | 0.0012731 | 0.00031273 | -0.0012723 | -0.00031737 | 8.5175e-07 | -4.6466e-06 | 0.001894 | 0.0018958 | 0.0018958 | 0.99903 | -0.0068419 | 0.99834 | -0.011794 | 0.70214
8 | 0.011115 | 0.0027836 | -0.011051 | -0.0027638 | 6.4124e-05 | 1.9783e-05 | 0.016554 | 0.016556 | 0.016556 | 0.99903 | -0.0068419 | 0.99308 | -0.048753 | 6.1319
9 | 0.013492 | 0.003382 | -0.013486 | -0.0033799 | 6.2144e-06 | 2.0674e-06 | 0.020096 | 0.020097 | 0.020097 | 0.99903 | -0.0068419 | 0.99855 | -0.010169 | 7.4432
10 | 0.039268 | 0.0098485 | -0.039225 | -0.0098324 | 4.2376e-05 | 1.6039e-05 | 0.058478 | 0.058478 | 0.058478 | 0.99924 | -0.0052929 | 0.99813 | -0.013085 | 21.6584
11 | 0.0056412 | 0.0014138 | -0.005641 | -0.0014138 | 2.4602e-07 | 2.1482e-08 | 0.0084017 | 0.0084017 | 0.0084017 | 0.99911 | -0.0062465 | 0.99906 | -0.0065616 | 3.1118
12 | 0.0012723 | 0.00031737 | -0.001272 | -0.00031879 | 2.6069e-07 | -1.4189e-06 | 0.0018958 | 0.0018963 | 0.0018963 | 0.99834 | -0.011794 | 0.99812 | -0.013281 | 0.70233
13 | 0.009358 | 0.0023458 | -0.0093415 | -0.0023412 | 1.6509e-05 | 4.612e-06 | 0.014022 | 0.014023 | 0.014023 | 0.99308 | -0.048753 | 0.99127 | -0.061506 | 5.1936
14 | 0.0016926 | 0.00041802 | -0.0016915 | -0.00042104 | 1.0621e-06 | -3.0174e-06 | 0.002534 | 0.0025352 | 0.0025352 | 0.99308 | -0.048753 | 0.99244 | -0.053384 | 0.93895
15 | 0.010716 | 0.0026857 | -0.010712 | -0.0026846 | 3.8879e-06 | 1.1764e-06 | 0.015975 | 0.015975 | 0.015975 | 0.99813 | -0.013085 | 0.99776 | -0.015707 | 5.9167
16 | 0.02851 | 0.0071467 | -0.028501 | -0.0071437 | 8.1985e-06 | 3.0583e-06 | 0.042503 | 0.042503 | 0.042503 | 0.99813 | -0.013085 | 0.99783 | -0.015162 | 15.7418
17 | 0.0062551 | 0.0015675 | -0.0062536 | -0.0015673 | 1.5234e-06 | 2.1995e-07 | 0.0093307 | 0.0093309 | 0.0093309 | 0.99753 | -0.017285 | 0.99728 | -0.019044 | 3.4559
18 | -0.020595 | -0.0051615 | 0.020601 | 0.0051637 | 6.0519e-06 | 2.1935e-06 | 0.030722 | 0.030722 | 0.030722 | 0.99753 | -0.017285 | 0.99783 | -0.015162 | 11.3785
19 | 0.0047407 | 0.0011881 | -0.0047405 | -0.0011881 | 1.8155e-07 | -6.1881e-09 | 0.0070701 | 0.0070701 | 0.0070701 | 0.99776 | -0.015707 | 0.99772 | -0.015983 | 2.6186
20 | 0.0028895 | 0.00072412 | -0.0028894 | -0.00072416 | 5.3774e-08 | -3.8366e-08 | 0.0043374 | 0.0043375 | 0.0043375 | 0.99127 | -0.061506 | 0.99125 | -0.061641 | 1.6065
21 | 0.0016915 | 0.00042104 | -0.0016913 | -0.00042167 | 2.2168e-07 | -6.2882e-07 | 0.0025352 | 0.0025354 | 0.0025354 | 0.99244 | -0.053384 | 0.9923 | -0.054342 | 0.93904
22 | -0.00085867 | -0.0002152 | 0.00085868 | 0.0002151 | 8.5962e-09 | -1.0395e-07 | 0.0012879 | 0.0012878 | 0.0012879 | 0.99212 | -0.055649 | 0.99213 | -0.055577 | 0.47699
23 | -0.00085868 | -0.0002151 | 0.00085883 | 0.00021334 | 1.4544e-07 | -1.7601e-06 | 0.0012878 | 0.0012872 | 0.0012878 | 0.99213 | -0.055577 | 0.9923 | -0.054342 | 0.47697
24 | 0.00083247 | 0.00020833 | -0.00083245 | -0.00020863 | 2.3626e-08 | -3.048e-07 | 0.0012482 | 0.0012483 | 0.0012483 | 0.9923 | -0.054342 | 0.99227 | -0.054547 | 0.46235

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11501 | 0.028633

## res_load
| p_mw | q_mvar
0 | 0.0095795 | 0.0024008
1 | 0.0064008 | 0.0016042
2 | 0.0053343 | 0.0013369
3 | 0.0050566 | 0.0012673
4 | 0.011818 | 0.0029619
5 | 0.0051395 | 0.0012881
6 | 0.013486 | 0.0033799
7 | 0.005641 | 0.0014138
8 | 0.01434 | 0.003594
9 | 0.0062536 | 0.0015673
10 | 0.0079001 | 0.0019799
11 | 0.005971 | 0.0014965
12 | 0.0047405 | 0.0011881
13 | 0.001272 | 0.00031879
14 | 0.0064521 | 0.001617
15 | 0.0028894 | 0.00072416
16 | 0.00085867 | 0.0002152
17 | 0.00083245 | 0.00020863

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1