## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-87_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-87_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-87_0_2_node_77 | 0.4 | n |  | TRUE
3 | bus_LV_1631-87_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-87_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-87_0_2_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_1631-87_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1631-87_0_2_node_76 | 0.4 | n |  | TRUE
8 | bus_LV_1631-87_0_2_node_64 | 0.4 | n |  | TRUE
9 | bus_LV_1631-87_0_2_node_72 | 0.4 | n |  | TRUE
10 | bus_LV_1631-87_0_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1631-87_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1631-87_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1631-87_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1631-87_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1631-87_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1631-87_0_2_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_1631-87_0_2_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1631-87_0_2_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1631-87_0_2_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1631-87_0_2_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1631-87_0_2_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1631-87_0_2_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1631-87_0_2_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1631-87_0_2_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1631-87_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1631-87_0_2_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1631-87_0_2_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1631-87_0_2_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1631-87_0_2_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1631-87_0_2_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1631-87_0_2_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1631-87_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_1631-87_0_2_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1631-87_0_2_node_27 | 0.4 | n |  | TRUE
35 | bus_MV_13_0_node_112 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-87_0_2_load_0 | 0 | 0.0017628 | 0.00044181 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-87_0_2_load_77 | 2 | 0.0008925 | 0.00022368 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-87_0_2_load_3 | 3 | 0.012699 | 0.0031827 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-87_0_2_load_64 | 8 | 0.0088404 | 0.0022156 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-87_0_2_load_72 | 9 | 0.0011454 | 0.00028706 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-87_0_2_load_35 | 10 | 0.00088516 | 0.00022184 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-87_0_2_load_6 | 11 | 0.0017416 | 0.00043649 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-87_0_2_load_7 | 12 | 0.0016206 | 0.00040617 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-87_0_2_load_9 | 14 | 0.0024133 | 0.00060484 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-87_0_2_load_65 | 16 | 0.016198 | 0.0040595 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-87_0_2_load_20 | 17 | 0.0036805 | 0.00092241 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-87_0_2_load_26 | 19 | 0.0051425 | 0.0012888 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-87_0_2_load_11 | 20 | 0.0035947 | 0.00090091 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-87_0_2_load_12 | 21 | 0.0031392 | 0.00078675 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-87_0_2_load_15 | 24 | 0.0025156 | 0.00063048 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-87_0_2_load_16 | 26 | 0.0015512 | 0.00038876 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-87_0_2_load_19 | 29 | 0.002521 | 0.00063182 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-87_0_2_load_21 | 30 | 0.010349 | 0.0025938 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-87_0_2_load_23 | 31 | 0.0044798 | 0.0011227 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-87_0_2_load_25 | 32 | 0.0028179 | 0.00070624 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-87_0_2_load_33 | 33 | 0.0026634 | 0.0006675 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-87_0_2_load_27 | 34 | 0.0035147 | 0.00088086 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-87_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-87_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.032476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-87_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.046051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-87_0_2_line_3 | NAYY 4x150 SE | 1 | 4 | 0.095839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-87_0_2_line_4 | NAYY 4x150 SE | 2 | 7 | 0.020991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-87_0_2_line_5 | NAYY 4x150 SE | 4 | 8 | 0.035035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-87_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.013823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-87_0_2_line_7 | NAYY 4x150 SE | 5 | 7 | 0.030247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-87_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.015535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-87_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.1029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-87_0_2_line_10 | NAYY 4x150 SE | 8 | 16 | 0.018292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-87_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.023922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-87_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.044233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-87_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.023316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-87_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.02611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-87_0_2_line_15 | NAYY 4x150 SE | 13 | 16 | 0.0946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-87_0_2_line_16 | NAYY 4x150 SE | 14 | 17 | 0.016776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-87_0_2_line_17 | NAYY 4x150 SE | 15 | 18 | 0.008289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-87_0_2_line_18 | NAYY 4x150 SE | 15 | 19 | 0.01207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-87_0_2_line_19 | NAYY 4x150 SE | 17 | 29 | 0.010227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-87_0_2_line_20 | NAYY 4x150 SE | 18 | 31 | 0.012506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-87_0_2_line_21 | NAYY 4x150 SE | 18 | 30 | 0.013453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-87_0_2_line_22 | NAYY 4x150 SE | 19 | 34 | 0.010104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-87_0_2_line_23 | NAYY 4x150 SE | 20 | 21 | 0.005443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-87_0_2_line_24 | NAYY 4x150 SE | 20 | 22 | 0.0082874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-87_0_2_line_25 | NAYY 4x150 SE | 21 | 23 | 0.026685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-87_0_2_line_26 | NAYY 4x150 SE | 22 | 24 | 0.050323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-87_0_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.039409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-87_0_2_line_28 | NAYY 4x150 SE | 23 | 26 | 0.022822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-87_0_2_line_29 | NAYY 4x150 SE | 24 | 27 | 0.043982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-87_0_2_line_30 | NAYY 4x150 SE | 25 | 28 | 0.026448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-87_0_2_line_31 | NAYY 4x150 SE | 27 | 29 | 0.0028435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-87_0_2_line_32 | NAYY 4x150 SE | 28 | 32 | 0.014204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-87_0_2_line_33 | NAYY 4x150 SE | 32 | 33 | 0.0010431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-87_0_2_trafo_26 | 0.25 MVA 20/0.4 kV | 35 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2718284.5635 | 1199862.4744 | 2718289.6782 | 1199865.3222 | 2718297.063 | 1199867.0847
1 | 2718297.063 | 1199867.0847 | 2718325.7907 | 1199851.9383
2 | 2718284.5635 | 1199862.4744 | 2718277.8719 | 1199865.8 | 2718273.6686 | 1199866.5396 | 2718270.1369 | 1199866.8254 | 2718264.6232 | 1199866.8163 | 2718260.9093 | 1199865.92 | 2718241.1744 | 1199857.5588
3 | 2718210.7186 | 1199824.508 | 2718215.7231 | 1199824.4625 | 2718221.0603 | 1199822.6111 | 2718227.4059 | 1199824.8383 | 2718236.9502 | 1199827.8293 | 2718247.2005 | 1199830.9343 | 2718252.9962 | 1199832.4723 | 2718262.3259 | 1199833.2241 | 2718262.1393 | 1199837.6459 | 2718262.7503 | 1199840.2488 | 2718264.2365 | 1199842.502 | 2718266.9756 | 1199844.5577 | 2718278.4084 | 1199848.7092 | 2718282.186 | 1199851.0079 | 2718284.8898 | 1199854.842 | 2718285.7286 | 1199858.2499 | 2718284.5635 | 1199862.4744
4 | 2718341.9867 | 1199865.1464 | 2718339.345 | 1199863.5596 | 2718335.0539 | 1199858.7378 | 2718325.7907 | 1199851.9383
5 | 2718210.7186 | 1199824.508 | 2718206.726 | 1199822.2941 | 2718202.4423 | 1199816.7053 | 2718198.8197 | 1199813.8871 | 2718195.7291 | 1199812.6585 | 2718193.3311 | 1199812.611 | 2718180.9884 | 1199817.0427
6 | 2718326.1908 | 1199890.9414 | 2718328.4517 | 1199897.9134 | 2718329.3982 | 1199904.3369
7 | 2718326.1908 | 1199890.9414 | 2718341.9867 | 1199865.1464
8 | 2718319.1107 | 1199892.7359 | 2718320.5673 | 1199893.7877 | 2718329.3982 | 1199904.3369
9 | 2718329.3982 | 1199904.3369 | 2718360.5833 | 1200002.3926
10 | 2718164.433 | 1199817.0317 | 2718170.4966 | 1199820.8099 | 2718180.9884 | 1199817.0427
11 | 2718061.488 | 1199914.3797 | 2718062.068 | 1199914.1686 | 2718078.0029 | 1199906.7002 | 2718083.3545 | 1199904.7188
12 | 2718126.9739 | 1199903.8991 | 2718108.1309 | 1199901.2915 | 2718099.8083 | 1199901.227 | 2718091.5178 | 1199902.2306 | 2718084.5317 | 1199904.283 | 2718083.3545 | 1199904.7188
13 | 2718038.7707 | 1199918.4089 | 2718049.3311 | 1199918.1978 | 2718055.9543 | 1199916.3939 | 2718061.488 | 1199914.3797
14 | 2718126.9739 | 1199903.8991 | 2718129.9729 | 1199910.1407 | 2718133.2635 | 1199914.3422 | 2718142.0508 | 1199918.6412 | 2718143.3042 | 1199919.9558 | 2718143.5258 | 1199922.2285
15 | 2718126.9739 | 1199903.8991 | 2718164.433 | 1199817.0317
16 | 2718022.1687 | 1199920.2667 | 2718022.4019 | 1199920.134 | 2718026.9449 | 1199919.1564 | 2718032.829 | 1199918.5277 | 2718038.7707 | 1199918.4089
17 | 2718143.5258 | 1199922.2285 | 2718142.1599 | 1199923.9028 | 2718139.5801 | 1199924.9637 | 2718136.2443 | 1199924.5863
18 | 2718143.5258 | 1199922.2285 | 2718155.521 | 1199923.5674
19 | 2718022.1687 | 1199920.2667 | 2718018.6817 | 1199922.251 | 2718015.928 | 1199924.7874 | 2718014.66 | 1199926.9083
20 | 2718136.2443 | 1199924.5863 | 2718135.4713 | 1199926.3168 | 2718136.5933 | 1199928.8853 | 2718144.216 | 1199930.5772
21 | 2718136.2443 | 1199924.5863 | 2718123.8631 | 1199919.3236
22 | 2718165.5626 | 1199924.6882 | 2718155.521 | 1199923.5674
23 | 2718094.976 | 1199980.3125 | 2718096.0877 | 1199983.4691 | 2718097.2194 | 1199985.2337
24 | 2718092.2228 | 1199972.4958 | 2718094.976 | 1199980.3125
25 | 2718120.0166 | 1199997.6856 | 2718109.0136 | 1199993.7542 | 2718102.2746 | 1199991.019 | 2718098.6661 | 1199987.4896 | 2718097.2194 | 1199985.2337
26 | 2718092.2228 | 1199972.4958 | 2718088.6927 | 1199970.3912 | 2718081.6207 | 1199969.0838 | 2718063.7741 | 1199967.7081 | 2718053.8169 | 1199964.8093 | 2718044.4269 | 1199959.5729
27 | 2718159.1471 | 1200001.0615 | 2718156.7903 | 1200000.092 | 2718154.2947 | 1199999.5868 | 2718141.4154 | 1200000.0436 | 2718130.7089 | 1199999.2203 | 2718120.0166 | 1199997.6856
28 | 2718120.0166 | 1199997.6856 | 2718124.6791 | 1199991.8179 | 2718125.3847 | 1199989.6414 | 2718125.1771 | 1199987.0465 | 2718120.9201 | 1199977.5175
29 | 2718014.2692 | 1199929.7249 | 2718016.1009 | 1199935.3096 | 2718019.4085 | 1199940.9679 | 2718030.5254 | 1199952.2401 | 2718041.0416 | 1199957.6851 | 2718044.4269 | 1199959.5729
30 | 2718159.1471 | 1200001.0615 | 2718170.6225 | 1199997.6637 | 2718176.6206 | 1199995.503 | 2718183.353 | 1199990.8771
31 | 2718014.2692 | 1199929.7249 | 2718014.66 | 1199926.9083
32 | 2718183.353 | 1199990.8771 | 2718187.2828 | 1199988.1751 | 2718193.9842 | 1199983.5709 | 2718195.1801 | 1199983.0507
33 | 2718196.1366 | 1199982.6345 | 2718195.1801 | 1199983.0507

## bus_geodata
| x | y | coords
0 | 2718297.063 | 1199867.0847
1 | 2718284.5635 | 1199862.4744
2 | 2718325.7907 | 1199851.9383
3 | 2718241.1744 | 1199857.5588
4 | 2718210.7186 | 1199824.508
5 | 2718326.1908 | 1199890.9414
6 | 2718329.3982 | 1199904.3369
7 | 2718341.9867 | 1199865.1464
8 | 2718180.9884 | 1199817.0427
9 | 2718319.1107 | 1199892.7359
10 | 2718360.5833 | 1200002.3926
11 | 2718083.3545 | 1199904.7188
12 | 2718061.488 | 1199914.3797
13 | 2718126.9739 | 1199903.8991
14 | 2718038.7707 | 1199918.4089
15 | 2718143.5258 | 1199922.2285
16 | 2718164.433 | 1199817.0317
17 | 2718022.1687 | 1199920.2667
18 | 2718136.2443 | 1199924.5863
19 | 2718155.521 | 1199923.5674
20 | 2718094.976 | 1199980.3125
21 | 2718097.2194 | 1199985.2337
22 | 2718092.2228 | 1199972.4958
23 | 2718120.0166 | 1199997.6856
24 | 2718044.4269 | 1199959.5729
25 | 2718159.1471 | 1200001.0615
26 | 2718120.9201 | 1199977.5175
27 | 2718014.2692 | 1199929.7249
28 | 2718183.353 | 1199990.8771
29 | 2718014.66 | 1199926.9083
30 | 2718123.8631 | 1199919.3236
31 | 2718144.216 | 1199930.5772
32 | 2718195.1801 | 1199983.0507
33 | 2718196.1366 | 1199982.6345
34 | 2718165.5626 | 1199924.6882
35 | 2718165.5626 | 1199924.6882

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98599 | -0.098403 | 0.0017628 | 0.00044181
1 | 0.98608 | -0.097753 | 0 | 0
2 | 0.98585 | -0.099384 | 0.0008925 | 0.00022368
3 | 0.98524 | -0.10376 | 0.012699 | 0.0031827
4 | 0.98849 | -0.080663 | 0 | 0
5 | 0.9857 | -0.10046 | 0 | 0
6 | 0.98566 | -0.10075 | 0 | 0
7 | 0.98579 | -0.099825 | 0 | 0
8 | 0.98937 | -0.074434 | 0.0088404 | 0.0022156
9 | 0.98564 | -0.10093 | 0.0011454 | 0.00028706
10 | 0.98553 | -0.10169 | 0.00088516 | 0.00022184
11 | 0.99406 | -0.041489 | 0.0017416 | 0.00043649
12 | 0.99314 | -0.047909 | 0.0016206 | 0.00040617
13 | 0.99585 | -0.028872 | 0 | 0
14 | 0.99231 | -0.053794 | 0.0024133 | 0.00060484
15 | 0.99851 | -0.010327 | 0 | 0
16 | 0.99007 | -0.069539 | 0.016198 | 0.0040595
17 | 0.99176 | -0.057623 | 0.0036805 | 0.00092241
18 | 0.99834 | -0.011558 | 0 | 0
19 | 1 | 0 | -0.090617 | -0.022604
20 | 0.98923 | -0.075565 | 0.0035947 | 0.00090091
21 | 0.98915 | -0.07613 | 0.0031392 | 0.00078675
22 | 0.98939 | -0.0744 | 0 | 0
23 | 0.98887 | -0.078048 | 0 | 0
24 | 0.99039 | -0.067336 | 0.0025156 | 0.00063048
25 | 0.98856 | -0.080256 | 0 | 0
26 | 0.98882 | -0.07841 | 0.0015512 | 0.00038876
27 | 0.99142 | -0.060048 | 0 | 0
28 | 0.98835 | -0.081737 | 0 | 0
29 | 0.99149 | -0.059577 | 0.002521 | 0.00063182
30 | 0.99814 | -0.012952 | 0.010349 | 0.0025938
31 | 0.99826 | -0.012119 | 0.0044798 | 0.0011227
32 | 0.98824 | -0.082533 | 0.0028179 | 0.00070624
33 | 0.98824 | -0.082561 | 0.0026634 | 0.0006675
34 | 0.99995 | -0.00035449 | 0.0035147 | 0.00088086
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0046868 | -0.001172 | 0.0046872 | 0.001172 | 4.1965e-07 | -1.0109e-08 | 0.0070722 | 0.0070721 | 0.0070722 | 0.98599 | -0.098403 | 0.98608 | -0.097753 | 2.6193
1 | 0.002924 | 0.00073018 | -0.0029236 | -0.00073044 | 3.9445e-07 | -2.6244e-07 | 0.0044118 | 0.0044119 | 0.0044119 | 0.98599 | -0.098403 | 0.98585 | -0.099384 | 1.634
2 | 0.01271 | 0.0031862 | -0.012699 | -0.0031827 | 1.0571e-05 | 3.4788e-06 | 0.01918 | 0.01918 | 0.01918 | 0.98608 | -0.097753 | 0.98524 | -0.10376 | 7.1037
3 | -0.017397 | -0.0043582 | 0.017438 | 0.0043728 | 4.1214e-05 | 1.4626e-05 | 0.026252 | 0.026251 | 0.026252 | 0.98608 | -0.097753 | 0.98849 | -0.080663 | 9.7229
4 | 0.0020311 | 0.00050676 | -0.0020309 | -0.00050698 | 1.2304e-07 | -2.2031e-07 | 0.0030648 | 0.0030649 | 0.0030649 | 0.98585 | -0.099384 | 0.98579 | -0.099825 | 1.1352
5 | -0.017438 | -0.0043728 | 0.017453 | 0.0043782 | 1.5066e-05 | 5.345e-06 | 0.026251 | 0.026251 | 0.026251 | 0.98849 | -0.080663 | 0.98937 | -0.074434 | 9.7227
6 | 0.0020308 | 0.0005073 | -0.0020307 | -0.00050745 | 8.1035e-08 | -1.4503e-07 | 0.003065 | 0.0030651 | 0.0030651 | 0.9857 | -0.10046 | 0.98566 | -0.10075 | 1.1352
7 | -0.0020308 | -0.0005073 | 0.0020309 | 0.00050698 | 1.7731e-07 | -3.174e-07 | 0.003065 | 0.0030649 | 0.003065 | 0.9857 | -0.10046 | 0.98579 | -0.099825 | 1.1352
8 | 0.0011454 | 0.00028687 | -0.0011454 | -0.00028706 | 2.8984e-08 | -1.8685e-07 | 0.0017291 | 0.0017292 | 0.0017292 | 0.98566 | -0.10075 | 0.98564 | -0.10093 | 0.64043
9 | 0.00088528 | 0.00022058 | -0.00088516 | -0.00022184 | 1.1464e-07 | -1.2672e-06 | 0.001336 | 0.0013365 | 0.0013365 | 0.98566 | -0.10075 | 0.98553 | -0.10169 | 0.49499
10 | -0.026294 | -0.0065938 | 0.026312 | 0.0066004 | 1.7852e-05 | 6.6309e-06 | 0.039547 | 0.039547 | 0.039547 | 0.98937 | -0.074434 | 0.99007 | -0.069539 | 14.6471
11 | 0.026618 | 0.0066805 | -0.026594 | -0.0066717 | 2.3703e-05 | 8.8066e-06 | 0.039848 | 0.039848 | 0.039848 | 0.99406 | -0.041489 | 0.99314 | -0.047909 | 14.7586
12 | -0.02836 | -0.007117 | 0.028409 | 0.0071355 | 4.975e-05 | 1.856e-05 | 0.042455 | 0.042455 | 0.042455 | 0.99406 | -0.041489 | 0.99585 | -0.028872 | 15.7241
13 | 0.024974 | 0.0062655 | -0.024953 | -0.006258 | 2.0372e-05 | 7.5341e-06 | 0.03742 | 0.03742 | 0.03742 | 0.99314 | -0.047909 | 0.99231 | -0.053794 | 13.8593
14 | -0.071159 | -0.017887 | 0.071344 | 0.017957 | 0.00018426 | 7.0529e-05 | 0.10635 | 0.10635 | 0.10635 | 0.99585 | -0.028872 | 0.99851 | -0.010327 | 39.3873
15 | 0.04275 | 0.010751 | -0.042509 | -0.01066 | 0.00024097 | 9.1455e-05 | 0.063891 | 0.063891 | 0.063891 | 0.99585 | -0.028872 | 0.99007 | -0.069539 | 23.6634
16 | 0.02254 | 0.0056531 | -0.022528 | -0.0056488 | 1.196e-05 | 4.3834e-06 | 0.033801 | 0.033801 | 0.033801 | 0.99231 | -0.053794 | 0.99176 | -0.057623 | 12.519
17 | 0.014834 | 0.0037179 | -0.014831 | -0.0037171 | 2.5276e-06 | 8.6374e-07 | 0.022106 | 0.022106 | 0.022106 | 0.99851 | -0.010327 | 0.99834 | -0.011558 | 8.1874
18 | -0.086178 | -0.021675 | 0.086302 | 0.021723 | 0.00012427 | 4.7637e-05 | 0.12845 | 0.12845 | 0.12845 | 0.99851 | -0.010327 | 1 | 0 | 47.5746
19 | 0.018847 | 0.0047263 | -0.018842 | -0.0047245 | 5.1035e-06 | 1.8309e-06 | 0.028279 | 0.028279 | 0.028279 | 0.99176 | -0.057623 | 0.99149 | -0.059577 | 10.4738
20 | 0.0044801 | 0.0011227 | -0.0044798 | -0.0011227 | 3.4797e-07 | -2.968e-08 | 0.0066775 | 0.0066776 | 0.0066776 | 0.99834 | -0.011558 | 0.99826 | -0.012119 | 2.4732
21 | 0.010351 | 0.0025943 | -0.010349 | -0.0025938 | 1.9983e-06 | 5.9269e-07 | 0.015428 | 0.015428 | 0.015428 | 0.99834 | -0.011558 | 0.99814 | -0.012952 | 5.7143
22 | 0.0035148 | 0.00088079 | -0.0035147 | -0.00088086 | 1.7246e-07 | -6.6218e-08 | 0.0052301 | 0.0052301 | 0.0052301 | 1 | 0 | 0.99995 | -0.00035449 | 1.9371
23 | 0.010178 | 0.0025499 | -0.010177 | -0.0025496 | 7.9605e-07 | 2.363e-07 | 0.015309 | 0.015309 | 0.015309 | 0.98923 | -0.075565 | 0.98915 | -0.07613 | 5.6702
24 | -0.013772 | -0.0034508 | 0.013775 | 0.0034515 | 2.2194e-06 | 7.4721e-07 | 0.020717 | 0.020717 | 0.020717 | 0.98923 | -0.075565 | 0.98939 | -0.0744 | 7.6728
25 | 0.0070378 | 0.0017629 | -0.007036 | -0.0017625 | 1.8664e-06 | 3.754e-07 | 0.010587 | 0.010587 | 0.010587 | 0.98915 | -0.07613 | 0.98887 | -0.078048 | 3.9212
26 | -0.013775 | -0.0034515 | 0.013788 | 0.0034561 | 1.3477e-05 | 4.5364e-06 | 0.020717 | 0.020716 | 0.020717 | 0.98939 | -0.0744 | 0.99039 | -0.067336 | 7.6728
27 | 0.0054847 | 0.001374 | -0.005483 | -0.0013739 | 1.675e-06 | 1.388e-07 | 0.008253 | 0.0082531 | 0.0082531 | 0.98887 | -0.078048 | 0.98856 | -0.080256 | 3.0567
28 | 0.0015513 | 0.0003885 | -0.0015512 | -0.00038876 | 7.7594e-08 | -2.6293e-07 | 0.0023342 | 0.0023343 | 0.0023343 | 0.98887 | -0.078048 | 0.98882 | -0.07841 | 0.86454
29 | -0.016304 | -0.0040865 | 0.01632 | 0.0040923 | 1.6468e-05 | 5.7673e-06 | 0.024496 | 0.024496 | 0.024496 | 0.99039 | -0.067336 | 0.99142 | -0.060048 | 9.0726
30 | 0.005483 | 0.0013739 | -0.0054819 | -0.0013738 | 1.1241e-06 | 9.3347e-08 | 0.0082531 | 0.0082533 | 0.0082533 | 0.98856 | -0.080256 | 0.98835 | -0.081737 | 3.0568
31 | -0.01632 | -0.0040923 | 0.016321 | 0.0040927 | 1.0647e-06 | 3.7283e-07 | 0.024496 | 0.024496 | 0.024496 | 0.99142 | -0.060048 | 0.99149 | -0.059577 | 9.0725
32 | 0.0054819 | 0.0013738 | -0.0054813 | -0.0013737 | 6.0374e-07 | 5.0196e-08 | 0.0082533 | 0.0082533 | 0.0082533 | 0.98835 | -0.081737 | 0.98824 | -0.082533 | 3.0568
33 | 0.0026634 | 0.00066749 | -0.0026634 | -0.0006675 | 1.0468e-08 | -9.3389e-09 | 0.0040103 | 0.0040103 | 0.0040103 | 0.98824 | -0.082533 | 0.98824 | -0.082561 | 1.4853

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.095759 | 0.023893

## res_load
| p_mw | q_mvar
0 | 0.0017628 | 0.00044181
1 | 0.0008925 | 0.00022368
2 | 0.012699 | 0.0031827
3 | 0.0088404 | 0.0022156
4 | 0.0011454 | 0.00028706
5 | 0.00088516 | 0.00022184
6 | 0.0017416 | 0.00043649
7 | 0.0016206 | 0.00040617
8 | 0.0024133 | 0.00060484
9 | 0.016198 | 0.0040595
10 | 0.0036805 | 0.00092241
11 | 0.0051425 | 0.0012888
12 | 0.0035947 | 0.00090091
13 | 0.0031392 | 0.00078675
14 | 0.0025156 | 0.00063048
15 | 0.0015512 | 0.00038876
16 | 0.002521 | 0.00063182
17 | 0.010349 | 0.0025938
18 | 0.0044798 | 0.0011227
19 | 0.0028179 | 0.00070624
20 | 0.0026634 | 0.0006675
21 | 0.0035147 | 0.00088086

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1