## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-92_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-92_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1631-92_0_3_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1631-92_0_3_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1631-92_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1631-92_0_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1631-92_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1631-92_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1631-92_0_3_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_1631-92_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1631-92_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1631-92_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1631-92_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1631-92_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1631-92_0_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1631-92_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1631-92_0_3_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1631-92_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1631-92_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1631-92_0_3_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1631-92_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1631-92_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1631-92_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1631-92_0_3_node_122 | 0.4 | n |  | TRUE
24 | bus_LV_1631-92_0_3_node_121 | 0.4 | n |  | TRUE
25 | bus_LV_1631-92_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1631-92_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1631-92_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1631-92_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1631-92_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1631-92_0_3_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1631-92_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1631-92_0_3_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1631-92_0_3_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1631-92_0_3_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1631-92_0_3_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_1631-92_0_3_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_1631-92_0_3_node_123 | 0.4 | n |  | TRUE
38 | bus_LV_1631-92_0_3_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_1631-92_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_1631-92_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1631-92_0_3_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_1631-92_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1631-92_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1631-92_0_3_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_1631-92_0_3_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_1631-92_0_3_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_1631-92_0_3_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_1631-92_0_3_node_47 | 0.4 | n |  | TRUE
49 | bus_LV_1631-92_0_3_node_119 | 0.4 | n |  | TRUE
50 | bus_LV_1631-92_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_1631-92_0_3_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_1631-92_0_3_node_126 | 0.4 | n |  | TRUE
53 | bus_LV_1631-92_0_3_node_118 | 0.4 | n |  | TRUE
54 | bus_LV_1631-92_0_3_node_120 | 0.4 | n |  | TRUE
55 | bus_LV_1631-92_0_3_node_124 | 0.4 | n |  | TRUE
56 | bus_LV_1631-92_0_3_node_125 | 0.4 | n |  | TRUE
57 | bus_MV_13_0_node_141 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-92_0_3_load_0 | 0 | 0.00023758 | 5.9544e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-92_0_3_load_7 | 3 | 0.00033481 | 8.3912e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-92_0_3_load_5 | 4 | 0.00032926 | 8.2521e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-92_0_3_load_26 | 8 | 0.00049794 | 0.0001248 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-92_0_3_load_9 | 9 | 0.00032993 | 8.2688e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-92_0_3_load_15 | 14 | 0.00045869 | 0.00011496 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-92_0_3_load_16 | 15 | 0.00029818 | 7.473e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-92_0_3_load_23 | 16 | 0.00032924 | 8.2515e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-92_0_3_load_17 | 17 | 0.00024972 | 6.2585e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-92_0_3_load_19 | 19 | 0.00023376 | 5.8585e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-92_0_3_load_122 | 23 | 0.0013836 | 0.00034676 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-92_0_3_load_121 | 24 | 0.001003 | 0.00025137 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-92_0_3_load_27 | 27 | 0.003088 | 0.00077392 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-92_0_3_load_30 | 30 | 0.0098547 | 0.0024698 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-92_0_3_load_31 | 31 | 0.0037395 | 0.0009372 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-92_0_3_load_32 | 32 | 0.0023751 | 0.00059525 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-92_0_3_load_39 | 35 | 0.0014528 | 0.0003641 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-92_0_3_load_38 | 36 | 0.0019364 | 0.0004853 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-92_0_3_load_35 | 38 | 0.0014579 | 0.00036539 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-92_0_3_load_36 | 39 | 0.001914 | 0.0004797 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-92_0_3_load_37 | 40 | 0.0018526 | 0.00046431 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-92_0_3_load_41 | 43 | 0.0016952 | 0.00042485 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-92_0_3_load_42 | 44 | 0.015978 | 0.0040044 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-92_0_3_load_46 | 47 | 0.0010892 | 0.00027297 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-92_0_3_load_47 | 48 | 0.0014079 | 0.00035285 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-92_0_3_load_48 | 50 | 0.0016351 | 0.00040979 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-92_0_3_load_126 | 52 | 0.0029897 | 0.0007493 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-92_0_3_load_118 | 53 | 0.0013434 | 0.00033669 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-92_0_3_load_120 | 54 | 0.0099868 | 0.0025029 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-92_0_3_load_124 | 55 | 0.0034403 | 0.00086223 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-92_0_3_load_125 | 56 | 0.0051509 | 0.0012909 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-92_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.40608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-92_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.010894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-92_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.30502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-92_0_3_line_3 | NAYY 4x150 SE | 3 | 7 | 0.030963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-92_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.19885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-92_0_3_line_5 | NAYY 4x150 SE | 5 | 12 | 0.32667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-92_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.32475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-92_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.11492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-92_0_3_line_8 | NAYY 4x150 SE | 8 | 26 | 0.025799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-92_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.15663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-92_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.032165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-92_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.17265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-92_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.046633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-92_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.23749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-92_0_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.068182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-92_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.016299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-92_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.10146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-92_0_3_line_17 | NAYY 4x150 SE | 16 | 25 | 0.059232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-92_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.032791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-92_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.011078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-92_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.25506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-92_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.2871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-92_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.14094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-92_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.036512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-92_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.031093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-92_0_3_line_25 | NAYY 4x150 SE | 24 | 46 | 0.062031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-92_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.13174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-92_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.018834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-92_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.014639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-92_0_3_line_29 | NAYY 4x150 SE | 28 | 30 | 0.015874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-92_0_3_line_30 | NAYY 4x150 SE | 28 | 31 | 0.018395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-92_0_3_line_31 | NAYY 4x150 SE | 29 | 32 | 0.01196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-92_0_3_line_32 | NAYY 4x150 SE | 29 | 33 | 0.17055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-92_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.047229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-92_0_3_line_34 | NAYY 4x150 SE | 33 | 35 | 0.033459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-92_0_3_line_35 | NAYY 4x150 SE | 33 | 36 | 0.023646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-92_0_3_line_36 | NAYY 4x150 SE | 34 | 37 | 0.024909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-92_0_3_line_37 | NAYY 4x150 SE | 35 | 41 | 0.0065166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-92_0_3_line_38 | NAYY 4x150 SE | 36 | 39 | 0.00024432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-92_0_3_line_39 | NAYY 4x150 SE | 37 | 55 | 0.05961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-92_0_3_line_40 | NAYY 4x150 SE | 37 | 51 | 0.41184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-92_0_3_line_41 | NAYY 4x150 SE | 38 | 39 | 0.027916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-92_0_3_line_42 | NAYY 4x150 SE | 38 | 40 | 0.0018976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-92_0_3_line_43 | NAYY 4x150 SE | 41 | 42 | 0.014699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-92_0_3_line_44 | NAYY 4x150 SE | 42 | 46 | 0.3297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-92_0_3_line_45 | NAYY 4x150 SE | 42 | 43 | 0.02658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-92_0_3_line_46 | NAYY 4x150 SE | 43 | 44 | 0.025225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1631-92_0_3_line_47 | NAYY 4x150 SE | 44 | 45 | 0.029046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1631-92_0_3_line_48 | NAYY 4x150 SE | 45 | 47 | 0.014414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1631-92_0_3_line_49 | NAYY 4x150 SE | 45 | 48 | 0.074227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1631-92_0_3_line_50 | NAYY 4x150 SE | 46 | 49 | 0.088259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1631-92_0_3_line_51 | NAYY 4x150 SE | 48 | 50 | 0.0086336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1631-92_0_3_line_52 | NAYY 4x150 SE | 49 | 54 | 0.062498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1631-92_0_3_line_53 | NAYY 4x150 SE | 49 | 53 | 0.014407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1631-92_0_3_line_54 | NAYY 4x150 SE | 51 | 52 | 0.049385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1631-92_0_3_line_55 | NAYY 4x150 SE | 55 | 56 | 0.016265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-92_0_3_trafo_44 | 0.25 MVA 20/0.4 kV | 57 | 45 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37
0 | 2720667.7267 | 1197922.4725 | 2720682.8904 | 1197914.7729 | 2720693.0779 | 1197909.0298 | 2720699.5594 | 1197904.2127 | 2720714.9345 | 1197886.4323 | 2720727.3441 | 1197874.0293 | 2720731.6011 | 1197869.2117 | 2720736.6039 | 1197862.1742 | 2720751.2344 | 1197849.2046 | 2720762.532 | 1197837.1683 | 2720772.345 | 1197827.7263 | 2720777.715 | 1197824.3878 | 2720791.0562 | 1197817.1632 | 2720823.8342 | 1197804.5717 | 2720830.8766 | 1197802.1679 | 2720835.6912 | 1197801.0532 | 2720846.616 | 1197800.6849 | 2720852.7297 | 1197799.7522 | 2720864.3995 | 1197794.9401 | 2720869.0228 | 1197791.6089 | 2720872.9144 | 1197787.1621 | 2720875.6974 | 1197782.1591 | 2720876.2485 | 1197778.2674 | 2720874.9555 | 1197773.6378 | 2720867.3563 | 1197763.6435 | 2720864.5817 | 1197759.1953 | 2720863.2812 | 1197754.5656 | 2720863.2837 | 1197750.6739 | 2720869.3981 | 1197729.7488 | 2720870.1347 | 1197722.336 | 2720870.5081 | 1197699.738 | 2720871.6186 | 1197694.5567 | 2720873.8414 | 1197689.3756 | 2720877.5468 | 1197685.8479 | 2720881.2477 | 1197680.6633 | 2720884.9519 | 1197673.811 | 2720887.1782 | 1197667.329 | 2720893.2208 | 1197644.8319
1 | 2720657.9898 | 1197927.4129 | 2720667.7267 | 1197922.4725
2 | 2720657.9898 | 1197927.4129 | 2720656.8769 | 1197916.1266 | 2720659.1018 | 1197906.6757 | 2720668.7294 | 1197900.7434 | 2720679.4732 | 1197885.5602 | 2720687.2509 | 1197873.1525 | 2720692.6457 | 1197857.2609 | 2720588.976 | 1197924.3517 | 2720564.8404 | 1197941.7555 | 2720563.4171 | 1197930.7409 | 2720536.4921 | 1197936.8692 | 2720521.6723 | 1197941.1291 | 2720515.3753 | 1197939.4565 | 2720507.3052 | 1197936.1164
3 | 2720478.3334 | 1197926.3115 | 2720483.1521 | 1197926.1195 | 2720507.3052 | 1197936.1164
4 | 2720535.4086 | 1197647.6906 | 2720568.0941 | 1197631.0151 | 2720586.2947 | 1197661.6157 | 2720601.293 | 1197639.1128 | 2720627.4898 | 1197595.9096 | 2720636.29 | 1197600.4126 | 2720641.895 | 1197614.1136 | 2720648.5344 | 1197637.4868
5 | 2720535.4086 | 1197647.6906 | 2720535.2079 | 1197656.1261 | 2720532.0458 | 1197661.0548 | 2720528.3409 | 1197666.8288 | 2720524.0835 | 1197670.5346 | 2720498.8926 | 1197680.5342 | 2720475.1848 | 1197693.3103 | 2720470.9274 | 1197697.0161 | 2720454.815 | 1197718.5073 | 2720443.1486 | 1197731.0926 | 2720436.0667 | 1197733.9521 | 2720444.6262 | 1197739.8066 | 2720446.0996 | 1197742.3047 | 2720428.3315 | 1197752.5877 | 2720422.9612 | 1197754.0584 | 2720404.4409 | 1197755.1751 | 2720392.5809 | 1197760.3623 | 2720386.2888 | 1197762.2148 | 2720382.9532 | 1197765.172 | 2720377.5835 | 1197777.5841 | 2720373.3229 | 1197782.5909 | 2720359.2429 | 1197789.0678 | 2720354.62 | 1197792.3994 | 2720351.2815 | 1197797.7694 | 2720347.3926 | 1197807.7763 | 2720341.4669 | 1197829.2617 | 2720338.3149 | 1197834.0795 | 2720333.1289 | 1197838.8898 | 2720327.7593 | 1197850.9239
6 | 2720478.3334 | 1197926.3115 | 2720474.8145 | 1197928.1641 | 2720467.7817 | 1197934.6383 | 2720460.1873 | 1197937.2316 | 2720451.1144 | 1197938.7166 | 2720440.1834 | 1197942.0544 | 2720432.4029 | 1197945.5669 | 2720417.4031 | 1197956.495 | 2720390.9132 | 1197972.4288 | 2720386.0992 | 1197974.2777 | 2720381.1057 | 1197974.8331 | 2720365.9143 | 1197973.3484 | 2720359.6179 | 1197973.5329 | 2720335.1672 | 1197983.17 | 2720330.5366 | 1197985.7565 | 2720328.8698 | 1197989.8371 | 2720327.3887 | 1198000.2037 | 2720324.9849 | 1198008.7283 | 2720322.022 | 1198009.8361 | 2720320.9152 | 1197998.2165 | 2720317.7839 | 1197989.1468 | 2720316.8205 | 1197980.2431 | 2720318.6755 | 1197971.3517 | 2720328.6921 | 1197960.4564 | 2720343.3195 | 1197930.9402 | 2720362.2106 | 1197915.9317 | 2720366.284 | 1197910.7543 | 2720368.5056 | 1197903.7161 | 2720368.6922 | 1197894.0795
7 | 2720368.6922 | 1197894.0795 | 2720359.6155 | 1197904.8269 | 2720335.7232 | 1197920.0126 | 2720328.5042 | 1197927.4172 | 2720322.3874 | 1197929.2733 | 2720317.2006 | 1197931.8597 | 2720313.8726 | 1197934.8282 | 2720307.5762 | 1197944.0861 | 2720304.2406 | 1197946.6764 | 2720293.6831 | 1197950.0109 | 2720287.388 | 1197953.5313 | 2720281.8328 | 1197959.2793 | 2720280.3128 | 1197962.8213
8 | 2720274.2348 | 1197987.7918 | 2720277.0112 | 1197978.5409 | 2720279.0512 | 1197965.7614 | 2720280.3128 | 1197962.8213
9 | 2720166.6309 | 1197912.2283 | 2720153.2934 | 1197917.0415 | 2720134.5879 | 1197928.5296 | 2720121.486 | 1197940.1972 | 2720110.5092 | 1197951.1291 | 2720106.6195 | 1197958.1672 | 2720103.1047 | 1197968.5376 | 2720098.8429 | 1197977.7921 | 2720086.4364 | 1197985.5708 | 2720080.2742 | 1197994.9984 | 2720072.7283 | 1198003.9089 | 2720058.0979 | 1198012.7994 | 2720055.9629 | 1198015.6687
10 | 2720030.1322 | 1198030.2062 | 2720034.8605 | 1198029.5785 | 2720046.7997 | 1198027.9837 | 2720055.9629 | 1198015.6687
11 | 2720166.6309 | 1197912.2283 | 2720181.4459 | 1197906.2995 | 2720201.2662 | 1197900.7494 | 2720218.4887 | 1197894.8247 | 2720237.938 | 1197885.3755 | 2720256.8285 | 1197878.3391 | 2720265.5319 | 1197876.6685 | 2720277.3867 | 1197869.4462 | 2720284.0514 | 1197866.4892 | 2720291.2729 | 1197864.6331 | 2720312.5775 | 1197855.3772 | 2720327.7593 | 1197850.9239
12 | 2720035.792 | 1198076.4871 | 2720030.1322 | 1198030.2062
13 | 2720327.7593 | 1197850.9239 | 2720283.3138 | 1197887.234 | 2720279.0533 | 1197891.8628 | 2720269.2319 | 1197906.3092 | 2720252.01 | 1197922.0521 | 2720249.9407 | 1197926.8251 | 2720247.5656 | 1197941.1211 | 2720243.1232 | 1197956.3096 | 2720239.9755 | 1197979.4633 | 2720241.0826 | 1197985.0229 | 2720245.5266 | 1197990.95 | 2720251.0848 | 1198009.6533 | 2720248.1247 | 1198026.1392 | 2720246.872 | 1198050.8887
14 | 2720035.792 | 1198076.4871 | 2720029.5746 | 1198068.9568 | 2720021.831 | 1198066.0992 | 2720010.3024 | 1198064.7001 | 2720003.4885 | 1198064.1073 | 2719998.0918 | 1198065.778 | 2719989.2542 | 1198071.1157 | 2719984.5103 | 1198075.5571 | 2719981.4675 | 1198080.2661 | 2719981.1537 | 1198083.8832
15 | 2720246.872 | 1198050.8887 | 2720246.822 | 1198051.8763 | 2720249.0488 | 1198065.7646 | 2720249.4626 | 1198066.9384
16 | 2719981.1537 | 1198083.8832 | 2719980.8628 | 1198087.2369 | 2719984.9439 | 1198101.3847 | 2719987.056 | 1198116.4603 | 2719988.8548 | 1198128.1717 | 2719987.8187 | 1198147.8987 | 2719986.3064 | 1198153.0277 | 2719984.6488 | 1198156.2857 | 2719981.1455 | 1198156.6156 | 2719977.674 | 1198153.4659 | 2719972.769 | 1198146.9627 | 2719962.9277 | 1198141.6397
17 | 2720274.7202 | 1198118.453 | 2720269.8412 | 1198116.3533 | 2720266.1888 | 1198112.7327 | 2720264.3403 | 1198108.8149 | 2720261.1548 | 1198099.4106 | 2720256.0126 | 1198085.786 | 2720250.7424 | 1198070.5689 | 2720249.4626 | 1198066.9384
18 | 2719943.7717 | 1198157.7443 | 2719942.4063 | 1198153.2803 | 2719944.4229 | 1198147.3164 | 2719947.5823 | 1198142.8654 | 2719954.1486 | 1198139.8505 | 2719960.3645 | 1198140.2533 | 2719962.9277 | 1198141.6397
19 | 2719943.7717 | 1198157.7443 | 2719949.9944 | 1198166.9092
20 | 2719880.1079 | 1198275.0534 | 2719883.6279 | 1198260.9803 | 2719883.2641 | 1198257.0924 | 2719873.2602 | 1198246.1616 | 2719867.5192 | 1198236.9064 | 2719864.5562 | 1198230.053 | 2719861.7743 | 1198211.8951 | 2719861.4048 | 1198204.4934 | 2719864.0015 | 1198187.0771 | 2719870.1115 | 1198172.6335 | 2719876.2223 | 1198152.0743 | 2719879.9237 | 1198127.4415 | 2719881.4045 | 1198125.7811 | 2719884.1839 | 1198130.7738 | 2719892.8873 | 1198138.1871 | 2719898.635 | 1198145.5967 | 2719902.8954 | 1198149.296 | 2719907.1507 | 1198150.5934 | 2719909.9307 | 1198149.8597 | 2719912.7121 | 1198151.3388 | 2719926.9685 | 1198172.8183 | 2719930.4857 | 1198175.9689 | 2719935.4869 | 1198176.1583 | 2719941.9045 | 1198174.0966 | 2719946.7857 | 1198170.781 | 2719949.9944 | 1198166.9092
21 | 2719736.5954 | 1198157.9695 | 2719739.3428 | 1198149.7407 | 2719741.5612 | 1198145.482 | 2719745.8333 | 1198146.7018 | 2719750.648 | 1198147.0763 | 2719750.9672 | 1198151.6749 | 2719752.9698 | 1198154.0056 | 2719757.5019 | 1198157.0765 | 2719773.0647 | 1198162.8146 | 2719778.6164 | 1198166.7065 | 2719782.1345 | 1198171.3359 | 2719786.0239 | 1198187.0809 | 2719787.3239 | 1198196.714 | 2719791.0261 | 1198203.9379 | 2719793.8017 | 1198201.9032 | 2719796.4003 | 1198196.1621 | 2719811.3988 | 1198178.3719 | 2719817.5095 | 1198173.0015 | 2719816.4017 | 1198189.4914 | 2719818.4394 | 1198196.5263 | 2719822.142 | 1198189.6732 | 2719825.8466 | 1198186.523 | 2719830.4775 | 1198185.048 | 2719832.6981 | 1198200.048 | 2719840.4788 | 1198212.8244 | 2719847.6976 | 1198222.087 | 2719851.4065 | 1198227.8322 | 2719854.549 | 1198235.234 | 2719857.1432 | 1198243.3809 | 2719859.927 | 1198250.0527 | 2719863.2549 | 1198255.4233 | 2719867.5156 | 1198259.8676 | 2719872.5181 | 1198262.6477 | 2719875.6698 | 1198265.7909 | 2719880.1079 | 1198275.0534
22 | 2719632.1531 | 1198122.5639 | 2719636.313 | 1198123.3032 | 2719641.7441 | 1198123.7122 | 2719655.0245 | 1198119.4193 | 2719677.4348 | 1198108.4932 | 2719688.3574 | 1198105.5319 | 2719697.8052 | 1198107.7449 | 2719719.7235 | 1198128.599 | 2719733.7376 | 1198140.1548 | 2719741.5612 | 1198145.482 | 2719739.3428 | 1198149.7407 | 2719736.5954 | 1198157.9695
23 | 2719630.4412 | 1198086.3142 | 2719632.1135 | 1198094.487 | 2719631.4666 | 1198101.3013 | 2719632.5728 | 1198114.9223 | 2719632.1531 | 1198122.5639
24 | 2719632.1531 | 1198122.5639 | 2719625.7568 | 1198120.9014 | 2719615.199 | 1198115.5306 | 2719602.7917 | 1198113.1251
25 | 2719543.5603 | 1198109.7491 | 2719559.8207 | 1198117.1908 | 2719567.0435 | 1198119.0477 | 2719572.9745 | 1198119.6001 | 2719578.3486 | 1198119.0516 | 2719591.495 | 1198114.6002 | 2719596.8688 | 1198113.3068 | 2719602.7917 | 1198113.1251
26 | 2720274.7202 | 1198118.453 | 2720271.2569 | 1198102.794 | 2720269.1646 | 1198082.2258 | 2720269.2376 | 1198073.6765 | 2720270.9961 | 1198054.8203 | 2720274.9709 | 1198029.9375 | 2720275.7009 | 1198021.3014 | 2720274.1771 | 1198005.7927 | 2720273.4396 | 1197994.3695 | 2720274.2348 | 1197987.7918
27 | 2719174.6421 | 1198308.2846 | 2719157.9655 | 1198317.0363
28 | 2719145.0035 | 1198323.8386 | 2719157.9655 | 1198317.0363
29 | 2719174.6421 | 1198308.2846 | 2719167.8495 | 1198293.9369
30 | 2719191.651 | 1198310.6588 | 2719186.2089 | 1198306.992 | 2719181.1172 | 1198306.379 | 2719174.6421 | 1198308.2846
31 | 2719145.0035 | 1198323.8386 | 2719150.2799 | 1198334.5721
32 | 2719145.0035 | 1198323.8386 | 2719123.2459 | 1198279.5838 | 2719116.1823 | 1198265.5439 | 2719113.2682 | 1198258.8699 | 2719154.1855 | 1198240.0604 | 2719162.5203 | 1198236.5795 | 2719203.2804 | 1198219.5574
33 | 2719173.8303 | 1198375.3285 | 2719170.1428 | 1198370.7739 | 2719162.0388 | 1198358.4923 | 2719150.2799 | 1198334.5721
34 | 2719203.2804 | 1198219.5574 | 2719227.8775 | 1198210.4523 | 2719235.0491 | 1198209.528
35 | 2719203.2804 | 1198219.5574 | 2719214.2948 | 1198240.4815
36 | 2719190.4552 | 1198393.8846 | 2719180.7441 | 1198383.8837 | 2719173.8303 | 1198375.3285
37 | 2719241.4633 | 1198210.679 | 2719235.0491 | 1198209.528
38 | 2719214.4086 | 1198240.6977 | 2719214.2948 | 1198240.4815
39 | 2719190.4552 | 1198393.8846 | 2719221.1718 | 1198342.7981
40 | 2719190.4552 | 1198393.8846 | 2719232.5754 | 1198437.2896 | 2719251.0354 | 1198457.7727 | 2719262.4246 | 1198476.0466 | 2719270.0341 | 1198492.8552 | 2719277.3028 | 1198514.9052 | 2719285.2 | 1198545.1515 | 2719291.1933 | 1198568.8885 | 2719293.6761 | 1198579.2123 | 2719296.8608 | 1198591.3847 | 2719300.2443 | 1198601.6153 | 2719304.6255 | 1198611.4766 | 2719308.2303 | 1198618.6315 | 2719314.0653 | 1198628.5441 | 2719321.6056 | 1198639.2691 | 2719327.8451 | 1198646.8548 | 2719334.5652 | 1198654.0164 | 2719341.242 | 1198660.2987 | 2719348.9909 | 1198666.6803 | 2719358.8218 | 1198673.6928 | 2719366.3923 | 1198678.3251 | 2719375.8525 | 1198683.3066 | 2719386.7269 | 1198688.0383 | 2719395.9321 | 1198691.2912 | 2719417.3012 | 1198697.6449 | 2719420.062 | 1198684.9018
41 | 2719227.412 | 1198265.4002 | 2719214.4086 | 1198240.6977
42 | 2719227.412 | 1198265.4002 | 2719228.2959 | 1198267.0794
43 | 2719255.3071 | 1198215.5365 | 2719249.7915 | 1198212.8801 | 2719241.4633 | 1198210.679
44 | 2719255.3071 | 1198215.5365 | 2719276.4829 | 1198210.6776 | 2719309.2981 | 1198195.1766 | 2719319.5503 | 1198191.0559 | 2719323.1852 | 1198190.617 | 2719327.7588 | 1198191.6202 | 2719329.5803 | 1198192.724 | 2719341.1524 | 1198206.4317 | 2719344.5289 | 1198206.3434 | 2719348.4174 | 1198205.4093 | 2719364.7509 | 1198193.9381 | 2719372.4324 | 1198190.3777 | 2719382.962 | 1198187.6304 | 2719402.1959 | 1198178.5523 | 2719409.8232 | 1198175.0354 | 2719421.1187 | 1198174.7497 | 2719432.0455 | 1198177.6701 | 2719436.3919 | 1198177.0787 | 2719443.7529 | 1198174.6907 | 2719452.1502 | 1198171.1448 | 2719459.7366 | 1198164.725 | 2719467.5506 | 1198154.5403 | 2719470.584 | 1198151.0428 | 2719487.5862 | 1198141.1976 | 2719493.9877 | 1198135.3658 | 2719506.5851 | 1198130.9365 | 2719511.0461 | 1198127.6678 | 2719520.0322 | 1198120.2086 | 2719543.5603 | 1198109.7491
45 | 2719255.3071 | 1198215.5365 | 2719275.1727 | 1198226.3184 | 2719278.1362 | 1198228.9708
46 | 2719278.1362 | 1198228.9708 | 2719284.5503 | 1198234.7116 | 2719295.9227 | 1198246.8278
47 | 2719318.9861 | 1198262.786 | 2719311.2038 | 1198261.1072 | 2719307.3008 | 1198258.95 | 2719295.9227 | 1198246.8278
48 | 2719318.9861 | 1198262.786 | 2719327.5916 | 1198274.3662
49 | 2719318.9861 | 1198262.786 | 2719333.606 | 1198262.3441 | 2719342.0078 | 1198260.8552 | 2719349.4973 | 1198259.2702 | 2719357.4735 | 1198258.8736 | 2719366.1189 | 1198260.8254 | 2719374.9621 | 1198265.839 | 2719383.4651 | 1198276.8168 | 2719385.3724 | 1198278.4511
50 | 2719543.5603 | 1198109.7491 | 2719549.7703 | 1198101.6896 | 2719555.0663 | 1198090.1982 | 2719559.2602 | 1198074.3928 | 2719559.652 | 1198060.1457 | 2719559.0455 | 1198049.3368 | 2719558.0832 | 1198044.8921 | 2719557.2743 | 1198041.151 | 2719553.4033 | 1198032.445 | 2719550.817 | 1198026.9225
51 | 2719391.9283 | 1198284.0689 | 2719385.3724 | 1198278.4511
52 | 2719550.817 | 1198026.9225 | 2719551.8327 | 1198021.8503 | 2719554.742 | 1198019.6068 | 2719557.163 | 1198018.5433 | 2719568.8422 | 1198019.2774 | 2719571.8638 | 1198019.0377 | 2719573.2133 | 1198017.8415 | 2719573.6652 | 1198015.8158 | 2719573.0054 | 1198013.0005 | 2719567.5584 | 1198009.578 | 2719558.8382 | 1198006.4013 | 2719548.706 | 1197996.8806
53 | 2719550.817 | 1198026.9225 | 2719536.7523 | 1198030.0436
54 | 2719420.062 | 1198684.9018 | 2719428.3254 | 1198644.5818 | 2719430.0313 | 1198636.5334
55 | 2719219.9974 | 1198328.9484 | 2719224.8479 | 1198336.6842 | 2719221.1718 | 1198342.7981

## bus_geodata
| x | y | coords
0 | 2720893.2208 | 1197644.8319
1 | 2720667.7267 | 1197922.4725
2 | 2720657.9898 | 1197927.4129
3 | 2720507.3052 | 1197936.1164
4 | 2720648.5344 | 1197637.4868
5 | 2720535.4086 | 1197647.6906
6 | 2720368.6922 | 1197894.0795
7 | 2720478.3334 | 1197926.3115
8 | 2720280.3128 | 1197962.8213
9 | 2720055.9629 | 1198015.6687
10 | 2720166.6309 | 1197912.2283
11 | 2720030.1322 | 1198030.2062
12 | 2720327.7593 | 1197850.9239
13 | 2720035.7921 | 1198076.4871
14 | 2720246.872 | 1198050.8887
15 | 2719981.1537 | 1198083.8832
16 | 2720249.4626 | 1198066.9384
17 | 2719962.9277 | 1198141.6397
18 | 2719943.7717 | 1198157.7443
19 | 2719949.9944 | 1198166.9092
20 | 2719880.1079 | 1198275.0534
21 | 2719736.5954 | 1198157.9695
22 | 2719632.1531 | 1198122.5639
23 | 2719630.4412 | 1198086.3142
24 | 2719602.7917 | 1198113.1251
25 | 2720274.7202 | 1198118.453
26 | 2720274.2348 | 1197987.7918
27 | 2719157.9655 | 1198317.0363
28 | 2719174.6421 | 1198308.2846
29 | 2719145.0035 | 1198323.8386
30 | 2719167.8495 | 1198293.9369
31 | 2719191.651 | 1198310.6588
32 | 2719150.2799 | 1198334.5721
33 | 2719203.2804 | 1198219.5574
34 | 2719173.8303 | 1198375.3285
35 | 2719235.0491 | 1198209.528
36 | 2719214.2948 | 1198240.4815
37 | 2719190.4552 | 1198393.8846
38 | 2719227.412 | 1198265.4002
39 | 2719214.4086 | 1198240.6977
40 | 2719228.2959 | 1198267.0794
41 | 2719241.4633 | 1198210.679
42 | 2719255.3071 | 1198215.5365
43 | 2719278.1361 | 1198228.9708
44 | 2719295.9227 | 1198246.8278
45 | 2719318.9862 | 1198262.786
46 | 2719543.5603 | 1198109.7491
47 | 2719327.5916 | 1198274.3662
48 | 2719385.3724 | 1198278.4511
49 | 2719550.817 | 1198026.9225
50 | 2719391.9283 | 1198284.0689
51 | 2719420.062 | 1198684.9018
52 | 2719430.0313 | 1198636.5334
53 | 2719536.7523 | 1198030.0436
54 | 2719548.706 | 1197996.8806
55 | 2719221.1718 | 1198342.7981
56 | 2719219.9974 | 1198328.9484
57 | 2719327.5916 | 1198274.3662

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97663 | -0.17159 | 0.00023758 | 5.9544e-05
1 | 0.97677 | -0.1705 | 0 | 0
2 | 0.97678 | -0.17047 | 0 | 0
3 | 0.97688 | -0.16955 | 0.00033481 | 8.3912e-05
4 | 0.97803 | -0.16031 | 0.00032926 | 8.2521e-05
5 | 0.97813 | -0.1596 | 0 | 0
6 | 0.97718 | -0.1671 | 0 | 0
7 | 0.97691 | -0.16934 | 0 | 0
8 | 0.97727 | -0.16629 | 0.00049794 | 0.0001248
9 | 0.97933 | -0.15011 | 0.00032993 | 8.2688e-05
10 | 0.97883 | -0.15405 | 0 | 0
11 | 0.97944 | -0.14919 | 0 | 0
12 | 0.97828 | -0.15837 | 0 | 0
13 | 0.97961 | -0.14785 | 0 | 0
14 | 0.97764 | -0.16333 | 0.00045869 | 0.00011496
15 | 0.97986 | -0.14589 | 0.00029818 | 7.473e-05
16 | 0.97761 | -0.16359 | 0.00032924 | 8.2515e-05
17 | 0.98028 | -0.14265 | 0.00024972 | 6.2585e-05
18 | 0.98042 | -0.14152 | 0 | 0
19 | 0.98047 | -0.14114 | 0.00023376 | 5.8585e-05
20 | 0.9817 | -0.13168 | 0 | 0
21 | 0.98307 | -0.121 | 0 | 0
22 | 0.98374 | -0.11573 | 0 | 0
23 | 0.98367 | -0.11625 | 0.0013836 | 0.00034676
24 | 0.98395 | -0.11412 | 0.001003 | 0.00025137
25 | 0.97752 | -0.16433 | 0 | 0
26 | 0.97731 | -0.16597 | 0 | 0
27 | 0.98161 | -0.12941 | 0.003088 | 0.00077392
28 | 0.98124 | -0.13207 | 0 | 0
29 | 0.98197 | -0.12688 | 0 | 0
30 | 0.98101 | -0.13369 | 0.0098547 | 0.0024698
31 | 0.98114 | -0.13278 | 0.0037395 | 0.0009372
32 | 0.98172 | -0.12862 | 0.0023751 | 0.00059525
33 | 0.98956 | -0.073087 | 0 | 0
34 | 0.98093 | -0.13431 | 0 | 0
35 | 0.9914 | -0.060191 | 0.0014528 | 0.0003641
36 | 0.98932 | -0.074814 | 0.0019364 | 0.0004853
37 | 0.98051 | -0.13732 | 0 | 0
38 | 0.98918 | -0.07577 | 0.0014579 | 0.00036539
39 | 0.98932 | -0.074827 | 0.001914 | 0.0004797
40 | 0.98918 | -0.075806 | 0.0018526 | 0.00046431
41 | 0.99177 | -0.057588 | 0 | 0
42 | 0.9926 | -0.051726 | 0 | 0
43 | 0.99477 | -0.03648 | 0.0016952 | 0.00042485
44 | 0.99689 | -0.021643 | 0.015978 | 0.0040044
45 | 1 | 0 | -0.079916 | -0.019902
46 | 0.98447 | -0.11027 | 0 | 0
47 | 0.99998 | -0.00015679 | 0.0010892 | 0.00027297
48 | 0.99968 | -0.0022583 | 0.0014079 | 0.00035285
49 | 0.98302 | -0.1206 | 0 | 0
50 | 0.99966 | -0.0023993 | 0.0016351 | 0.00040979
51 | 0.97871 | -0.15023 | 0 | 0
52 | 0.9785 | -0.15177 | 0.0029897 | 0.0007493
53 | 0.98299 | -0.1208 | 0.0013434 | 0.00033669
54 | 0.98211 | -0.12705 | 0.0099868 | 0.0025029
55 | 0.97976 | -0.14264 | 0.0034403 | 0.00086223
56 | 0.97964 | -0.14351 | 0.0051509 | 0.0012909
57 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00023758 | -5.9544e-05 | 0.00023761 | 5.4474e-05 | 3.3039e-08 | -5.0694e-06 | 0.00036198 | 0.00036023 | 0.00036198 | 0.97663 | -0.17159 | 0.97677 | -0.1705 | 0.13407
1 | -0.00023761 | -5.4474e-05 | 0.00023762 | 5.4338e-05 | 8.8202e-10 | -1.3602e-07 | 0.00036023 | 0.00036019 | 0.00036023 | 0.97677 | -0.1705 | 0.97678 | -0.17047 | 0.13342
2 | -0.00023762 | -5.4338e-05 | 0.00023764 | 5.0529e-05 | 2.4608e-08 | -3.8088e-06 | 0.00036019 | 0.00035897 | 0.00036019 | 0.97678 | -0.17047 | 0.97688 | -0.16955 | 0.1334
3 | -0.00057245 | -0.00013444 | 0.00057247 | 0.00013406 | 1.4583e-08 | -3.8204e-07 | 0.00086883 | 0.0008687 | 0.00086883 | 0.97688 | -0.16955 | 0.97691 | -0.16934 | 0.32179
4 | -0.00032926 | -8.2521e-05 | 0.00032929 | 8.0037e-05 | 3.1084e-08 | -2.4837e-06 | 0.00050095 | 0.00050007 | 0.00050095 | 0.97803 | -0.16031 | 0.97813 | -0.1596 | 0.18554
5 | -0.00032929 | -8.0037e-05 | 0.00032934 | 7.5956e-05 | 5.0831e-08 | -4.0813e-06 | 0.00050007 | 0.00049868 | 0.00050007 | 0.97813 | -0.1596 | 0.97828 | -0.15837 | 0.18521
6 | 0.00057262 | 0.00013005 | -0.00057247 | -0.00013406 | 1.5269e-07 | -4.0084e-06 | 0.00086735 | 0.0008687 | 0.0008687 | 0.97718 | -0.1671 | 0.97691 | -0.16934 | 0.32174
7 | -0.00057262 | -0.00013005 | 0.00057268 | 0.00012863 | 5.3917e-08 | -1.419e-06 | 0.00086735 | 0.00086689 | 0.00086735 | 0.97718 | -0.1671 | 0.97727 | -0.16629 | 0.32124
8 | -0.0010706 | -0.00025343 | 0.0010707 | 0.00025312 | 4.2505e-08 | -3.0692e-07 | 0.0016249 | 0.0016248 | 0.0016249 | 0.97727 | -0.16629 | 0.97731 | -0.16597 | 0.60183
9 | 0.0021917 | 0.0005183 | -0.0021907 | -0.00051985 | 1.0771e-06 | -1.5555e-06 | 0.0033194 | 0.00332 | 0.00332 | 0.97933 | -0.15011 | 0.97883 | -0.15405 | 1.2296
10 | -0.0025217 | -0.00060099 | 0.002522 | 0.00060069 | 2.9297e-07 | -2.9208e-07 | 0.0038206 | 0.0038205 | 0.0038206 | 0.97933 | -0.15011 | 0.97944 | -0.14919 | 1.4151
11 | 0.0021907 | 0.00051985 | -0.0021895 | -0.00052157 | 1.1878e-06 | -1.7121e-06 | 0.00332 | 0.0033208 | 0.0033208 | 0.97883 | -0.15405 | 0.97828 | -0.15837 | 1.2299
12 | -0.002522 | -0.00060069 | 0.0025224 | 0.00060027 | 4.2471e-07 | -4.2365e-07 | 0.0038205 | 0.0038203 | 0.0038205 | 0.97944 | -0.14919 | 0.97961 | -0.14785 | 1.415
13 | 0.0018601 | 0.00044561 | -0.001859 | -0.00044814 | 1.1807e-06 | -2.5258e-06 | 0.0028221 | 0.0028232 | 0.0028232 | 0.97828 | -0.15837 | 0.97764 | -0.16333 | 1.0456
14 | -0.0025224 | -0.00060027 | 0.002523 | 0.00059965 | 6.2089e-07 | -6.1981e-07 | 0.0038203 | 0.00382 | 0.0038203 | 0.97961 | -0.14785 | 0.97986 | -0.14589 | 1.4149
15 | 0.0014003 | 0.00033318 | -0.0014002 | -0.00033336 | 4.5931e-08 | -1.8671e-07 | 0.002125 | 0.0021251 | 0.0021251 | 0.97764 | -0.16333 | 0.97761 | -0.16359 | 0.78708
16 | -0.0028212 | -0.00067438 | 0.0028223 | 0.00067355 | 1.1557e-06 | -8.3404e-07 | 0.0042728 | 0.0042724 | 0.0042728 | 0.97986 | -0.14589 | 0.98028 | -0.14265 | 1.5825
17 | 0.001071 | 0.00025085 | -0.0010709 | -0.00025155 | 9.7497e-08 | -7.051e-07 | 0.001624 | 0.0016243 | 0.0016243 | 0.97761 | -0.16359 | 0.97752 | -0.16433 | 0.60158
18 | -0.0030721 | -0.00073613 | 0.0030725 | 0.00073589 | 4.4268e-07 | -2.4319e-07 | 0.0046514 | 0.0046513 | 0.0046514 | 0.98028 | -0.14265 | 0.98042 | -0.14152 | 1.7227
19 | -0.0030725 | -0.00073589 | 0.0030727 | 0.00073581 | 1.4955e-07 | -8.2188e-08 | 0.0046513 | 0.0046512 | 0.0046513 | 0.98042 | -0.14152 | 0.98047 | -0.14114 | 1.7227
20 | -0.0033064 | -0.00079439 | 0.0033104 | 0.0007927 | 3.9875e-06 | -1.6871e-06 | 0.0050059 | 0.0050048 | 0.0050059 | 0.98047 | -0.14114 | 0.9817 | -0.13168 | 1.8541
21 | -0.0033104 | -0.0007927 | 0.0033149 | 0.0007908 | 4.4863e-06 | -1.9095e-06 | 0.0050048 | 0.0050036 | 0.0050048 | 0.9817 | -0.13168 | 0.98307 | -0.121 | 1.8536
22 | -0.0033149 | -0.0007908 | 0.0033171 | 0.00078985 | 2.2016e-06 | -9.4143e-07 | 0.0050036 | 0.005003 | 0.0050036 | 0.98307 | -0.121 | 0.98374 | -0.11573 | 1.8532
23 | 0.0013837 | 0.00034633 | -0.0013836 | -0.00034676 | 9.9795e-08 | -4.2515e-07 | 0.0020928 | 0.002093 | 0.002093 | 0.98374 | -0.11573 | 0.98367 | -0.11625 | 0.77517
24 | -0.0047008 | -0.0011362 | 0.0047017 | 0.0011362 | 9.7684e-07 | -1.9136e-08 | 0.0070957 | 0.0070956 | 0.0070957 | 0.98374 | -0.11573 | 0.98395 | -0.11412 | 2.628
25 | -0.0057047 | -0.0013875 | 0.0057076 | 0.0013879 | 2.8709e-06 | 3.1589e-07 | 0.0086123 | 0.008612 | 0.0086123 | 0.98395 | -0.11412 | 0.98447 | -0.11027 | 3.1897
26 | 0.0010709 | 0.00025155 | -0.0010707 | -0.00025312 | 2.1696e-07 | -1.5677e-06 | 0.0016243 | 0.0016248 | 0.0016248 | 0.97752 | -0.16433 | 0.97731 | -0.16597 | 0.60179
27 | 0.013602 | 0.0034093 | -0.013597 | -0.0034076 | 4.9963e-06 | 1.6837e-06 | 0.020619 | 0.020619 | 0.020619 | 0.98161 | -0.12941 | 0.98124 | -0.13207 | 7.6367
28 | -0.01669 | -0.0041832 | 0.016696 | 0.0041853 | 5.8468e-06 | 2.0637e-06 | 0.0253 | 0.0253 | 0.0253 | 0.98161 | -0.12941 | 0.98197 | -0.12688 | 9.3704
29 | 0.0098569 | 0.0024705 | -0.0098547 | -0.0024698 | 2.2133e-06 | 6.5079e-07 | 0.014948 | 0.014948 | 0.014948 | 0.98124 | -0.13207 | 0.98101 | -0.13369 | 5.5362
30 | 0.0037398 | 0.00093711 | -0.0037395 | -0.0009372 | 3.6919e-07 | -9.0338e-08 | 0.0056713 | 0.0056714 | 0.0056714 | 0.98124 | -0.13207 | 0.98114 | -0.13278 | 2.1005
31 | 0.013986 | 0.0035015 | -0.013983 | -0.0035004 | 3.3519e-06 | 1.1379e-06 | 0.021193 | 0.021193 | 0.021193 | 0.98197 | -0.12688 | 0.98172 | -0.12862 | 7.8491
32 | -0.030682 | -0.0076867 | 0.030912 | 0.007773 | 0.00023004 | 8.6301e-05 | 0.046492 | 0.046492 | 0.046492 | 0.98197 | -0.12688 | 0.98956 | -0.073087 | 17.2194
33 | 0.011608 | 0.0029051 | -0.011599 | -0.0029022 | 9.1214e-06 | 2.9115e-06 | 0.017593 | 0.017593 | 0.017593 | 0.98172 | -0.12862 | 0.98093 | -0.13431 | 6.5159
34 | -0.038075 | -0.0095679 | 0.038143 | 0.0095938 | 6.8461e-05 | 2.5901e-05 | 0.057263 | 0.057263 | 0.057263 | 0.98956 | -0.073087 | 0.9914 | -0.060191 | 21.2084
35 | 0.0071631 | 0.0017948 | -0.0071614 | -0.0017945 | 1.7119e-06 | 3.5471e-07 | 0.010771 | 0.010771 | 0.010771 | 0.98956 | -0.073087 | 0.98932 | -0.074814 | 3.9893
36 | 0.011599 | 0.0029022 | -0.011594 | -0.0029007 | 4.8108e-06 | 1.536e-06 | 0.017593 | 0.017593 | 0.017593 | 0.98093 | -0.13431 | 0.98051 | -0.13732 | 6.5159
37 | -0.039596 | -0.0099579 | 0.039611 | 0.0099633 | 1.4368e-05 | 5.4423e-06 | 0.059443 | 0.059443 | 0.059443 | 0.9914 | -0.060191 | 0.99177 | -0.057588 | 22.016
38 | 0.005225 | 0.0013092 | -0.005225 | -0.0013092 | 9.4161e-09 | 4.8414e-10 | 0.0078587 | 0.0078587 | 0.0078587 | 0.98932 | -0.074814 | 0.98932 | -0.074827 | 2.9106
39 | 0.0085982 | 0.0021549 | -0.0085918 | -0.0021532 | 6.3334e-06 | 1.6846e-06 | 0.013049 | 0.013049 | 0.013049 | 0.98051 | -0.13732 | 0.97976 | -0.14264 | 4.8329
40 | 0.0029957 | 0.00074578 | -0.0029904 | -0.00074892 | 5.3095e-06 | -3.1428e-06 | 0.0045445 | 0.0045463 | 0.0045463 | 0.98051 | -0.13732 | 0.97871 | -0.15023 | 1.6838
41 | -0.0033106 | -0.00082968 | 0.003311 | 0.00082949 | 4.3201e-07 | -1.9225e-07 | 0.00498 | 0.0049799 | 0.00498 | 0.98918 | -0.07577 | 0.98932 | -0.074827 | 1.8445
42 | 0.0018526 | 0.00046429 | -0.0018526 | -0.00046431 | 9.1966e-09 | -2.0822e-08 | 0.0027869 | 0.0027869 | 0.0027869 | 0.98918 | -0.07577 | 0.98918 | -0.075806 | 1.0322
43 | -0.039611 | -0.0099633 | 0.039643 | 0.0099756 | 3.241e-05 | 1.2275e-05 | 0.059443 | 0.059443 | 0.059443 | 0.99177 | -0.057588 | 0.9926 | -0.051726 | 22.016
44 | 0.0172 | 0.0042834 | -0.017063 | -0.0042351 | 0.00013668 | 4.8344e-05 | 0.025775 | 0.025776 | 0.025776 | 0.9926 | -0.051726 | 0.98447 | -0.11027 | 9.5467
45 | -0.056843 | -0.014259 | 0.056963 | 0.014305 | 0.00012045 | 4.5982e-05 | 0.085218 | 0.085217 | 0.085218 | 0.9926 | -0.051726 | 0.99477 | -0.03648 | 31.5621
46 | -0.058658 | -0.01473 | 0.058779 | 0.014776 | 0.00012121 | 4.6292e-05 | 0.087753 | 0.087753 | 0.087753 | 0.99477 | -0.03648 | 0.99689 | -0.021643 | 32.5012
47 | -0.074757 | -0.018781 | 0.074983 | 0.018867 | 0.00022575 | 8.6446e-05 | 0.1116 | 0.1116 | 0.1116 | 0.99689 | -0.021643 | 1 | 0 | 41.3341
48 | 0.0010892 | 0.00027279 | -0.0010892 | -0.00027297 | 2.3625e-08 | -1.8001e-07 | 0.0016206 | 0.0016207 | 0.0016207 | 1 | 0 | 0.99998 | -0.00015679 | 0.60026
49 | 0.0030439 | 0.00076193 | -0.003043 | -0.00076253 | 9.5016e-07 | -6.0804e-07 | 0.0045291 | 0.0045294 | 0.0045294 | 1 | 0 | 0.99968 | -0.0022583 | 1.6776
50 | 0.011355 | 0.0028472 | -0.011339 | -0.0028421 | 1.6226e-05 | 5.1201e-06 | 0.017164 | 0.017165 | 0.017165 | 0.98447 | -0.11027 | 0.98302 | -0.1206 | 6.3572
51 | 0.0016351 | 0.00040969 | -0.0016351 | -0.00040979 | 3.1912e-08 | -1.0092e-07 | 0.0024338 | 0.0024338 | 0.0024338 | 0.99968 | -0.0022583 | 0.99966 | -0.0023993 | 0.90142
52 | 0.0099958 | 0.0025056 | -0.0099868 | -0.0025029 | 8.9288e-06 | 2.6426e-06 | 0.015131 | 0.015131 | 0.015131 | 0.98302 | -0.1206 | 0.98211 | -0.12705 | 5.6042
53 | 0.0013434 | 0.00033652 | -0.0013434 | -0.00033669 | 3.7177e-08 | -1.6834e-07 | 0.0020335 | 0.0020336 | 0.0020336 | 0.98302 | -0.1206 | 0.98299 | -0.1208 | 0.75319
54 | 0.0029904 | 0.00074892 | -0.0029897 | -0.0007493 | 6.3697e-07 | -3.7549e-07 | 0.0045463 | 0.0045465 | 0.0045465 | 0.97871 | -0.15023 | 0.9785 | -0.15177 | 1.6839
55 | 0.0051515 | 0.001291 | -0.0051509 | -0.0012909 | 6.2125e-07 | 3.4137e-08 | 0.0078238 | 0.0078239 | 0.0078239 | 0.97976 | -0.14264 | 0.97964 | -0.14351 | 2.8977

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.079916 | 0.019902

## res_load
| p_mw | q_mvar
0 | 0.00023758 | 5.9544e-05
1 | 0.00033481 | 8.3912e-05
2 | 0.00032926 | 8.2521e-05
3 | 0.00049794 | 0.0001248
4 | 0.00032993 | 8.2688e-05
5 | 0.00045869 | 0.00011496
6 | 0.00029818 | 7.473e-05
7 | 0.00032924 | 8.2515e-05
8 | 0.00024972 | 6.2585e-05
9 | 0.00023376 | 5.8585e-05
10 | 0.0013836 | 0.00034676
11 | 0.001003 | 0.00025137
12 | 0.003088 | 0.00077392
13 | 0.0098547 | 0.0024698
14 | 0.0037395 | 0.0009372
15 | 0.0023751 | 0.00059525
16 | 0.0014528 | 0.0003641
17 | 0.0019364 | 0.0004853
18 | 0.0014579 | 0.00036539
19 | 0.001914 | 0.0004797
20 | 0.0018526 | 0.00046431
21 | 0.0016952 | 0.00042485
22 | 0.015978 | 0.0040044
23 | 0.0010892 | 0.00027297
24 | 0.0014079 | 0.00035285
25 | 0.0016351 | 0.00040979
26 | 0.0029897 | 0.0007493
27 | 0.0013434 | 0.00033669
28 | 0.0099868 | 0.0025029
29 | 0.0034403 | 0.00086223
30 | 0.0051509 | 0.0012909

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1