## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-99_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-99_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-99_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-99_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-99_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-99_0_2_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_1631-99_0_2_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1631-99_0_2_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_1631-99_0_2_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_1631-99_0_2_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_1631-99_0_2_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1631-99_0_2_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1631-99_0_2_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1631-99_0_2_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1631-99_0_2_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_1631-99_0_2_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1631-99_0_2_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1631-99_0_2_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1631-99_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1631-99_0_2_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1631-99_0_2_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1631-99_0_2_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1631-99_0_2_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1631-99_0_2_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-99_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1631-99_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_MV_13_0_node_121 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-99_0_2_load_0 | 0 | 0.0048945 | 0.0012267 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-99_0_2_load_1 | 1 | 0.0069205 | 0.0017344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-99_0_2_load_4 | 4 | 0.0057152 | 0.0014324 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-99_0_2_load_26 | 5 | 0.0047368 | 0.0011872 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-99_0_2_load_27 | 8 | 0.034619 | 0.0086765 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-99_0_2_load_23 | 10 | 0.0097785 | 0.0024507 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-99_0_2_load_13 | 12 | 0.0026802 | 0.00067172 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-99_0_2_load_17 | 13 | 0.0019811 | 0.00049652 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-99_0_2_load_5 | 14 | 0.0026528 | 0.00066486 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-99_0_2_load_6 | 15 | 0.0018925 | 0.0004743 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-99_0_2_load_8 | 17 | 0.0019069 | 0.0004779 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-99_0_2_load_14 | 20 | 0.0020275 | 0.00050814 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-99_0_2_load_10 | 21 | 0.0024484 | 0.00061362 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-99_0_2_load_12 | 22 | 0.0015509 | 0.00038869 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-99_0_2_load_20 | 23 | 0.017289 | 0.0043331 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-99_0_2_load_19 | 24 | 0.02675 | 0.0067042 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-99_0_2_load_24 | 25 | 0.012545 | 0.0031442 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-99_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-99_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.016612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-99_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.008341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-99_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-99_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.042423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-99_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.023435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-99_0_2_line_6 | NAYY 4x150 SE | 5 | 8 | 0.022832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-99_0_2_line_7 | NAYY 4x150 SE | 6 | 12 | 0.017006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-99_0_2_line_8 | NAYY 4x150 SE | 6 | 13 | 0.014632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-99_0_2_line_9 | NAYY 4x150 SE | 7 | 8 | 0.0096263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-99_0_2_line_10 | NAYY 4x150 SE | 7 | 9 | 0.091383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-99_0_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.012674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-99_0_2_line_12 | NAYY 4x150 SE | 9 | 11 | 0.033381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-99_0_2_line_13 | NAYY 4x150 SE | 10 | 25 | 0.016703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-99_0_2_line_14 | NAYY 4x150 SE | 11 | 23 | 0.023784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-99_0_2_line_15 | NAYY 4x150 SE | 12 | 19 | 0.0015225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-99_0_2_line_16 | NAYY 4x150 SE | 13 | 24 | 0.0078422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-99_0_2_line_17 | NAYY 4x150 SE | 14 | 15 | 0.0067163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-99_0_2_line_18 | NAYY 4x150 SE | 14 | 16 | 0.018394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-99_0_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.0047732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-99_0_2_line_20 | NAYY 4x150 SE | 16 | 18 | 0.048748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-99_0_2_line_21 | NAYY 4x150 SE | 17 | 19 | 0.0061381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-99_0_2_line_22 | NAYY 4x150 SE | 18 | 20 | 0.01267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-99_0_2_line_23 | NAYY 4x150 SE | 19 | 21 | 0.012624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-99_0_2_line_24 | NAYY 4x150 SE | 21 | 22 | 0.002928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-99_0_2_trafo_26 | 0.25 MVA 20/0.4 kV | 26 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2718931.8203 | 1197733.7413 | 2718915.6313 | 1197747.587
1 | 2718902.3135 | 1197757.494 | 2718912.3047 | 1197750.432 | 2718915.6313 | 1197747.587
2 | 2718902.3135 | 1197757.494 | 2718897.3967 | 1197750.7468
3 | 2718902.3135 | 1197757.494 | 2718915.0282 | 1197775.0458
4 | 2718897.3967 | 1197750.7468 | 2718870.6297 | 1197770.4401 | 2718865.1626 | 1197763.0504
5 | 2718928.7767 | 1197794.0247 | 2718915.0282 | 1197775.0458
6 | 2718865.1626 | 1197763.0504 | 2718851.583 | 1197744.6952
7 | 2718928.7767 | 1197794.0247 | 2718938.7534 | 1197807.7966
8 | 2718928.7767 | 1197794.0247 | 2718916.1118 | 1197801.3521
9 | 2718845.8577 | 1197736.9566 | 2718851.583 | 1197744.6952
10 | 2718820.4702 | 1197790.7245 | 2718812.1104 | 1197779.3501 | 2718802.8284 | 1197767.6127 | 2718806.3872 | 1197764.1142 | 2718805.7082 | 1197759.564 | 2718806.9229 | 1197757.8647 | 2718809.343 | 1197756.8454 | 2718814.0461 | 1197759.0182 | 2718817.5085 | 1197759.5985 | 2718821.0396 | 1197759.413 | 2718824.9016 | 1197757.9109 | 2718829.6087 | 1197754.9022 | 2718835.113 | 1197753.177 | 2718840.6463 | 1197749.6178 | 2718845.8577 | 1197736.9566
11 | 2718820.4702 | 1197790.7245 | 2718831.9682 | 1197785.3934
12 | 2718820.4702 | 1197790.7245 | 2718827.4429 | 1197799.8253 | 2718834.8341 | 1197810.8691 | 2718838.9803 | 1197818.4348
13 | 2718847.1215 | 1197778.3674 | 2718831.9682 | 1197785.3934
14 | 2718838.9803 | 1197818.4348 | 2718860.127 | 1197807.5491
15 | 2718939.6466 | 1197809.0296 | 2718938.7534 | 1197807.7966
16 | 2718909.3238 | 1197805.2793 | 2718916.1118 | 1197801.3521
17 | 2718945.727 | 1197818.0898 | 2718949.4697 | 1197823.6666
18 | 2718959.7198 | 1197838.9397 | 2718949.4697 | 1197823.6666
19 | 2718945.727 | 1197818.0898 | 2718943.0671 | 1197814.1264
20 | 2718959.7198 | 1197838.9397 | 2718955.6614 | 1197843.4177 | 2718939.7497 | 1197849.7725 | 2718944.8473 | 1197863.8842 | 2718934.9389 | 1197867.5564
21 | 2718939.6466 | 1197809.0296 | 2718943.0671 | 1197814.1264
22 | 2718934.9389 | 1197867.5564 | 2718922.985 | 1197871.756
23 | 2718939.6466 | 1197809.0296 | 2718950.1925 | 1197802.0912
24 | 2718952.6385 | 1197800.4819 | 2718950.1925 | 1197802.0912

## bus_geodata
| x | y | coords
0 | 2718915.6313 | 1197747.587
1 | 2718931.8203 | 1197733.7413
2 | 2718902.3135 | 1197757.494
3 | 2718897.3967 | 1197750.7468
4 | 2718915.0282 | 1197775.0458
5 | 2718865.1626 | 1197763.0504
6 | 2718928.7767 | 1197794.0247
7 | 2718845.8577 | 1197736.9566
8 | 2718851.583 | 1197744.6952
9 | 2718820.4702 | 1197790.7245
10 | 2718831.9682 | 1197785.3934
11 | 2718838.9803 | 1197818.4348
12 | 2718938.7534 | 1197807.7966
13 | 2718916.1118 | 1197801.3521
14 | 2718949.4697 | 1197823.6666
15 | 2718945.727 | 1197818.0898
16 | 2718959.7198 | 1197838.9397
17 | 2718943.0671 | 1197814.1264
18 | 2718934.9389 | 1197867.5564
19 | 2718939.6466 | 1197809.0296
20 | 2718922.985 | 1197871.756
21 | 2718950.1925 | 1197802.0912
22 | 2718952.6385 | 1197800.4819
23 | 2718860.127 | 1197807.5491
24 | 2718909.3238 | 1197805.2793
25 | 2718847.1215 | 1197778.3674
26 | 2718865.1626 | 1197763.0504

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99524 | -0.033249 | 0.0048945 | 0.0012267
1 | 0.99503 | -0.034735 | 0.0069205 | 0.0017344
2 | 0.99552 | -0.031271 | 0 | 0
3 | 0.99626 | -0.026114 | 0 | 0
4 | 0.99398 | -0.042118 | 0.0057152 | 0.0014324
5 | 1 | 0 | -0.13733 | -0.03433
6 | 0.9925 | -0.052528 | 0 | 0
7 | 0.99702 | -0.02079 | 0 | 0
8 | 0.99757 | -0.016961 | 0.034619 | 0.0086765
9 | 0.99181 | -0.057337 | 0 | 0
10 | 0.99141 | -0.060209 | 0.0097785 | 0.0024507
11 | 0.99098 | -0.063199 | 0 | 0
12 | 0.99213 | -0.055143 | 0.0026802 | 0.00067172
13 | 0.9919 | -0.05679 | 0.0019811 | 0.00049652
14 | 0.99194 | -0.056502 | 0.0026528 | 0.00066486
15 | 0.99198 | -0.056183 | 0.0018925 | 0.0004743
16 | 0.99188 | -0.056882 | 0 | 0
17 | 0.99203 | -0.055864 | 0.0019069 | 0.0004779
18 | 0.99174 | -0.057886 | 0 | 0
19 | 0.9921 | -0.055336 | 0 | 0
20 | 0.9917 | -0.058147 | 0.0020275 | 0.00050814
21 | 0.99203 | -0.055848 | 0.0024484 | 0.00061362
22 | 0.99202 | -0.055894 | 0.0015509 | 0.00038869
23 | 0.99039 | -0.06738 | 0.017289 | 0.0043331
24 | 0.99159 | -0.058919 | 0.02675 | 0.0067042
25 | 0.99111 | -0.062337 | 0.012545 | 0.0031442
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0069219 | 0.0017347 | -0.0069205 | -0.0017344 | 1.4237e-06 | 2.7082e-07 | 0.010349 | 0.010349 | 0.010349 | 0.99524 | -0.033249 | 0.99503 | -0.034735 | 3.833
1 | -0.011816 | -0.0029614 | 0.01182 | 0.0029624 | 3.2355e-06 | 1.0285e-06 | 0.017667 | 0.017667 | 0.017667 | 0.99524 | -0.033249 | 0.99552 | -0.031271 | 6.5433
2 | -0.061596 | -0.015458 | 0.06164 | 0.015475 | 4.4125e-05 | 1.6863e-05 | 0.092075 | 0.092075 | 0.092075 | 0.99552 | -0.031271 | 0.99626 | -0.026114 | 34.1019
3 | 0.049776 | 0.012495 | -0.049701 | -0.012467 | 7.4877e-05 | 2.8518e-05 | 0.074408 | 0.074408 | 0.074408 | 0.99552 | -0.031271 | 0.99398 | -0.042118 | 27.5586
4 | -0.06164 | -0.015475 | 0.061864 | 0.01556 | 0.00022442 | 8.5763e-05 | 0.092075 | 0.092075 | 0.092075 | 0.99626 | -0.026114 | 1 | 0 | 34.1019
5 | 0.043986 | 0.011035 | -0.043923 | -0.01101 | 6.3417e-05 | 2.4088e-05 | 0.065852 | 0.065853 | 0.065853 | 0.99398 | -0.042118 | 0.9925 | -0.052528 | 24.3898
6 | 0.074668 | 0.018769 | -0.074492 | -0.018702 | 0.00017595 | 6.7373e-05 | 0.11113 | 0.11113 | 0.11113 | 1 | 0 | 0.99757 | -0.016961 | 41.1583
7 | 0.015167 | 0.0038005 | -0.015161 | -0.0037986 | 5.4868e-06 | 1.8906e-06 | 0.022739 | 0.022739 | 0.022739 | 0.9925 | -0.052528 | 0.99213 | -0.055143 | 8.4218
8 | 0.028756 | 0.00721 | -0.028739 | -0.0072036 | 1.6971e-05 | 6.3384e-06 | 0.043114 | 0.043114 | 0.043114 | 0.9925 | -0.052528 | 0.9919 | -0.05679 | 15.9681
9 | -0.039852 | -0.010017 | 0.039873 | 0.010025 | 2.1257e-05 | 8.0501e-06 | 0.059488 | 0.059488 | 0.059488 | 0.99702 | -0.02079 | 0.99757 | -0.016961 | 22.0325
10 | 0.039852 | 0.010017 | -0.03965 | -0.009941 | 0.00020179 | 7.6427e-05 | 0.059488 | 0.059488 | 0.059488 | 0.99702 | -0.02079 | 0.99181 | -0.057337 | 22.0326
11 | 0.022336 | 0.0055994 | -0.022328 | -0.0055961 | 8.8815e-06 | 3.2525e-06 | 0.033512 | 0.033512 | 0.033512 | 0.99181 | -0.057337 | 0.99141 | -0.060209 | 12.4118
12 | 0.017313 | 0.0043416 | -0.017299 | -0.0043367 | 1.4055e-05 | 4.9755e-06 | 0.025976 | 0.025976 | 0.025976 | 0.99181 | -0.057337 | 0.99098 | -0.063199 | 9.6209
13 | 0.012549 | 0.0031454 | -0.012545 | -0.0031442 | 3.6976e-06 | 1.2068e-06 | 0.018835 | 0.018835 | 0.018835 | 0.99141 | -0.060209 | 0.99111 | -0.062337 | 6.976
14 | 0.017299 | 0.0043367 | -0.017289 | -0.0043331 | 1.0014e-05 | 3.5455e-06 | 0.025976 | 0.025976 | 0.025976 | 0.99098 | -0.063199 | 0.99039 | -0.06738 | 9.6209
15 | 0.012481 | 0.0031269 | -0.012481 | -0.0031268 | 3.329e-07 | 1.0838e-07 | 0.018719 | 0.018719 | 0.018719 | 0.99213 | -0.055143 | 0.9921 | -0.055336 | 6.933
16 | 0.026758 | 0.0067071 | -0.02675 | -0.0067042 | 7.8853e-06 | 2.9316e-06 | 0.040142 | 0.040142 | 0.040142 | 0.9919 | -0.05679 | 0.99159 | -0.058919 | 14.8673
17 | -0.0046808 | -0.0011721 | 0.004681 | 0.0011721 | 2.0661e-07 | -7.2354e-09 | 0.0070214 | 0.0070213 | 0.0070214 | 0.99194 | -0.056502 | 0.99198 | -0.056183 | 2.6005
18 | 0.002028 | 0.00050729 | -0.0020279 | -0.00050748 | 1.062e-07 | -1.9658e-07 | 0.0030418 | 0.0030419 | 0.0030419 | 0.99194 | -0.056502 | 0.99188 | -0.056882 | 1.1266
19 | -0.0065735 | -0.0016464 | 0.0065738 | 0.0016465 | 2.8957e-07 | 4.9751e-08 | 0.0098601 | 0.0098601 | 0.0098601 | 0.99198 | -0.056183 | 0.99203 | -0.055864 | 3.6519
20 | 0.0020279 | 0.00050748 | -0.0020276 | -0.000508 | 2.815e-07 | -5.2085e-07 | 0.0030419 | 0.0030421 | 0.0030421 | 0.99188 | -0.056882 | 0.99174 | -0.057886 | 1.1267
21 | -0.0084806 | -0.0021244 | 0.0084812 | 0.0021246 | 6.1975e-07 | 1.5911e-07 | 0.01272 | 0.01272 | 0.01272 | 0.99203 | -0.055864 | 0.9921 | -0.055336 | 4.7112
22 | 0.0020276 | 0.000508 | -0.0020275 | -0.00050814 | 7.317e-08 | -1.3534e-07 | 0.0030421 | 0.0030422 | 0.0030422 | 0.99174 | -0.057886 | 0.9917 | -0.058147 | 1.1267
23 | 0.0039996 | 0.0010022 | -0.0039993 | -0.0010023 | 2.8346e-07 | -5.3972e-08 | 0.0059987 | 0.0059988 | 0.0059988 | 0.9921 | -0.055336 | 0.99203 | -0.055848 | 2.2218
24 | 0.0015509 | 0.00038865 | -0.0015509 | -0.00038869 | 9.8874e-09 | -3.4e-08 | 0.0023263 | 0.0023263 | 0.0023263 | 0.99203 | -0.055848 | 0.99202 | -0.055894 | 0.86159

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14207 | 0.035517

## res_load
| p_mw | q_mvar
0 | 0.0048945 | 0.0012267
1 | 0.0069205 | 0.0017344
2 | 0.0057152 | 0.0014324
3 | 0.0047368 | 0.0011872
4 | 0.034619 | 0.0086765
5 | 0.0097785 | 0.0024507
6 | 0.0026802 | 0.00067172
7 | 0.0019811 | 0.00049652
8 | 0.0026528 | 0.00066486
9 | 0.0018925 | 0.0004743
10 | 0.0019069 | 0.0004779
11 | 0.0020275 | 0.00050814
12 | 0.0024484 | 0.00061362
13 | 0.0015509 | 0.00038869
14 | 0.017289 | 0.0043331
15 | 0.02675 | 0.0067042
16 | 0.012545 | 0.0031442

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1