## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2299-18_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2299-18_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2299-18_0_3_node_114 | 0.4 | n |  | TRUE
3 | bus_LV_2299-18_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2299-18_0_3_node_62 | 0.4 | n |  | TRUE
5 | bus_LV_2299-18_0_3_node_61 | 0.4 | n |  | TRUE
6 | bus_LV_2299-18_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2299-18_0_3_node_70 | 0.4 | n |  | TRUE
8 | bus_LV_2299-18_0_3_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_2299-18_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2299-18_0_3_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_2299-18_0_3_node_69 | 0.4 | n |  | TRUE
12 | bus_LV_2299-18_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2299-18_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2299-18_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2299-18_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2299-18_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2299-18_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2299-18_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2299-18_0_3_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_2299-18_0_3_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_2299-18_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2299-18_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2299-18_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2299-18_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_2299-18_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_2299-18_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2299-18_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2299-18_0_3_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2299-18_0_3_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2299-18_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2299-18_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2299-18_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_2299-18_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2299-18_0_3_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_2299-18_0_3_node_54 | 0.4 | n |  | TRUE
36 | bus_LV_2299-18_0_3_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_2299-18_0_3_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_2299-18_0_3_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_2299-18_0_3_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_2299-18_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_2299-18_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_2299-18_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_2299-18_0_3_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2299-18_0_3_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_2299-18_0_3_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_2299-18_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_2299-18_0_3_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_2299-18_0_3_node_115 | 0.4 | n |  | TRUE
49 | bus_LV_2299-18_0_3_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_2299-18_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2299-18_0_3_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_2299-18_0_3_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_2299-18_0_3_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_2299-18_0_3_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_2299-18_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_2299-18_0_3_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_2299-18_0_3_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_2299-18_0_3_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_2299-18_0_3_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_2299-18_0_3_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_2299-18_0_3_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_2299-18_0_3_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2299-18_0_3_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_2299-18_0_3_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_2299-18_0_3_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_2299-18_0_3_node_100 | 0.4 | n |  | TRUE
67 | bus_LV_2299-18_0_3_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_2299-18_0_3_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2299-18_0_3_node_103 | 0.4 | n |  | TRUE
70 | bus_LV_2299-18_0_3_node_89 | 0.4 | n |  | TRUE
71 | bus_LV_2299-18_0_3_node_102 | 0.4 | n |  | TRUE
72 | bus_LV_2299-18_0_3_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2299-18_0_3_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_2299-18_0_3_node_112 | 0.4 | n |  | TRUE
75 | bus_LV_2299-18_0_3_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_2299-18_0_3_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_2299-18_0_3_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_2299-18_0_3_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_2299-18_0_3_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_2299-18_0_3_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_2299-18_0_3_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_2299-18_0_3_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_2299-18_0_3_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_2299-18_0_3_node_99 | 0.4 | n |  | TRUE
85 | bus_LV_2299-18_0_3_node_98 | 0.4 | n |  | TRUE
86 | bus_LV_2299-18_0_3_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_2299-18_0_3_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_2299-18_0_3_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_2299-18_0_3_node_80 | 0.4 | n |  | TRUE
90 | bus_LV_2299-18_0_3_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_2299-18_0_3_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_2299-18_0_3_node_96 | 0.4 | n |  | TRUE
93 | bus_LV_2299-18_0_3_node_86 | 0.4 | n |  | TRUE
94 | bus_LV_2299-18_0_3_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_2299-18_0_3_node_108 | 0.4 | n |  | TRUE
96 | bus_LV_2299-18_0_3_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_2299-18_0_3_node_104 | 0.4 | n |  | TRUE
98 | bus_LV_2299-18_0_3_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_2299-18_0_3_node_109 | 0.4 | n |  | TRUE
100 | bus_LV_2299-18_0_3_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_2299-18_0_3_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_2299-18_0_3_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_2299-18_0_3_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_2299-18_0_3_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_2299-18_0_3_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_2299-18_0_3_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_2299-18_0_3_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_2299-18_0_3_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_2299-18_0_3_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_2299-18_0_3_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_2299-18_0_3_node_101 | 0.4 | n |  | TRUE
112 | bus_LV_2299-18_0_3_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_2299-18_0_3_node_110 | 0.4 | n |  | TRUE
114 | bus_LV_2299-18_0_3_node_113 | 0.4 | n |  | TRUE
115 | bus_MV_36_0_node_198 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2299-18_0_3_load_0 | 0 | 0.00039417 | 9.8788e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2299-18_0_3_load_114 | 2 | 0.00037139 | 9.308e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2299-18_0_3_load_62 | 4 | 0.00091353 | 0.00022895 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2299-18_0_3_load_61 | 5 | 0.000567 | 0.0001421 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2299-18_0_3_load_5 | 6 | 0.00039323 | 9.8553e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2299-18_0_3_load_70 | 7 | 0.00010246 | 2.568e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2299-18_0_3_load_3 | 8 | 0.00027953 | 7.0056e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2299-18_0_3_load_59 | 10 | 0.00017096 | 4.2848e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2299-18_0_3_load_69 | 11 | 0.00018849 | 4.7241e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2299-18_0_3_load_6 | 12 | 0.0073026 | 0.0018302 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2299-18_0_3_load_9 | 15 | 0.0018522 | 0.00046421 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2299-18_0_3_load_10 | 16 | 0.0052052 | 0.0013045 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2299-18_0_3_load_12 | 18 | 0.00753 | 0.0018872 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2299-18_0_3_load_25 | 19 | 0.0038595 | 0.00096728 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2299-18_0_3_load_15 | 21 | 0.0011948 | 0.00029945 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2299-18_0_3_load_13 | 22 | 0.0058676 | 0.0014706 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2299-18_0_3_load_26 | 24 | 0.0014328 | 0.00035909 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2299-18_0_3_load_28 | 25 | 0.0010304 | 0.00025824 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2299-18_0_3_load_19 | 27 | 0.0010736 | 0.00026906 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2299-18_0_3_load_20 | 30 | 0.0028979 | 0.00072629 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2299-18_0_3_load_21 | 31 | 0.0022439 | 0.00056237 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2299-18_0_3_load_24 | 32 | 0.00077269 | 0.00019365 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2299-18_0_3_load_52 | 34 | 0.0041191 | 0.0010324 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2299-18_0_3_load_54 | 35 | 0.0023388 | 0.00058616 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2299-18_0_3_load_22 | 36 | 0.001856 | 0.00046515 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2299-18_0_3_load_32 | 40 | 0.0031012 | 0.00077724 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2299-18_0_3_load_29 | 41 | 0.011377 | 0.0028513 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2299-18_0_3_load_43 | 43 | 0.0013042 | 0.00032688 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2299-18_0_3_load_34 | 46 | 0.0010694 | 0.00026803 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2299-18_0_3_load_115 | 48 | 0.0033336 | 0.00083548 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2299-18_0_3_load_35 | 49 | 0.00015885 | 3.9812e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2299-18_0_3_load_44 | 50 | 0.00017401 | 4.3612e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2299-18_0_3_load_36 | 52 | 0.00017827 | 4.4679e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2299-18_0_3_load_37 | 53 | 0.00035544 | 8.9081e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2299-18_0_3_load_41 | 55 | 0.00098219 | 0.00024616 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2299-18_0_3_load_68 | 57 | 0.00034008 | 8.5232e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2299-18_0_3_load_51 | 60 | 0.0035675 | 0.0008941 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2299-18_0_3_load_45 | 62 | 0.0054919 | 0.0013764 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2299-18_0_3_load_46 | 63 | 0.0020804 | 0.00052141 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2299-18_0_3_load_47 | 64 | 0.0016164 | 0.00040511 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2299-18_0_3_load_53 | 65 | 0.0089942 | 0.0022542 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2299-18_0_3_load_100 | 66 | 0.0038205 | 0.0009575 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2299-18_0_3_load_56 | 67 | 0.0012782 | 0.00032034 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2299-18_0_3_load_57 | 68 | 0.0006118 | 0.00015333 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2299-18_0_3_load_89 | 70 | 0.001441 | 0.00036114 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2299-18_0_3_load_102 | 71 | 0.0011819 | 0.00029621 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2299-18_0_3_load_58 | 72 | 0.00089851 | 0.00022519 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2299-18_0_3_load_112 | 74 | 0.0005565 | 0.00013947 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2299-18_0_3_load_63 | 75 | 0.00050695 | 0.00012705 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2299-18_0_3_load_67 | 77 | 0.0010997 | 0.00027561 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2299-18_0_3_load_71 | 79 | 0.00053815 | 0.00013487 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2299-18_0_3_load_73 | 80 | 0.00013633 | 3.4168e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2299-18_0_3_load_74 | 81 | 0.00017515 | 4.3898e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2299-18_0_3_load_76 | 83 | 0.00053767 | 0.00013475 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2299-18_0_3_load_77 | 86 | 0.00049936 | 0.00012515 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2299-18_0_3_load_78 | 87 | 0.00015959 | 3.9997e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2299-18_0_3_load_80 | 89 | 0.00052465 | 0.00013149 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2299-18_0_3_load_82 | 91 | 0.00087231 | 0.00021862 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2299-18_0_3_load_96 | 92 | 0.00049958 | 0.00012521 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2299-18_0_3_load_86 | 93 | 0.0011098 | 0.00027814 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2299-18_0_3_load_83 | 94 | 0.0038303 | 0.00095996 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2299-18_0_3_load_108 | 95 | 0.00041421 | 0.00010381 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2299-18_0_3_load_97 | 96 | 0.00052658 | 0.00013197 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2299-18_0_3_load_104 | 97 | 0.0011289 | 0.00028294 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2299-18_0_3_load_84 | 98 | 0.0019894 | 0.0004986 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2299-18_0_3_load_109 | 99 | 0.00036528 | 9.1548e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2299-18_0_3_load_90 | 101 | 0.0016233 | 0.00040683 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2299-18_0_3_load_87 | 102 | 0.0016786 | 0.00042069 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2299-18_0_3_load_88 | 103 | 0.0068865 | 0.0017259 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2299-18_0_3_load_91 | 104 | 0.0018953 | 0.00047501 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2299-18_0_3_load_92 | 105 | 0.0023752 | 0.00059528 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2299-18_0_3_load_93 | 106 | 0.0023874 | 0.00059835 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2299-18_0_3_load_94 | 107 | 0.0035769 | 0.00089646 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2299-18_0_3_load_95 | 108 | 0.0025383 | 0.00063616 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2299-18_0_3_load_107 | 109 | 0.0011795 | 0.00029562 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2299-18_0_3_load_106 | 110 | 0.0021997 | 0.00055131 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2299-18_0_3_load_101 | 111 | 0.0027175 | 0.00068106 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2299-18_0_3_load_105 | 112 | 0.0022885 | 0.00057356 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2299-18_0_3_load_110 | 113 | 0.0001741 | 4.3634e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2299-18_0_3_load_113 | 114 | 0.00082313 | 0.0002063 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2299-18_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.056104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2299-18_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.26836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2299-18_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.007905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2299-18_0_3_line_3 | NAYY 4x150 SE | 2 | 7 | 0.22067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2299-18_0_3_line_4 | NAYY 4x150 SE | 2 | 6 | 0.081842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2299-18_0_3_line_5 | NAYY 4x150 SE | 3 | 8 | 0.031656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2299-18_0_3_line_6 | NAYY 4x150 SE | 4 | 5 | 0.021648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2299-18_0_3_line_7 | NAYY 4x150 SE | 5 | 10 | 0.0075924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2299-18_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.14115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2299-18_0_3_line_9 | NAYY 4x150 SE | 7 | 11 | 0.0019943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2299-18_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.025192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2299-18_0_3_line_11 | NAYY 4x150 SE | 10 | 72 | 0.014409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2299-18_0_3_line_12 | NAYY 4x150 SE | 11 | 79 | 0.011048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2299-18_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.035449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2299-18_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.037038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2299-18_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0053988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2299-18_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.033098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2299-18_0_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.004917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2299-18_0_3_line_18 | NAYY 4x150 SE | 14 | 18 | 0.0066379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2299-18_0_3_line_19 | NAYY 4x150 SE | 15 | 19 | 0.011367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2299-18_0_3_line_20 | NAYY 4x150 SE | 16 | 20 | 0.017472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2299-18_0_3_line_21 | NAYY 4x150 SE | 17 | 21 | 0.0053312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2299-18_0_3_line_22 | NAYY 4x150 SE | 17 | 22 | 0.010482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2299-18_0_3_line_23 | NAYY 4x150 SE | 18 | 23 | 0.032634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2299-18_0_3_line_24 | NAYY 4x150 SE | 19 | 24 | 0.011268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2299-18_0_3_line_25 | NAYY 4x150 SE | 20 | 25 | 0.027725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2299-18_0_3_line_26 | NAYY 4x150 SE | 21 | 26 | 0.016018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2299-18_0_3_line_27 | NAYY 4x150 SE | 23 | 27 | 0.01435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2299-18_0_3_line_28 | NAYY 4x150 SE | 23 | 28 | 0.031973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2299-18_0_3_line_29 | NAYY 4x150 SE | 24 | 39 | 0.042807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2299-18_0_3_line_30 | NAYY 4x150 SE | 25 | 42 | 0.016863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2299-18_0_3_line_31 | NAYY 4x150 SE | 26 | 30 | 0.008061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2299-18_0_3_line_32 | NAYY 4x150 SE | 27 | 32 | 0.014538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2299-18_0_3_line_33 | NAYY 4x150 SE | 28 | 29 | 0.024807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2299-18_0_3_line_34 | NAYY 4x150 SE | 29 | 31 | 0.022124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2299-18_0_3_line_35 | NAYY 4x150 SE | 31 | 36 | 0.0040763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2299-18_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.041847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2299-18_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.0037787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2299-18_0_3_line_38 | NAYY 4x150 SE | 34 | 37 | 0.050285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2299-18_0_3_line_39 | NAYY 4x150 SE | 35 | 38 | 0.02514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2299-18_0_3_line_40 | NAYY 4x150 SE | 37 | 65 | 0.03616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_2299-18_0_3_line_41 | NAYY 4x150 SE | 37 | 63 | 0.013773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2299-18_0_3_line_42 | NAYY 4x150 SE | 38 | 67 | 0.039008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2299-18_0_3_line_43 | NAYY 4x150 SE | 38 | 68 | 0.027623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2299-18_0_3_line_44 | NAYY 4x150 SE | 39 | 40 | 0.01032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2299-18_0_3_line_45 | NAYY 4x150 SE | 39 | 41 | 0.086857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2299-18_0_3_line_46 | NAYY 4x150 SE | 40 | 47 | 0.040626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2299-18_0_3_line_47 | NAYY 4x150 SE | 41 | 44 | 0.0095271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2299-18_0_3_line_48 | NAYY 4x150 SE | 42 | 43 | 0.0036014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_2299-18_0_3_line_49 | NAYY 4x150 SE | 43 | 59 | 0.014398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_2299-18_0_3_line_50 | NAYY 4x150 SE | 44 | 45 | 0.01137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2299-18_0_3_line_51 | NAYY 4x150 SE | 44 | 46 | 0.0078067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2299-18_0_3_line_52 | NAYY 4x150 SE | 45 | 48 | 0.031472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2299-18_0_3_line_53 | NAYY 4x150 SE | 46 | 49 | 0.032395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2299-18_0_3_line_54 | NAYY 4x150 SE | 47 | 50 | 0.00995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2299-18_0_3_line_55 | NAYY 4x150 SE | 47 | 51 | 0.056318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2299-18_0_3_line_56 | NAYY 4x150 SE | 51 | 52 | 0.013612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2299-18_0_3_line_57 | NAYY 4x150 SE | 52 | 53 | 0.013919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2299-18_0_3_line_58 | NAYY 4x150 SE | 53 | 54 | 0.059441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2299-18_0_3_line_59 | NAYY 4x150 SE | 54 | 55 | 0.089433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2299-18_0_3_line_60 | NAYY 4x150 SE | 55 | 56 | 0.046548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2299-18_0_3_line_61 | NAYY 4x150 SE | 56 | 57 | 0.01934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2299-18_0_3_line_62 | NAYY 4x150 SE | 56 | 58 | 0.020438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2299-18_0_3_line_63 | NAYY 4x150 SE | 58 | 76 | 0.004667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2299-18_0_3_line_64 | NAYY 4x150 SE | 58 | 75 | 0.057857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2299-18_0_3_line_65 | NAYY 4x150 SE | 59 | 60 | 0.059996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2299-18_0_3_line_66 | NAYY 4x150 SE | 59 | 61 | 0.029553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_2299-18_0_3_line_67 | NAYY 4x150 SE | 60 | 66 | 0.035176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2299-18_0_3_line_68 | NAYY 4x150 SE | 61 | 65 | 0.026145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_2299-18_0_3_line_69 | NAYY 4x150 SE | 61 | 64 | 0.0077569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2299-18_0_3_line_70 | NAYY 4x150 SE | 62 | 63 | 0.058174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2299-18_0_3_line_71 | NAYY 4x150 SE | 67 | 69 | 0.0035997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2299-18_0_3_line_72 | NAYY 4x150 SE | 69 | 70 | 0.013968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2299-18_0_3_line_73 | NAYY 4x150 SE | 69 | 71 | 0.019117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2299-18_0_3_line_74 | NAYY 4x150 SE | 70 | 100 | 0.016973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2299-18_0_3_line_75 | NAYY 4x150 SE | 71 | 111 | 0.02846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2299-18_0_3_line_76 | NAYY 4x150 SE | 72 | 73 | 0.013453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2299-18_0_3_line_77 | NAYY 4x150 SE | 73 | 74 | 0.18888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2299-18_0_3_line_78 | NAYY 4x150 SE | 76 | 77 | 0.06256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2299-18_0_3_line_79 | NAYY 4x150 SE | 77 | 78 | 0.14097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2299-18_0_3_line_80 | NAYY 4x150 SE | 78 | 80 | 0.043536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2299-18_0_3_line_81 | NAYY 4x150 SE | 78 | 79 | 0.026619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2299-18_0_3_line_82 | NAYY 4x150 SE | 81 | 82 | 0.024126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2299-18_0_3_line_83 | NAYY 4x150 SE | 82 | 83 | 0.0082113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2299-18_0_3_line_84 | NAYY 4x150 SE | 83 | 84 | 0.024159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2299-18_0_3_line_85 | NAYY 4x150 SE | 84 | 85 | 0.031682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2299-18_0_3_line_86 | NAYY 4x150 SE | 85 | 96 | 0.0022655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2299-18_0_3_line_87 | NAYY 4x150 SE | 85 | 107 | 0.016935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2299-18_0_3_line_88 | NAYY 4x150 SE | 86 | 87 | 0.010381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2299-18_0_3_line_89 | NAYY 4x150 SE | 86 | 88 | 0.016232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2299-18_0_3_line_90 | NAYY 4x150 SE | 87 | 89 | 0.0103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2299-18_0_3_line_91 | NAYY 4x150 SE | 88 | 90 | 0.030893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2299-18_0_3_line_92 | NAYY 4x150 SE | 88 | 91 | 0.01009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2299-18_0_3_line_93 | NAYY 4x150 SE | 89 | 92 | 0.0061901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2299-18_0_3_line_94 | NAYY 4x150 SE | 90 | 93 | 0.018212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2299-18_0_3_line_95 | NAYY 4x150 SE | 90 | 94 | 0.00013535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2299-18_0_3_line_96 | NAYY 4x150 SE | 91 | 95 | 0.025609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2299-18_0_3_line_97 | NAYY 4x150 SE | 92 | 96 | 0.01814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2299-18_0_3_line_98 | NAYY 4x150 SE | 93 | 97 | 0.022859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2299-18_0_3_line_99 | NAYY 4x150 SE | 94 | 98 | 0.021909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2299-18_0_3_line_100 | NAYY 4x150 SE | 95 | 99 | 0.081741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2299-18_0_3_line_101 | NAYY 4x150 SE | 98 | 100 | 0.021742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2299-18_0_3_line_102 | NAYY 4x150 SE | 99 | 113 | 0.014425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2299-18_0_3_line_103 | NAYY 4x150 SE | 100 | 101 | 0.049428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2299-18_0_3_line_104 | NAYY 4x150 SE | 100 | 102 | 0.019068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2299-18_0_3_line_105 | NAYY 4x150 SE | 102 | 103 | 0.019011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2299-18_0_3_line_106 | NAYY 4x150 SE | 104 | 105 | 0.00025698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2299-18_0_3_line_107 | NAYY 4x150 SE | 104 | 106 | 0.017188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2299-18_0_3_line_108 | NAYY 4x150 SE | 105 | 107 | 0.030734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2299-18_0_3_line_109 | NAYY 4x150 SE | 106 | 108 | 0.021099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2299-18_0_3_line_110 | NAYY 4x150 SE | 108 | 109 | 0.012476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2299-18_0_3_line_111 | NAYY 4x150 SE | 109 | 110 | 0.0090315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2299-18_0_3_line_112 | NAYY 4x150 SE | 110 | 112 | 0.019094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2299-18_0_3_line_113 | NAYY 4x150 SE | 113 | 114 | 0.10748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2299-18_0_3_trafo_27 | 0.25 MVA 20/0.4 kV | 115 | 20 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2588989.4498 | 1177567.5092 | 2588997.9577 | 1177573.3409 | 2589008.6473 | 1177589.6628 | 2589016.0404 | 1177595.9857 | 2589022.8164 | 1177603.3325 | 2589028.8917 | 1177605.7962
1 | 2589028.8917 | 1177605.7962 | 2589287.7233 | 1177676.6762
2 | 2588987.5996 | 1177575.1943 | 2588989.4498 | 1177567.5092
3 | 2589130.0829 | 1177831.0966 | 2589287.7233 | 1177676.6762
4 | 2589342.0868 | 1177615.4979 | 2589287.7233 | 1177676.6762
5 | 2588987.5996 | 1177575.1943 | 2588980.284 | 1177577.7202 | 2588971.8021 | 1177573.5338 | 2588964.2972 | 1177572.8696 | 2588960.6532 | 1177566.9828
6 | 2588832.481 | 1177630.7301 | 2588837.59 | 1177637.9277 | 2588843.9396 | 1177649.067
7 | 2588832.481 | 1177630.7301 | 2588828.0863 | 1177624.5389
8 | 2588832.481 | 1177630.7301 | 2588945.8407 | 1177546.6349
9 | 2589129.6086 | 1177833.0337 | 2589130.0829 | 1177831.0966
10 | 2588945.8407 | 1177546.6349 | 2588948.3676 | 1177549.4761 | 2588959.9669 | 1177565.874 | 2588960.6532 | 1177566.9828
11 | 2588818.1631 | 1177614.2071 | 2588825.1862 | 1177620.4532 | 2588828.0863 | 1177624.5389
12 | 2589129.6086 | 1177833.0337 | 2589128.8657 | 1177836.0675 | 2589123.1034 | 1177841.5076
13 | 2588793.7511 | 1178055.0781 | 2588781.3619 | 1178061.1601 | 2588768.5429 | 1178066.2424 | 2588761.2512 | 1178069.1694
14 | 2588725.5881 | 1178078.6855 | 2588735.7013 | 1178077.1545 | 2588753.0442 | 1178072.4637 | 2588761.2512 | 1178069.1694
15 | 2588793.7511 | 1178055.0781 | 2588798.2841 | 1178052.1458
16 | 2588793.7511 | 1178055.0781 | 2588795.5052 | 1178061.4336 | 2588796.5262 | 1178068.0573 | 2588798.9575 | 1178072.9663 | 2588803.3164 | 1178079.039 | 2588806.8607 | 1178082.6008 | 2588805.7938 | 1178084.0814
17 | 2588725.5881 | 1178078.6855 | 2588725.9641 | 1178083.5873
18 | 2588725.5881 | 1178078.6855 | 2588719.0279 | 1178079.6987
19 | 2588798.2841 | 1178052.1458 | 2588802.4203 | 1178049.4701 | 2588803.9615 | 1178048.2666 | 2588807.4939 | 1178045.503
20 | 2588817.7438 | 1178096.3652 | 2588814.6087 | 1178095.0259 | 2588811.2397 | 1178091.2415 | 2588805.7938 | 1178084.0814
21 | 2588725.9641 | 1178083.5873 | 2588726.4607 | 1178088.8953
22 | 2588725.9641 | 1178083.5873 | 2588715.5186 | 1178084.4588
23 | 2588686.4824 | 1178082.0725 | 2588718.3011 | 1178079.811 | 2588719.0279 | 1178079.6987
24 | 2588813.9922 | 1178036.2978 | 2588807.4939 | 1178045.503 | 2588807.4939 | 1178045.503
25 | 2588817.7438 | 1178096.3652 | 2588825.3196 | 1178102.5541 | 2588835.1165 | 1178111.6293 | 2588838.5675 | 1178114.6528
26 | 2588728.0062 | 1178104.8387 | 2588726.8375 | 1178092.9237 | 2588726.4607 | 1178088.8953
27 | 2588686.4824 | 1178082.0725 | 2588672.1328 | 1178082.2286
28 | 2588686.4824 | 1178082.0725 | 2588689.7038 | 1178108.691 | 2588690.8114 | 1178108.5778 | 2588694.8372 | 1178108.1699
29 | 2588818.0731 | 1177995.0907 | 2588820.2695 | 1178005.0806 | 2588820.5747 | 1178017.0417 | 2588818.7057 | 1178026.7724 | 2588816.303 | 1178033.0245 | 2588813.9922 | 1178036.2978
30 | 2588850.9442 | 1178126.0403 | 2588848.014 | 1178123.9669 | 2588840.9406 | 1178116.732 | 2588838.5675 | 1178114.6528
31 | 2588728.0062 | 1178104.8387 | 2588736.0502 | 1178104.0342
32 | 2588672.1328 | 1178082.2286 | 2588657.5953 | 1178082.3867
33 | 2588692.1552 | 1178128.1741 | 2588691.5846 | 1178125.4405 | 2588689.7038 | 1178108.691 | 2588690.8114 | 1178108.5778 | 2588694.8372 | 1178108.1699
34 | 2588692.1552 | 1178128.1741 | 2588683.7143 | 1178129.1573 | 2588670.1323 | 1178130.2458
35 | 2588666.0691 | 1178130.5715 | 2588670.1323 | 1178130.2458
36 | 2588715.8452 | 1178166.7711 | 2588717.8475 | 1178162.9764 | 2588724.3508 | 1178159.6402 | 2588738.9704 | 1178153.3315 | 2588753.223 | 1178151.8923
37 | 2588715.8452 | 1178166.7711 | 2588717.2007 | 1178170.2983
38 | 2588782.5571 | 1178176.3944 | 2588775.7677 | 1178149.6157 | 2588753.223 | 1178151.8923
39 | 2588726.2186 | 1178193.7652 | 2588717.2007 | 1178170.2983
40 | 2588782.5571 | 1178176.3944 | 2588792.9666 | 1178174.0736 | 2588817.4991 | 1178167.134
41 | 2588782.5571 | 1178176.3944 | 2588774.6395 | 1178179.3552 | 2588772.2273 | 1178184.097
42 | 2588726.2186 | 1178193.7652 | 2588744.3868 | 1178228.2837
43 | 2588726.2186 | 1178193.7652 | 2588701.1199 | 1178205.3003
44 | 2588818.0731 | 1177995.0907 | 2588821.6673 | 1177985.4173
45 | 2588818.0731 | 1177995.0907 | 2588799.3774 | 1177983.4533 | 2588777.0585 | 1177971.0779 | 2588754.0589 | 1177946.2753 | 2588749.0353 | 1177944.0618
46 | 2588826.0504 | 1177946.4621 | 2588827.5866 | 1177950.7725 | 2588829.1727 | 1177957.195 | 2588828.8035 | 1177964.0214 | 2588827.7204 | 1177969.1261 | 2588821.6673 | 1177985.4173
47 | 2588740.317 | 1177940.2204 | 2588749.0353 | 1177944.0618
48 | 2588850.9442 | 1178126.0403 | 2588853.241 | 1178128.8142
49 | 2588862.4233 | 1178139.9036 | 2588853.241 | 1178128.8142
50 | 2588740.317 | 1177940.2204 | 2588729.8863 | 1177935.6267
51 | 2588740.317 | 1177940.2204 | 2588744.4151 | 1177933.5759
52 | 2588714.2899 | 1177962.9813 | 2588729.8863 | 1177935.6267
53 | 2588737.2443 | 1177903.2852 | 2588745.3707 | 1177921.6903 | 2588746.3673 | 1177927.4691 | 2588744.4151 | 1177933.5759
54 | 2588822.7167 | 1177937.0858 | 2588826.0504 | 1177946.4621
55 | 2588850.8721 | 1177904.0162 | 2588847.0345 | 1177907.0916 | 2588839.0775 | 1177913.632 | 2588837.6739 | 1177918.9818 | 2588839.4833 | 1177930.4065 | 2588840.3842 | 1177934.1067 | 2588840.2375 | 1177937.3753 | 2588837.4916 | 1177939.904 | 2588831.9872 | 1177942.36 | 2588826.0504 | 1177946.4621
56 | 2588850.8721 | 1177904.0162 | 2588846.8971 | 1177894.8967 | 2588845.209 | 1177891.6444
57 | 2588845.209 | 1177891.6444 | 2588838.797 | 1177879.2907
58 | 2588804.0801 | 1177831.0779 | 2588837.5645 | 1177876.9162 | 2588838.797 | 1177879.2907
59 | 2588804.0801 | 1177831.0779 | 2588825.1973 | 1177829.8821 | 2588848.6498 | 1177835.3075 | 2588874.103 | 1177844.2089 | 2588885.5747 | 1177845.6771 | 2588891.0408 | 1177844.1317
60 | 2588931.6021 | 1177857.3529 | 2588920.5138 | 1177856.5509 | 2588904.4863 | 1177841.8288 | 2588894.4411 | 1177843.1704 | 2588891.0408 | 1177844.1317
61 | 2588931.6021 | 1177857.3529 | 2588931.7355 | 1177876.6928
62 | 2588931.6021 | 1177857.3529 | 2588931.6176 | 1177836.9202
63 | 2588936.1812 | 1177837.9567 | 2588931.6176 | 1177836.9202
64 | 2588931.6176 | 1177836.9202 | 2588928.8917 | 1177809.1778 | 2588923.9281 | 1177786.1309 | 2588920.9572 | 1177780.4554
65 | 2588862.4233 | 1178139.9036 | 2588876.3638 | 1178170.8156 | 2588883.6836 | 1178195.8535
66 | 2588862.4233 | 1178139.9036 | 2588842.6945 | 1178155.6931 | 2588842.6568 | 1178160.0176
67 | 2588883.6836 | 1178195.8535 | 2588885.1761 | 1178200.9589 | 2588887.7609 | 1178230.7035
68 | 2588842.6568 | 1178160.0176 | 2588817.4991 | 1178167.134
69 | 2588842.6568 | 1178160.0176 | 2588845.6321 | 1178167.1811
70 | 2588814.4016 | 1178198.1409 | 2588788.1392 | 1178203.1531 | 2588779.8092 | 1178202.146 | 2588774.4031 | 1178199.8884 | 2588771.7911 | 1178196.3359 | 2588770.408 | 1178192.2365 | 2588771.0846 | 1178186.3433 | 2588772.2273 | 1178184.097
71 | 2588746.0634 | 1178231.4691 | 2588744.3868 | 1178228.2837
72 | 2588746.0634 | 1178231.4691 | 2588753.6254 | 1178243.2132
73 | 2588746.0634 | 1178231.4691 | 2588727.9924 | 1178237.705
74 | 2588762.8144 | 1178257.484 | 2588753.6254 | 1178243.2132
75 | 2588701.0887 | 1178246.9888 | 2588727.9924 | 1178237.705
76 | 2588808.1102 | 1177605.2664 | 2588818.1631 | 1177614.2071
77 | 2588808.1102 | 1177605.2664 | 2588651.6063 | 1177711.0053
78 | 2588936.1812 | 1177837.9567 | 2588942.8008 | 1177843.4584 | 2588948.0018 | 1177850.4078 | 2588951.7972 | 1177857.471 | 2588966.4414 | 1177891.7265
79 | 2588966.4414 | 1177891.7265 | 2589103.7477 | 1177859.7811
80 | 2589103.7477 | 1177859.7811 | 2589111.7734 | 1177869.6714 | 2589118.335 | 1177877.0187 | 2589122.3956 | 1177878.79 | 2589127.4387 | 1177878.9031 | 2589137.6333 | 1177873.6393
81 | 2589103.7477 | 1177859.7811 | 2589123.1034 | 1177841.5076
82 | 2588898.4774 | 1178348.0647 | 2588918.8163 | 1178361.041
83 | 2588898.4774 | 1178348.0647 | 2588897.4583 | 1178339.9168
84 | 2588894.4599 | 1178315.9447 | 2588897.4583 | 1178339.9168
85 | 2588894.4599 | 1178315.9447 | 2588862.7091 | 1178317.1601
86 | 2588862.7091 | 1178317.1601 | 2588860.455 | 1178317.387
87 | 2588862.7091 | 1178317.1601 | 2588859.9089 | 1178300.4586
88 | 2588815.6392 | 1178321.5182 | 2588825.998 | 1178320.8382
89 | 2588799.4425 | 1178322.5816 | 2588815.6392 | 1178321.5182
90 | 2588836.2476 | 1178319.823 | 2588826.4628 | 1178320.8077 | 2588825.998 | 1178320.8382
91 | 2588784.2717 | 1178295.6519 | 2588799.4425 | 1178322.5816
92 | 2588799.4425 | 1178322.5816 | 2588795.4748 | 1178329.3925 | 2588795.4564 | 1178331.6005
93 | 2588842.4066 | 1178319.2032 | 2588836.2476 | 1178319.823
94 | 2588784.2717 | 1178295.6519 | 2588768.8275 | 1178305.3034
95 | 2588784.2053 | 1178295.534 | 2588784.2717 | 1178295.6519
96 | 2588803.6851 | 1178355.2876 | 2588795.4 | 1178338.3861 | 2588795.4564 | 1178331.6005
97 | 2588842.4066 | 1178319.2032 | 2588860.455 | 1178317.387
98 | 2588749.4424 | 1178317.4176 | 2588768.8275 | 1178305.3034
99 | 2588784.2053 | 1178295.534 | 2588773.469 | 1178276.4363
100 | 2588803.6851 | 1178355.2876 | 2588827.6201 | 1178404.1147 | 2588837.709 | 1178429.5496
101 | 2588762.8144 | 1178257.484 | 2588773.469 | 1178276.4363
102 | 2588844.2973 | 1178442.3376 | 2588839.6491 | 1178434.4409 | 2588837.709 | 1178429.5496
103 | 2588762.8144 | 1178257.484 | 2588721.1104 | 1178284.0143
104 | 2588762.8144 | 1178257.484 | 2588778.9214 | 1178247.2777
105 | 2588794.9801 | 1178237.1019 | 2588778.9214 | 1178247.2777
106 | 2588854.7843 | 1178269.8941 | 2588854.8268 | 1178270.1475
107 | 2588854.7843 | 1178269.8941 | 2588851.9422 | 1178252.9427
108 | 2588859.9089 | 1178300.4586 | 2588854.8268 | 1178270.1475
109 | 2588851.9422 | 1178252.9427 | 2588848.4534 | 1178232.1342
110 | 2588846.3905 | 1178219.8299 | 2588846.3905 | 1178219.8299 | 2588848.4534 | 1178232.1342
111 | 2588846.3905 | 1178219.8299 | 2588837.5187 | 1178221.521
112 | 2588818.762 | 1178225.0961 | 2588837.5187 | 1178221.521
113 | 2588844.2973 | 1178442.3376 | 2588746.9608 | 1178487.9093

## bus_geodata
| x | y | coords
0 | 2589028.8917 | 1177605.7962
1 | 2588989.4498 | 1177567.5092
2 | 2589287.7233 | 1177676.6762
3 | 2588987.5996 | 1177575.1943
4 | 2588843.9396 | 1177649.067
5 | 2588832.481 | 1177630.7301
6 | 2589342.0868 | 1177615.4979
7 | 2589130.0829 | 1177831.0966
8 | 2588960.6532 | 1177566.9828
9 | 2588945.8407 | 1177546.6349
10 | 2588828.0863 | 1177624.5389
11 | 2589129.6086 | 1177833.0337
12 | 2588761.2512 | 1178069.1694
13 | 2588793.7511 | 1178055.0781
14 | 2588725.5881 | 1178078.6855
15 | 2588798.2841 | 1178052.1458
16 | 2588805.7938 | 1178084.0814
17 | 2588725.9641 | 1178083.5873
18 | 2588719.0279 | 1178079.6987
19 | 2588807.4939 | 1178045.503
20 | 2588817.7438 | 1178096.3652
21 | 2588726.4607 | 1178088.8953
22 | 2588715.5186 | 1178084.4588
23 | 2588686.4824 | 1178082.0725
24 | 2588813.9922 | 1178036.2978
25 | 2588838.5675 | 1178114.6528
26 | 2588728.0062 | 1178104.8387
27 | 2588672.1328 | 1178082.2286
28 | 2588694.8372 | 1178108.1699
29 | 2588692.1552 | 1178128.1741
30 | 2588736.0502 | 1178104.0342
31 | 2588670.1323 | 1178130.2458
32 | 2588657.5953 | 1178082.3867
33 | 2588715.8452 | 1178166.7711
34 | 2588753.223 | 1178151.8923
35 | 2588717.2007 | 1178170.2983
36 | 2588666.0691 | 1178130.5715
37 | 2588782.5571 | 1178176.3944
38 | 2588726.2186 | 1178193.7652
39 | 2588818.0731 | 1177995.0907
40 | 2588821.6673 | 1177985.4173
41 | 2588749.0353 | 1177944.0618
42 | 2588850.9442 | 1178126.0403
43 | 2588853.241 | 1178128.8142
44 | 2588740.317 | 1177940.2204
45 | 2588729.8863 | 1177935.6267
46 | 2588744.4151 | 1177933.5759
47 | 2588826.0504 | 1177946.4621
48 | 2588714.2899 | 1177962.9813
49 | 2588737.2443 | 1177903.2852
50 | 2588822.7167 | 1177937.0858
51 | 2588850.8721 | 1177904.0162
52 | 2588845.209 | 1177891.6444
53 | 2588838.797 | 1177879.2907
54 | 2588804.0801 | 1177831.0779
55 | 2588891.0408 | 1177844.1317
56 | 2588931.6021 | 1177857.3529
57 | 2588931.7355 | 1177876.6928
58 | 2588931.6176 | 1177836.9202
59 | 2588862.4233 | 1178139.9036
60 | 2588883.6836 | 1178195.8535
61 | 2588842.6568 | 1178160.0176
62 | 2588814.4016 | 1178198.1409
63 | 2588772.2273 | 1178184.097
64 | 2588845.6321 | 1178167.1811
65 | 2588817.4991 | 1178167.134
66 | 2588887.7609 | 1178230.7035
67 | 2588744.3868 | 1178228.2837
68 | 2588701.1199 | 1178205.3003
69 | 2588746.0634 | 1178231.4691
70 | 2588753.6254 | 1178243.2132
71 | 2588727.9924 | 1178237.705
72 | 2588818.1631 | 1177614.2071
73 | 2588808.1102 | 1177605.2664
74 | 2588651.6063 | 1177711.0053
75 | 2588920.9572 | 1177780.4554
76 | 2588936.1812 | 1177837.9567
77 | 2588966.4414 | 1177891.7265
78 | 2589103.7477 | 1177859.7811
79 | 2589123.1034 | 1177841.5076
80 | 2589137.6333 | 1177873.6393
81 | 2588918.8163 | 1178361.041
82 | 2588898.4774 | 1178348.0647
83 | 2588897.4583 | 1178339.9168
84 | 2588894.4599 | 1178315.9447
85 | 2588862.7091 | 1178317.1601
86 | 2588815.6392 | 1178321.5183
87 | 2588825.998 | 1178320.8382
88 | 2588799.4425 | 1178322.5816
89 | 2588836.2476 | 1178319.823
90 | 2588784.2717 | 1178295.6519
91 | 2588795.4564 | 1178331.6005
92 | 2588842.4066 | 1178319.2032
93 | 2588768.8275 | 1178305.3034
94 | 2588784.2053 | 1178295.534
95 | 2588803.6851 | 1178355.2876
96 | 2588860.455 | 1178317.387
97 | 2588749.4424 | 1178317.4176
98 | 2588773.469 | 1178276.4363
99 | 2588837.709 | 1178429.5496
100 | 2588762.8144 | 1178257.484
101 | 2588721.1104 | 1178284.0143
102 | 2588778.9214 | 1178247.2777
103 | 2588794.9801 | 1178237.1019
104 | 2588854.7843 | 1178269.8941
105 | 2588854.8268 | 1178270.1475
106 | 2588851.9422 | 1178252.9427
107 | 2588859.9089 | 1178300.4586
108 | 2588848.4534 | 1178232.1342
109 | 2588846.3905 | 1178219.8299
110 | 2588837.5187 | 1178221.521
111 | 2588701.0887 | 1178246.9888
112 | 2588818.762 | 1178225.0961
113 | 2588844.2973 | 1178442.3376
114 | 2588746.9608 | 1178487.9093
115 | 2588850.9442 | 1178126.0403

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98269 | -0.12319 | 0.00039417 | 9.8788e-05
1 | 0.98242 | -0.12518 | 0 | 0
2 | 0.98416 | -0.11255 | 0.00037139 | 9.308e-05
3 | 0.98238 | -0.12546 | 0 | 0
4 | 0.98144 | -0.13219 | 0.00091353 | 0.00022895
5 | 0.98147 | -0.13199 | 0.000567 | 0.0001421
6 | 0.98412 | -0.11289 | 0.00039323 | 9.8553e-05
7 | 0.98562 | -0.10203 | 0.00010246 | 2.568e-05
8 | 0.98222 | -0.12658 | 0.00027953 | 7.0056e-05
9 | 0.98211 | -0.1274 | 0 | 0
10 | 0.98145 | -0.13212 | 0.00017096 | 4.2848e-05
11 | 0.98563 | -0.10193 | 0.00018849 | 4.7241e-05
12 | 0.9935 | -0.045546 | 0.0073026 | 0.0018302
13 | 0.99506 | -0.034537 | 0 | 0
14 | 0.99225 | -0.054342 | 0 | 0
15 | 0.99479 | -0.036471 | 0.0018522 | 0.00046421
16 | 0.99821 | -0.01249 | 0.0052052 | 0.0013045
17 | 0.99218 | -0.054839 | 0 | 0
18 | 0.99212 | -0.05525 | 0.00753 | 0.0018872
19 | 0.99424 | -0.040333 | 0.0038595 | 0.00096728
20 | 1 | 0 | -0.15805 | -0.039645
21 | 0.99215 | -0.05506 | 0.0011948 | 0.00029945
22 | 0.99209 | -0.055462 | 0.0058676 | 0.0014706
23 | 0.99184 | -0.057222 | 0 | 0
24 | 0.99376 | -0.043727 | 0.0014328 | 0.00035909
25 | 0.99831 | -0.01164 | 0.0010304 | 0.00025824
26 | 0.99208 | -0.055531 | 0 | 0
27 | 0.99181 | -0.057491 | 0.0010736 | 0.00026906
28 | 0.99166 | -0.058554 | 0 | 0
29 | 0.99151 | -0.059588 | 0 | 0
30 | 0.99205 | -0.055768 | 0.0028979 | 0.00072629
31 | 0.99138 | -0.060509 | 0.0022439 | 0.00056237
32 | 0.99179 | -0.057605 | 0.00077269 | 0.00019365
33 | 0.9843 | -0.10938 | 0 | 0
34 | 0.98747 | -0.087075 | 0.0041191 | 0.0010324
35 | 0.98401 | -0.1114 | 0.0023388 | 0.00058616
36 | 0.99137 | -0.060586 | 0.001856 | 0.00046515
37 | 0.99158 | -0.058353 | 0 | 0
38 | 0.98219 | -0.12427 | 0 | 0
39 | 0.99202 | -0.056025 | 0 | 0
40 | 0.99184 | -0.057325 | 0.0031012 | 0.00077724
41 | 0.99003 | -0.070104 | 0.011377 | 0.0028513
42 | 0.9973 | -0.018651 | 0 | 0
43 | 0.99708 | -0.02015 | 0.0013042 | 0.00032688
44 | 0.98997 | -0.070548 | 0 | 0
45 | 0.98991 | -0.070934 | 0 | 0
46 | 0.98995 | -0.070646 | 0.0010694 | 0.00026803
47 | 0.9913 | -0.061166 | 0 | 0
48 | 0.98976 | -0.072003 | 0.0033336 | 0.00083548
49 | 0.98994 | -0.070698 | 0.00015885 | 3.9812e-05
50 | 0.9913 | -0.061184 | 0.00017401 | 4.3612e-05
51 | 0.99057 | -0.066396 | 0 | 0
52 | 0.99039 | -0.06766 | 0.00017827 | 4.4679e-05
53 | 0.99022 | -0.068929 | 0.00035544 | 8.9081e-05
54 | 0.98949 | -0.074132 | 0 | 0
55 | 0.9884 | -0.081969 | 0.00098219 | 0.00024616
56 | 0.9879 | -0.085584 | 0 | 0
57 | 0.98789 | -0.085652 | 0.00034008 | 8.5232e-05
58 | 0.98769 | -0.0871 | 0 | 0
59 | 0.99623 | -0.026056 | 0 | 0
60 | 0.99559 | -0.03052 | 0.0035675 | 0.0008941
61 | 0.99463 | -0.037106 | 0 | 0
62 | 0.99097 | -0.06266 | 0.0054919 | 0.0013764
63 | 0.99143 | -0.059413 | 0.0020804 | 0.00052141
64 | 0.99462 | -0.037232 | 0.0016164 | 0.00040511
65 | 0.99325 | -0.046696 | 0.0089942 | 0.0022542
66 | 0.9954 | -0.031874 | 0.0038205 | 0.0009575
67 | 0.9794 | -0.14408 | 0.0012782 | 0.00032034
68 | 0.98217 | -0.12445 | 0.0006118 | 0.00015333
69 | 0.97915 | -0.14587 | 0 | 0
70 | 0.97826 | -0.15224 | 0.001441 | 0.00036114
71 | 0.97904 | -0.14665 | 0.0011819 | 0.00029621
72 | 0.98142 | -0.13234 | 0.00089851 | 0.00022519
73 | 0.98141 | -0.13242 | 0 | 0
74 | 0.98126 | -0.13352 | 0.0005565 | 0.00013947
75 | 0.98764 | -0.087402 | 0.00050695 | 0.00012705
76 | 0.98764 | -0.087422 | 0 | 0
77 | 0.98704 | -0.091737 | 0.0010997 | 0.00027561
78 | 0.98592 | -0.099872 | 0 | 0
79 | 0.98571 | -0.10137 | 0.00053815 | 0.00013487
80 | 0.98591 | -0.099934 | 0.00013633 | 3.4168e-05
81 | 0.97215 | -0.19604 | 0.00017515 | 4.3898e-05
82 | 0.97215 | -0.19599 | 0 | 0
83 | 0.97216 | -0.19598 | 0.00053767 | 0.00013475
84 | 0.97218 | -0.19579 | 0 | 0
85 | 0.97221 | -0.19555 | 0 | 0
86 | 0.97362 | -0.18547 | 0.00049936 | 0.00012515
87 | 0.9733 | -0.18776 | 0.00015959 | 3.9997e-05
88 | 0.97413 | -0.18182 | 0 | 0
89 | 0.97299 | -0.19001 | 0.00052465 | 0.00013149
90 | 0.97521 | -0.17401 | 0 | 0
91 | 0.97409 | -0.1821 | 0.00087231 | 0.00021862
92 | 0.9728 | -0.19132 | 0.00049958 | 0.00012521
93 | 0.97515 | -0.17444 | 0.0011098 | 0.00027814
94 | 0.97522 | -0.17397 | 0.0038303 | 0.00095996
95 | 0.97402 | -0.18259 | 0.00041421 | 0.00010381
96 | 0.97228 | -0.19509 | 0.00052658 | 0.00013197
97 | 0.97512 | -0.17471 | 0.0011289 | 0.00028294
98 | 0.97619 | -0.16705 | 0.0019894 | 0.0004986
99 | 0.97386 | -0.18377 | 0.00036528 | 9.1548e-05
100 | 0.97721 | -0.15974 | 0 | 0
101 | 0.97709 | -0.16058 | 0.0016233 | 0.00040683
102 | 0.97697 | -0.16145 | 0.0016786 | 0.00042069
103 | 0.97678 | -0.16282 | 0.0068865 | 0.0017259
104 | 0.97108 | -0.20372 | 0.0018953 | 0.00047501
105 | 0.97109 | -0.20369 | 0.0023752 | 0.00059528
106 | 0.97081 | -0.20565 | 0.0023874 | 0.00059835
107 | 0.97176 | -0.19885 | 0.0035769 | 0.00089646
108 | 0.97056 | -0.20749 | 0.0025383 | 0.00063616
109 | 0.97046 | -0.20824 | 0.0011795 | 0.00029562
110 | 0.9704 | -0.20867 | 0.0021997 | 0.00055131
111 | 0.97893 | -0.14745 | 0.0027175 | 0.00068106
112 | 0.97033 | -0.20913 | 0.0022885 | 0.00057356
113 | 0.97384 | -0.18392 | 0.0001741 | 4.3634e-05
114 | 0.97371 | -0.18486 | 0.00082313 | 0.0002063
115 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0033901 | 0.00084376 | -0.0033892 | -0.00084411 | 9.2183e-07 | -3.5604e-07 | 0.0051313 | 0.0051315 | 0.0051315 | 0.98269 | -0.12319 | 0.98242 | -0.12518 | 1.9006
1 | -0.0037843 | -0.00094255 | 0.0037898 | 0.00094125 | 5.4934e-06 | -1.2922e-06 | 0.0057281 | 0.0057269 | 0.0057281 | 0.98269 | -0.12319 | 0.98416 | -0.11255 | 2.1215
2 | 0.0033892 | 0.00084411 | -0.003389 | -0.00084417 | 1.2989e-07 | -5.0131e-08 | 0.0051315 | 0.0051316 | 0.0051316 | 0.98242 | -0.12518 | 0.98238 | -0.12546 | 1.9006
3 | -0.0045544 | -0.0011319 | 0.0045609 | 0.0011316 | 6.522e-06 | -2.9978e-07 | 0.0068827 | 0.0068817 | 0.0068827 | 0.98416 | -0.11255 | 0.98562 | -0.10203 | 2.5491
4 | 0.00039325 | 9.752e-05 | -0.00039323 | -9.8553e-05 | 1.8043e-08 | -1.033e-06 | 0.00059421 | 0.00059458 | 0.00059458 | 0.98416 | -0.11255 | 0.98412 | -0.11289 | 0.22021
5 | 0.003389 | 0.00084417 | -0.0033885 | -0.00084437 | 5.2017e-07 | -2.0066e-07 | 0.0051316 | 0.0051317 | 0.0051317 | 0.98238 | -0.12546 | 0.98222 | -0.12658 | 1.9006
6 | -0.00091353 | -0.00022895 | 0.00091355 | 0.00022869 | 2.5913e-08 | -2.6361e-07 | 0.001385 | 0.0013849 | 0.001385 | 0.98144 | -0.13219 | 0.98147 | -0.13199 | 0.51298
7 | 0.0016261 | 0.00040474 | -0.0016261 | -0.00040482 | 2.8773e-08 | -8.4882e-08 | 0.0024644 | 0.0024644 | 0.0024644 | 0.98147 | -0.13199 | 0.98145 | -0.13212 | 0.91275
8 | -0.0031067 | -0.00077553 | 0.0031086 | 0.00077449 | 1.9528e-06 | -1.0339e-06 | 0.004709 | 0.0047083 | 0.004709 | 0.98147 | -0.13199 | 0.98211 | -0.1274 | 1.7441
9 | -0.0046634 | -0.0011572 | 0.0046634 | 0.0011572 | 6.1613e-08 | -1.7199e-09 | 0.0070364 | 0.0070363 | 0.0070364 | 0.98562 | -0.10203 | 0.98563 | -0.10193 | 2.6061
10 | 0.003109 | 0.00077431 | -0.0031086 | -0.00077449 | 3.4848e-07 | -1.8479e-07 | 0.0047082 | 0.0047083 | 0.0047083 | 0.98222 | -0.12658 | 0.98211 | -0.1274 | 1.7438
11 | 0.0014551 | 0.00036197 | -0.0014551 | -0.00036214 | 4.3726e-08 | -1.6527e-07 | 0.0022052 | 0.0022053 | 0.0022053 | 0.98145 | -0.13212 | 0.98142 | -0.13234 | 0.81677
12 | -0.0048519 | -0.0012045 | 0.0048523 | 0.0012045 | 3.6948e-07 | 1.2914e-09 | 0.0073209 | 0.0073209 | 0.0073209 | 0.98563 | -0.10193 | 0.98571 | -0.10137 | 2.7115
13 | -0.030775 | -0.0077146 | 0.030821 | 0.0077322 | 4.6995e-05 | 1.7615e-05 | 0.046093 | 0.046093 | 0.046093 | 0.9935 | -0.045546 | 0.99506 | -0.034537 | 17.0716
14 | 0.023472 | 0.0058843 | -0.023443 | -0.0058738 | 2.8564e-05 | 1.0507e-05 | 0.035156 | 0.035156 | 0.035156 | 0.9935 | -0.045546 | 0.99225 | -0.054342 | 13.0207
15 | 0.035518 | 0.0089003 | -0.035508 | -0.0088967 | 9.5034e-06 | 3.585e-06 | 0.053113 | 0.053113 | 0.053113 | 0.99506 | -0.034537 | 0.99479 | -0.036471 | 19.6714
16 | -0.066339 | -0.016633 | 0.066543 | 0.01671 | 0.00020326 | 7.7747e-05 | 0.099206 | 0.099206 | 0.099206 | 0.99506 | -0.034537 | 0.99821 | -0.01249 | 36.7429
17 | 0.0099619 | 0.0024963 | -0.0099612 | -0.0024961 | 6.8476e-07 | 1.9986e-07 | 0.014939 | 0.014939 | 0.014939 | 0.99225 | -0.054342 | 0.99218 | -0.054839 | 5.533
18 | 0.013481 | 0.0033775 | -0.01348 | -0.0033769 | 1.6929e-06 | 5.654e-07 | 0.020217 | 0.020217 | 0.020217 | 0.99225 | -0.054342 | 0.99212 | -0.05525 | 7.4877
19 | 0.033656 | 0.0084325 | -0.033638 | -0.0084258 | 1.7976e-05 | 6.7662e-06 | 0.050342 | 0.050342 | 0.050342 | 0.99479 | -0.036471 | 0.99424 | -0.040333 | 18.6453
20 | -0.071748 | -0.018015 | 0.071873 | 0.018063 | 0.00012474 | 4.7748e-05 | 0.10696 | 0.10696 | 0.10696 | 0.99821 | -0.01249 | 1 | 0 | 39.6166
21 | 0.0040931 | 0.0010255 | -0.004093 | -0.0010255 | 1.2536e-07 | -2.0637e-08 | 0.0061385 | 0.0061386 | 0.0061386 | 0.99218 | -0.054839 | 0.99215 | -0.05506 | 2.2735
22 | 0.0058681 | 0.0014706 | -0.0058676 | -0.0014706 | 5.0658e-07 | 5.9479e-08 | 0.0088006 | 0.0088007 | 0.0088007 | 0.99218 | -0.054839 | 0.99209 | -0.055462 | 3.2595
23 | 0.0059497 | 0.0014898 | -0.0059481 | -0.0014895 | 1.6214e-06 | 2.0232e-07 | 0.008923 | 0.0089232 | 0.0089232 | 0.99212 | -0.05525 | 0.99184 | -0.057222 | 3.3049
24 | 0.029779 | 0.0074585 | -0.029765 | -0.0074533 | 1.3965e-05 | 5.225e-06 | 0.044566 | 0.044566 | 0.044566 | 0.99424 | -0.040333 | 0.99376 | -0.043727 | 16.506
25 | 0.085376 | 0.021582 | -0.085236 | -0.021529 | 0.00013975 | 5.3024e-05 | 0.12711 | 0.12711 | 0.12711 | 1 | 0 | 0.99831 | -0.01164 | 23.5381
26 | 0.0028982 | 0.00072609 | -0.002898 | -0.00072622 | 1.8884e-07 | -1.3421e-07 | 0.0043466 | 0.0043467 | 0.0043467 | 0.99215 | -0.05506 | 0.99208 | -0.055531 | 1.6099
27 | 0.0018463 | 0.00046237 | -0.0018463 | -0.00046253 | 6.8702e-08 | -1.5878e-07 | 0.0027698 | 0.0027699 | 0.0027699 | 0.99184 | -0.057222 | 0.99181 | -0.057491 | 1.0259
28 | 0.0041017 | 0.0010272 | -0.004101 | -0.0010273 | 7.5543e-07 | -1.2202e-07 | 0.0061533 | 0.0061535 | 0.0061535 | 0.99184 | -0.057222 | 0.99166 | -0.058554 | 2.2791
29 | 0.028332 | 0.0070942 | -0.028284 | -0.0070762 | 4.8068e-05 | 1.7934e-05 | 0.042421 | 0.042421 | 0.042421 | 0.99376 | -0.043727 | 0.99202 | -0.056025 | 15.7114
30 | 0.084205 | 0.021271 | -0.084122 | -0.02124 | 8.2958e-05 | 3.1466e-05 | 0.12557 | 0.12557 | 0.12557 | 0.99831 | -0.01164 | 0.9973 | -0.018651 | 23.2537
31 | 0.002898 | 0.00072622 | -0.0028979 | -0.00072629 | 9.5037e-08 | -6.7531e-08 | 0.0043467 | 0.0043467 | 0.0043467 | 0.99208 | -0.055531 | 0.99205 | -0.055768 | 1.6099
32 | 0.0007727 | 0.00019347 | -0.00077269 | -0.00019365 | 1.2192e-08 | -1.8293e-07 | 0.0011592 | 0.0011593 | 0.0011593 | 0.99181 | -0.057491 | 0.99179 | -0.057605 | 0.42937
33 | 0.004101 | 0.0010273 | -0.0041004 | -0.0010274 | 5.8615e-07 | -9.4552e-08 | 0.0061535 | 0.0061536 | 0.0061536 | 0.99166 | -0.058554 | 0.99151 | -0.059588 | 2.2791
34 | 0.0041004 | 0.0010274 | -0.0040999 | -0.0010275 | 5.2276e-07 | -8.4237e-08 | 0.0061536 | 0.0061537 | 0.0061537 | 0.99151 | -0.059588 | 0.99138 | -0.060509 | 2.2791
35 | 0.001856 | 0.0004651 | -0.001856 | -0.00046515 | 1.9739e-08 | -4.4967e-08 | 0.0027857 | 0.0027857 | 0.0027857 | 0.99138 | -0.060509 | 0.99137 | -0.060586 | 1.0318
36 | -0.05232 | -0.013167 | 0.052483 | 0.01323 | 0.00016344 | 6.2328e-05 | 0.079114 | 0.079114 | 0.079114 | 0.9843 | -0.10938 | 0.98747 | -0.087075 | 29.3015
37 | 0.05232 | 0.013167 | -0.052305 | -0.013162 | 1.4758e-05 | 5.6282e-06 | 0.079114 | 0.079114 | 0.079114 | 0.9843 | -0.10938 | 0.98401 | -0.1114 | 29.3015
38 | -0.056602 | -0.014262 | 0.056831 | 0.014349 | 0.00022842 | 8.7208e-05 | 0.085321 | 0.085321 | 0.085321 | 0.98747 | -0.087075 | 0.99158 | -0.058353 | 31.6004
39 | 0.049966 | 0.012575 | -0.049877 | -0.012541 | 8.9605e-05 | 3.4145e-05 | 0.075577 | 0.075578 | 0.075578 | 0.98401 | -0.1114 | 0.98219 | -0.12427 | 27.9917
40 | -0.064407 | -0.016247 | 0.064512 | 0.016287 | 0.00010547 | 3.9632e-05 | 0.096689 | 0.096689 | 0.096689 | 0.99158 | -0.058353 | 0.99325 | -0.046696 | 17.9055
41 | 0.0075759 | 0.0018983 | -0.0075748 | -0.001898 | 1.1108e-06 | 2.4959e-07 | 0.011369 | 0.011369 | 0.011369 | 0.99158 | -0.058353 | 0.99143 | -0.059413 | 4.2106
42 | 0.049265 | 0.012388 | -0.049129 | -0.012337 | 0.00013565 | 5.1679e-05 | 0.074651 | 0.074651 | 0.074651 | 0.98219 | -0.12427 | 0.9794 | -0.14408 | 27.6485
43 | 0.00061182 | 0.00015299 | -0.0006118 | -0.00015333 | 1.4807e-08 | -3.4389e-07 | 0.00092678 | 0.0009269 | 0.0009269 | 0.98219 | -0.12427 | 0.98217 | -0.12445 | 0.3433
44 | 0.012313 | 0.0030716 | -0.012311 | -0.0030709 | 2.1954e-06 | 7.1116e-07 | 0.018464 | 0.018464 | 0.018464 | 0.99202 | -0.056025 | 0.99184 | -0.057325 | 6.8386
45 | 0.015971 | 0.0040047 | -0.01594 | -0.0039938 | 3.1107e-05 | 1.0845e-05 | 0.023957 | 0.023957 | 0.023957 | 0.99202 | -0.056025 | 0.99003 | -0.070104 | 8.873
46 | 0.0092095 | 0.0022936 | -0.0092047 | -0.0022923 | 4.8358e-06 | 1.3359e-06 | 0.013812 | 0.013812 | 0.013812 | 0.99184 | -0.057325 | 0.9913 | -0.061166 | 5.1154
47 | 0.0045629 | 0.0011425 | -0.0045626 | -0.0011425 | 2.7957e-07 | -1.4972e-08 | 0.0068576 | 0.0068577 | 0.0068577 | 0.99003 | -0.070104 | 0.98997 | -0.070548 | 2.5399
48 | 0.084122 | 0.02124 | -0.084105 | -0.021233 | 1.7717e-05 | 6.7204e-06 | 0.12557 | 0.12557 | 0.12557 | 0.9973 | -0.018651 | 0.99708 | -0.02015 | 23.2537
49 | 0.082801 | 0.020906 | -0.082732 | -0.02088 | 6.8651e-05 | 2.6029e-05 | 0.12362 | 0.12362 | 0.12362 | 0.99708 | -0.02015 | 0.99623 | -0.026056 | 22.8933
50 | 0.0033343 | 0.00083519 | -0.0033341 | -0.00083526 | 1.782e-07 | -7.7643e-08 | 0.0050116 | 0.0050116 | 0.0050116 | 0.98997 | -0.070548 | 0.98991 | -0.070934 | 1.8562
51 | 0.0012283 | 0.00030733 | -0.0012283 | -0.00030743 | 1.6602e-08 | -9.3986e-08 | 0.0018461 | 0.0018461 | 0.0018461 | 0.98997 | -0.070548 | 0.98995 | -0.070646 | 0.68376
52 | 0.0033341 | 0.00083526 | -0.0033336 | -0.00083548 | 4.9326e-07 | -2.1482e-07 | 0.0050116 | 0.0050118 | 0.0050118 | 0.98991 | -0.070934 | 0.98976 | -0.072003 | 1.8562
53 | 0.00015885 | 3.9396e-05 | -0.00015885 | -3.9812e-05 | 1.1518e-09 | -4.1605e-07 | 0.00023863 | 0.00023878 | 0.00023878 | 0.98995 | -0.070646 | 0.98994 | -0.070698 | 0.088436
54 | 0.00017402 | 4.3484e-05 | -0.00017401 | -4.3612e-05 | 4.2355e-10 | -1.2811e-07 | 0.00026116 | 0.00026121 | 0.00026121 | 0.9913 | -0.061166 | 0.9913 | -0.061184 | 0.096744
55 | 0.0090306 | 0.0022488 | -0.0090242 | -0.002247 | 6.4529e-06 | 1.7564e-06 | 0.013551 | 0.013551 | 0.013551 | 0.9913 | -0.061166 | 0.99057 | -0.066396 | 5.0188
56 | 0.0090242 | 0.002247 | -0.0090226 | -0.0022466 | 1.5597e-06 | 4.247e-07 | 0.013551 | 0.013551 | 0.013551 | 0.99057 | -0.066396 | 0.99039 | -0.06766 | 5.0188
57 | 0.0088444 | 0.0022019 | -0.0088428 | -0.0022015 | 1.5324e-06 | 4.1031e-07 | 0.013283 | 0.013283 | 0.013283 | 0.99039 | -0.06766 | 0.99022 | -0.068929 | 4.9197
58 | 0.0084874 | 0.0021124 | -0.0084814 | -0.0021109 | 6.0288e-06 | 1.5547e-06 | 0.012749 | 0.012749 | 0.012749 | 0.99022 | -0.068929 | 0.98949 | -0.074132 | 4.7219
59 | 0.0084814 | 0.0021109 | -0.0084723 | -0.0021086 | 9.0712e-06 | 2.3414e-06 | 0.012749 | 0.01275 | 0.01275 | 0.98949 | -0.074132 | 0.9884 | -0.081969 | 4.7221
60 | 0.0074901 | 0.0018624 | -0.0074864 | -0.0018616 | 3.6899e-06 | 8.2291e-07 | 0.011271 | 0.011271 | 0.011271 | 0.9884 | -0.081969 | 0.9879 | -0.085584 | 4.1745
61 | 0.00034008 | 8.4985e-05 | -0.00034008 | -8.5232e-05 | 3.1662e-09 | -2.4641e-07 | 0.00051216 | 0.00051225 | 0.00051225 | 0.9879 | -0.085584 | 0.98789 | -0.085652 | 0.18972
62 | 0.0071463 | 0.0017766 | -0.0071449 | -0.0017763 | 1.4763e-06 | 3.0618e-07 | 0.010759 | 0.010759 | 0.010759 | 0.9879 | -0.085584 | 0.98769 | -0.0871 | 3.9849
63 | 0.0066379 | 0.00165 | -0.0066376 | -0.0016499 | 2.9096e-07 | 5.2183e-08 | 0.0099956 | 0.0099956 | 0.0099956 | 0.98769 | -0.0871 | 0.98764 | -0.087422 | 3.7021
64 | 0.00050697 | 0.00012632 | -0.00050695 | -0.00012705 | 2.1055e-08 | -7.3234e-07 | 0.00076353 | 0.00076379 | 0.00076379 | 0.98769 | -0.0871 | 0.98764 | -0.087402 | 0.28289
65 | 0.0073933 | 0.0018524 | -0.0073887 | -0.0018514 | 4.5653e-06 | 9.7521e-07 | 0.011043 | 0.011043 | 0.011043 | 0.99623 | -0.026056 | 0.99559 | -0.03052 | 4.09
66 | 0.075339 | 0.019028 | -0.075222 | -0.018984 | 0.00011687 | 4.418e-05 | 0.11258 | 0.11258 | 0.11258 | 0.99623 | -0.026056 | 0.99463 | -0.037106 | 20.8484
67 | 0.0038212 | 0.00095731 | -0.0038205 | -0.0009575 | 7.1592e-07 | -1.8198e-07 | 0.005711 | 0.0057112 | 0.0057112 | 0.99559 | -0.03052 | 0.9954 | -0.031874 | 2.1152
68 | 0.073605 | 0.018579 | -0.073506 | -0.018541 | 9.8995e-05 | 3.7397e-05 | 0.11016 | 0.11016 | 0.11016 | 0.99463 | -0.037106 | 0.99325 | -0.046696 | 20.4006
69 | 0.0016164 | 0.00040502 | -0.0016164 | -0.00040511 | 2.8305e-08 | -8.9787e-08 | 0.0024182 | 0.0024182 | 0.0024182 | 0.99463 | -0.037106 | 0.99462 | -0.037232 | 0.89565
70 | -0.0054919 | -0.0013764 | 0.0054944 | 0.0013766 | 2.4685e-06 | 1.996e-07 | 0.0082465 | 0.0082462 | 0.0082465 | 0.99097 | -0.06266 | 0.99143 | -0.059413 | 3.0542
71 | 0.047851 | 0.012016 | -0.047839 | -0.012012 | 1.1875e-05 | 4.522e-06 | 0.072709 | 0.072709 | 0.072709 | 0.9794 | -0.14408 | 0.97915 | -0.14587 | 26.9293
72 | 0.043939 | 0.011035 | -0.0439 | -0.01102 | 3.8873e-05 | 1.4775e-05 | 0.066782 | 0.066782 | 0.066782 | 0.97915 | -0.14587 | 0.97826 | -0.15224 | 24.7342
73 | 0.0039001 | 0.00097695 | -0.0038997 | -0.00097703 | 4.1902e-07 | -7.9259e-08 | 0.0059268 | 0.0059268 | 0.0059268 | 0.97915 | -0.14587 | 0.97904 | -0.14665 | 2.1951
74 | 0.042459 | 0.010659 | -0.042415 | -0.010642 | 4.4187e-05 | 1.6782e-05 | 0.064591 | 0.064591 | 0.064591 | 0.97826 | -0.15224 | 0.97721 | -0.15974 | 23.9224
75 | 0.0027178 | 0.00068082 | -0.0027175 | -0.00068106 | 3.0301e-07 | -2.4131e-07 | 0.0041305 | 0.0041307 | 0.0041307 | 0.97904 | -0.14665 | 0.97893 | -0.14745 | 1.5299
76 | 0.00055659 | 0.00013695 | -0.00055659 | -0.00013712 | 5.9662e-09 | -1.6771e-07 | 0.00084299 | 0.00084305 | 0.00084305 | 0.98142 | -0.13234 | 0.98141 | -0.13242 | 0.31224
77 | 0.00055659 | 0.00013712 | -0.0005565 | -0.00013947 | 8.385e-08 | -2.354e-06 | 0.00084305 | 0.0008439 | 0.0008439 | 0.98141 | -0.13242 | 0.98126 | -0.13352 | 0.31255
78 | 0.0066376 | 0.0016499 | -0.0066337 | -0.0016492 | 3.9004e-06 | 7.0007e-07 | 0.0099956 | 0.0099959 | 0.0099959 | 0.98764 | -0.087422 | 0.98704 | -0.091737 | 3.7022
79 | 0.005534 | 0.0013736 | -0.0055279 | -0.001373 | 6.1162e-06 | 5.526e-07 | 0.0083381 | 0.0083387 | 0.0083387 | 0.98704 | -0.091737 | 0.98592 | -0.099872 | 3.0884
80 | 0.00013633 | 3.3613e-05 | -0.00013633 | -3.4168e-05 | 1.1491e-09 | -5.5474e-07 | 0.00020557 | 0.00020576 | 0.00020576 | 0.98592 | -0.099872 | 0.98591 | -0.099934 | 0.076208
81 | 0.0053916 | 0.0013394 | -0.0053905 | -0.0013393 | 1.0987e-06 | 8.3211e-08 | 0.0081331 | 0.0081332 | 0.0081332 | 0.98592 | -0.099872 | 0.98571 | -0.10137 | 3.0123
82 | -0.00017515 | -4.3898e-05 | 0.00017516 | 4.3599e-05 | 1.0816e-09 | -2.9871e-07 | 0.0002681 | 0.00026799 | 0.0002681 | 0.97215 | -0.19604 | 0.97215 | -0.19599 | 0.099296
83 | -0.00017516 | -4.3599e-05 | 0.00017516 | 4.3497e-05 | 3.6796e-10 | -1.0167e-07 | 0.00026799 | 0.00026796 | 0.00026799 | 0.97215 | -0.19599 | 0.97216 | -0.19598 | 0.099256
84 | -0.00071283 | -0.00017825 | 0.00071284 | 0.00017796 | 1.794e-08 | -2.9265e-07 | 0.0010909 | 0.0010908 | 0.0010909 | 0.97216 | -0.19598 | 0.97218 | -0.19579 | 0.40405
85 | -0.00071284 | -0.00017796 | 0.00071287 | 0.00017757 | 2.3521e-08 | -3.8381e-07 | 0.0010908 | 0.0010907 | 0.0010908 | 0.97218 | -0.19579 | 0.97221 | -0.19555 | 0.40401
86 | -0.019178 | -0.0048071 | 0.019179 | 0.0048076 | 1.218e-06 | 4.4037e-07 | 0.029353 | 0.029353 | 0.029353 | 0.97221 | -0.19555 | 0.97228 | -0.19509 | 10.8716
87 | 0.018465 | 0.0046295 | -0.018457 | -0.0046265 | 8.4408e-06 | 3.0366e-06 | 0.028263 | 0.028263 | 0.028263 | 0.97221 | -0.19555 | 0.97176 | -0.19885 | 10.4676
88 | 0.020917 | 0.0052461 | -0.02091 | -0.0052437 | 6.6206e-06 | 2.4173e-06 | 0.031969 | 0.031969 | 0.031969 | 0.97362 | -0.18547 | 0.9733 | -0.18776 | 11.8406
89 | -0.021416 | -0.0053712 | 0.021427 | 0.0053752 | 1.0852e-05 | 3.9718e-06 | 0.032733 | 0.032733 | 0.032733 | 0.97362 | -0.18547 | 0.97413 | -0.18182 | 12.1232
90 | 0.020751 | 0.0052037 | -0.020744 | -0.0052013 | 6.4691e-06 | 2.3601e-06 | 0.031726 | 0.031726 | 0.031726 | 0.9733 | -0.18776 | 0.97299 | -0.19001 | 11.7502
91 | -0.024077 | -0.0060364 | 0.024103 | 0.006046 | 2.6076e-05 | 9.6442e-06 | 0.036779 | 0.036779 | 0.036779 | 0.97413 | -0.18182 | 0.97521 | -0.17401 | 13.6218
92 | 0.0026496 | 0.00066115 | -0.0026495 | -0.00066124 | 1.0309e-07 | -8.5962e-08 | 0.0040463 | 0.0040464 | 0.0040464 | 0.97413 | -0.18182 | 0.97409 | -0.1821 | 1.4987
93 | 0.02022 | 0.0050698 | -0.020216 | -0.0050685 | 3.6936e-06 | 1.3438e-06 | 0.030923 | 0.030923 | 0.030923 | 0.97299 | -0.19001 | 0.9728 | -0.19132 | 11.453
94 | 0.0022389 | 0.00056063 | -0.0022388 | -0.00056081 | 1.3261e-07 | -1.7621e-07 | 0.003416 | 0.0034161 | 0.0034161 | 0.97521 | -0.17401 | 0.97515 | -0.17444 | 1.2652
95 | -0.026342 | -0.0066066 | 0.026342 | 0.0066067 | 1.3645e-07 | 5.0792e-08 | 0.040195 | 0.040195 | 0.040195 | 0.97521 | -0.17401 | 0.97522 | -0.17397 | 14.887
96 | 0.0017772 | 0.00044261 | -0.0017771 | -0.00044289 | 1.177e-07 | -2.7349e-07 | 0.0027138 | 0.0027139 | 0.0027139 | 0.97409 | -0.1821 | 0.97402 | -0.18259 | 1.0052
97 | 0.019716 | 0.0049433 | -0.019706 | -0.0049395 | 1.0296e-05 | 3.7347e-06 | 0.030159 | 0.030159 | 0.030159 | 0.9728 | -0.19132 | 0.97228 | -0.19509 | 11.1701
98 | 0.001129 | 0.00028267 | -0.0011289 | -0.00028294 | 4.2331e-08 | -2.6888e-07 | 0.0017226 | 0.0017227 | 0.0017227 | 0.97515 | -0.17444 | 0.97512 | -0.17471 | 0.63805
99 | -0.030172 | -0.0075666 | 0.030201 | 0.0075775 | 2.8977e-05 | 1.0871e-05 | 0.046039 | 0.046039 | 0.046039 | 0.97522 | -0.17397 | 0.97619 | -0.16705 | 17.0515
100 | 0.0013629 | 0.00033908 | -0.0013626 | -0.00034001 | 2.2096e-07 | -9.3223e-07 | 0.0020812 | 0.0020815 | 0.0020815 | 0.97402 | -0.18259 | 0.97386 | -0.18377 | 0.77093
101 | -0.032191 | -0.0080761 | 0.032223 | 0.0080884 | 3.2669e-05 | 1.2293e-05 | 0.049072 | 0.049071 | 0.049072 | 0.97619 | -0.16705 | 0.97721 | -0.15974 | 18.1747
102 | 0.00099736 | 0.00024846 | -0.00099733 | -0.00024863 | 2.089e-08 | -1.7144e-07 | 0.0015234 | 0.0015234 | 0.0015234 | 0.97386 | -0.18377 | 0.97384 | -0.18392 | 0.56424
103 | 0.0016234 | 0.00040628 | -0.0016233 | -0.00040683 | 1.8847e-07 | -5.4667e-07 | 0.0024718 | 0.0024721 | 0.0024721 | 0.97721 | -0.15974 | 0.97709 | -0.16058 | 0.91558
104 | 0.0085684 | 0.0021474 | -0.0085664 | -0.0021469 | 2.0256e-06 | 5.4023e-07 | 0.013047 | 0.013047 | 0.013047 | 0.97721 | -0.15974 | 0.97697 | -0.16145 | 4.8324
105 | 0.0068878 | 0.0017262 | -0.0068865 | -0.0017259 | 1.3056e-06 | 2.6414e-07 | 0.010491 | 0.010491 | 0.010491 | 0.97697 | -0.16145 | 0.97678 | -0.16282 | 3.8855
106 | -0.012495 | -0.0031313 | 0.012495 | 0.0031313 | 5.8783e-08 | 1.9429e-08 | 0.019146 | 0.019146 | 0.019146 | 0.97108 | -0.20372 | 0.97109 | -0.20369 | 7.0911
107 | 0.010599 | 0.0026563 | -0.010597 | -0.0026554 | 2.8293e-06 | 8.7561e-07 | 0.016242 | 0.016242 | 0.016242 | 0.97108 | -0.20372 | 0.97081 | -0.20565 | 6.0155
108 | -0.01487 | -0.0037266 | 0.01488 | 0.00373 | 9.9569e-06 | 3.4491e-06 | 0.022786 | 0.022785 | 0.022786 | 0.97109 | -0.20369 | 0.97176 | -0.19885 | 8.4391
109 | 0.0082092 | 0.0020571 | -0.0082071 | -0.0020565 | 2.0844e-06 | 5.4089e-07 | 0.012583 | 0.012583 | 0.012583 | 0.97081 | -0.20565 | 0.97056 | -0.20749 | 4.6602
110 | 0.0056688 | 0.0014204 | -0.0056682 | -0.0014203 | 5.8804e-07 | 7.2004e-08 | 0.008691 | 0.0086911 | 0.0086911 | 0.97056 | -0.20749 | 0.97046 | -0.20824 | 3.2189
111 | 0.0044887 | 0.0011247 | -0.0044884 | -0.0011247 | 2.6695e-07 | -8.9073e-09 | 0.0068825 | 0.0068825 | 0.0068825 | 0.97046 | -0.20824 | 0.9704 | -0.20867 | 2.5491
112 | 0.0022887 | 0.00057338 | -0.0022885 | -0.00057356 | 1.4675e-07 | -1.7943e-07 | 0.0035094 | 0.0035095 | 0.0035095 | 0.9704 | -0.20867 | 0.97033 | -0.20913 | 1.2998
113 | 0.00082323 | 0.000205 | -0.00082313 | -0.0002063 | 1.0608e-07 | -1.2962e-06 | 0.0012574 | 0.0012579 | 0.0012579 | 0.97384 | -0.18392 | 0.97371 | -0.18486 | 0.46589

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15805 | 0.039645

## res_load
| p_mw | q_mvar
0 | 0.00039417 | 9.8788e-05
1 | 0.00037139 | 9.308e-05
2 | 0.00091353 | 0.00022895
3 | 0.000567 | 0.0001421
4 | 0.00039323 | 9.8553e-05
5 | 0.00010246 | 2.568e-05
6 | 0.00027953 | 7.0056e-05
7 | 0.00017096 | 4.2848e-05
8 | 0.00018849 | 4.7241e-05
9 | 0.0073026 | 0.0018302
10 | 0.0018522 | 0.00046421
11 | 0.0052052 | 0.0013045
12 | 0.00753 | 0.0018872
13 | 0.0038595 | 0.00096728
14 | 0.0011948 | 0.00029945
15 | 0.0058676 | 0.0014706
16 | 0.0014328 | 0.00035909
17 | 0.0010304 | 0.00025824
18 | 0.0010736 | 0.00026906
19 | 0.0028979 | 0.00072629
20 | 0.0022439 | 0.00056237
21 | 0.00077269 | 0.00019365
22 | 0.0041191 | 0.0010324
23 | 0.0023388 | 0.00058616
24 | 0.001856 | 0.00046515
25 | 0.0031012 | 0.00077724
26 | 0.011377 | 0.0028513
27 | 0.0013042 | 0.00032688
28 | 0.0010694 | 0.00026803
29 | 0.0033336 | 0.00083548
30 | 0.00015885 | 3.9812e-05
31 | 0.00017401 | 4.3612e-05
32 | 0.00017827 | 4.4679e-05
33 | 0.00035544 | 8.9081e-05
34 | 0.00098219 | 0.00024616
35 | 0.00034008 | 8.5232e-05
36 | 0.0035675 | 0.0008941
37 | 0.0054919 | 0.0013764
38 | 0.0020804 | 0.00052141
39 | 0.0016164 | 0.00040511
40 | 0.0089942 | 0.0022542
41 | 0.0038205 | 0.0009575
42 | 0.0012782 | 0.00032034
43 | 0.0006118 | 0.00015333
44 | 0.001441 | 0.00036114
45 | 0.0011819 | 0.00029621
46 | 0.00089851 | 0.00022519
47 | 0.0005565 | 0.00013947
48 | 0.00050695 | 0.00012705
49 | 0.0010997 | 0.00027561
50 | 0.00053815 | 0.00013487
51 | 0.00013633 | 3.4168e-05
52 | 0.00017515 | 4.3898e-05
53 | 0.00053767 | 0.00013475
54 | 0.00049936 | 0.00012515
55 | 0.00015959 | 3.9997e-05
56 | 0.00052465 | 0.00013149
57 | 0.00087231 | 0.00021862
58 | 0.00049958 | 0.00012521
59 | 0.0011098 | 0.00027814
60 | 0.0038303 | 0.00095996
61 | 0.00041421 | 0.00010381
62 | 0.00052658 | 0.00013197
63 | 0.0011289 | 0.00028294
64 | 0.0019894 | 0.0004986
65 | 0.00036528 | 9.1548e-05
66 | 0.0016233 | 0.00040683
67 | 0.0016786 | 0.00042069
68 | 0.0068865 | 0.0017259
69 | 0.0018953 | 0.00047501
70 | 0.0023752 | 0.00059528
71 | 0.0023874 | 0.00059835
72 | 0.0035769 | 0.00089646
73 | 0.0025383 | 0.00063616
74 | 0.0011795 | 0.00029562
75 | 0.0021997 | 0.00055131
76 | 0.0027175 | 0.00068106
77 | 0.0022885 | 0.00057356
78 | 0.0001741 | 4.3634e-05
79 | 0.00082313 | 0.0002063

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1