## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2299-28_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2299-28_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2299-28_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2299-28_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2299-28_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2299-28_0_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_2299-28_0_3_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_2299-28_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2299-28_0_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2299-28_0_3_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2299-28_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2299-28_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2299-28_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2299-28_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2299-28_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2299-28_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2299-28_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2299-28_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2299-28_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_2299-28_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2299-28_0_3_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2299-28_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_2299-28_0_3_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_2299-28_0_3_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_2299-28_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2299-28_0_3_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_2299-28_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2299-28_0_3_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_2299-28_0_3_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_2299-28_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2299-28_0_3_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2299-28_0_3_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2299-28_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_2299-28_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2299-28_0_3_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_2299-28_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_2299-28_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2299-28_0_3_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_2299-28_0_3_node_37 | 0.4 | n |  | TRUE
39 | bus_MV_36_0_node_200 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2299-28_0_3_load_0 | 0 | 0.0015448 | 0.00038717 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2299-28_0_3_load_3 | 2 | 0.00066914 | 0.0001677 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2299-28_0_3_load_5 | 4 | 0.0014287 | 0.00035808 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2299-28_0_3_load_13 | 5 | 0.0077977 | 0.0019543 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2299-28_0_3_load_2 | 6 | 0.011676 | 0.0029264 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2299-28_0_3_load_16 | 7 | 0.0022383 | 0.00056097 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2299-28_0_3_load_6 | 10 | 0.0013555 | 0.00033972 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2299-28_0_3_load_8 | 12 | 0.0055148 | 0.0013821 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2299-28_0_3_load_9 | 13 | 0.0042899 | 0.0010751 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2299-28_0_3_load_10 | 14 | 0.0023135 | 0.00057981 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2299-28_0_3_load_11 | 15 | 0.0015058 | 0.0003774 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2299-28_0_3_load_12 | 16 | 0.0016726 | 0.0004192 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2299-28_0_3_load_17 | 17 | 0.0014064 | 0.00035248 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2299-28_0_3_load_18 | 18 | 0.0018507 | 0.00046383 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2299-28_0_3_load_15 | 19 | 0.0062981 | 0.0015785 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2299-28_0_3_load_24 | 20 | 0.0062009 | 0.0015541 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2299-28_0_3_load_25 | 21 | 0.0061305 | 0.0015365 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2299-28_0_3_load_23 | 22 | 0.0030845 | 0.00077304 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2299-28_0_3_load_26 | 23 | 0.0012311 | 0.00030854 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2299-28_0_3_load_31 | 26 | 0.0021089 | 0.00052854 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2299-28_0_3_load_38 | 27 | 0.0019301 | 0.00048372 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2299-28_0_3_load_32 | 28 | 0.0019419 | 0.00048669 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2299-28_0_3_load_20 | 29 | 0.0073941 | 0.0018531 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2299-28_0_3_load_21 | 30 | 0.0023199 | 0.00058141 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2299-28_0_3_load_22 | 31 | 0.0050354 | 0.001262 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2299-28_0_3_load_29 | 33 | 0.0016466 | 0.00041268 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2299-28_0_3_load_30 | 34 | 0.0018597 | 0.00046608 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2299-28_0_3_load_33 | 35 | 0.0010609 | 0.00026589 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2299-28_0_3_load_35 | 36 | 0.0018168 | 0.00045533 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2299-28_0_3_load_36 | 37 | 0.0018262 | 0.00045769 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2299-28_0_3_load_37 | 38 | 0.0041458 | 0.001039 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2299-28_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.049607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2299-28_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.020025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2299-28_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.058367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2299-28_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.067141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2299-28_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.066729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2299-28_0_3_line_5 | NAYY 4x150 SE | 4 | 10 | 0.027144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2299-28_0_3_line_6 | NAYY 4x150 SE | 5 | 9 | 0.017792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2299-28_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.13683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2299-28_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.018497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2299-28_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.058241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2299-28_0_3_line_10 | NAYY 4x150 SE | 8 | 22 | 0.016592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2299-28_0_3_line_11 | NAYY 4x150 SE | 8 | 23 | 0.024531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2299-28_0_3_line_12 | NAYY 4x150 SE | 9 | 19 | 0.025713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2299-28_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.061694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2299-28_0_3_line_14 | NAYY 4x150 SE | 11 | 12 | 0.018529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2299-28_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.23711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2299-28_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.013086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2299-28_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.0057307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2299-28_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.016537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2299-28_0_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0052261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2299-28_0_3_line_20 | NAYY 4x150 SE | 18 | 24 | 0.033369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2299-28_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.032036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2299-28_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0061367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2299-28_0_3_line_23 | NAYY 4x150 SE | 22 | 30 | 0.017928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2299-28_0_3_line_24 | NAYY 4x150 SE | 23 | 32 | 0.036076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2299-28_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.003757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2299-28_0_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.011673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2299-28_0_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.027679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2299-28_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.04001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2299-28_0_3_line_29 | NAYY 4x150 SE | 28 | 35 | 0.018358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2299-28_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.0094383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2299-28_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.0081225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2299-28_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.024836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2299-28_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.016432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2299-28_0_3_line_34 | NAYY 4x150 SE | 33 | 35 | 0.00061232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2299-28_0_3_line_35 | NAYY 4x150 SE | 34 | 36 | 0.022129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2299-28_0_3_line_36 | NAYY 4x150 SE | 36 | 37 | 0.0049025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2299-28_0_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.011979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2299-28_0_3_trafo_28 | 0.25 MVA 20/0.4 kV | 39 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2588963.8017 | 1170167.1157 | 2588993.2563 | 1170146.1841 | 2589005.2419 | 1170140.0324
1 | 2588963.8017 | 1170167.1157 | 2588972.4969 | 1170185.1546
2 | 2588963.8017 | 1170167.1157 | 2588951.4121 | 1170136.5344 | 2588971.4894 | 1170121.0228
3 | 2588972.4969 | 1170185.1546 | 2589001.6505 | 1170245.6359
4 | 2588971.4894 | 1170121.0228 | 2589003.4229 | 1170112.3594 | 2589025.8371 | 1170098.5556 | 2589031.6882 | 1170094.1618
5 | 2589013.437 | 1170270.0877 | 2589001.6505 | 1170245.6359
6 | 2589045.9156 | 1170083.4778 | 2589031.6882 | 1170094.1618
7 | 2589093.1352 | 1170049.4853 | 2589156.305 | 1170170.8649
8 | 2589109.1238 | 1170040.1847 | 2589093.1352 | 1170049.4853
9 | 2589045.9156 | 1170083.4778 | 2589067.9866 | 1170065.9841 | 2589093.1352 | 1170049.4853 | 2589093.1352 | 1170049.4853
10 | 2589109.1238 | 1170040.1847 | 2589100.4255 | 1170026.0555
11 | 2589109.1238 | 1170040.1847 | 2589126.5322 | 1170033.3162 | 2589132.1615 | 1170031.8535
12 | 2589045.9156 | 1170083.4778 | 2589041.6946 | 1170072.2132 | 2589039.2957 | 1170058.7417
13 | 2589040.6073 | 1170325.4758 | 2589025.0955 | 1170294.0774 | 2589017.393 | 1170278.2948 | 2589013.437 | 1170270.0877
14 | 2589040.6073 | 1170325.4758 | 2589057.4817 | 1170317.8214
15 | 2589242.3634 | 1169985.1835 | 2589458.0217 | 1169886.6285
16 | 2589233.5845 | 1169975.4793 | 2589242.3634 | 1169985.1835
17 | 2589229.74 | 1169971.2296 | 2589233.5845 | 1169975.4793
18 | 2589229.74 | 1169971.2296 | 2589218.6457 | 1169958.966
19 | 2589215.1514 | 1169955.08 | 2589216.3977 | 1169956.481 | 2589218.6457 | 1169958.966
20 | 2589190.4909 | 1169935.0061 | 2589194.6982 | 1169934.5982 | 2589199.6539 | 1169937.6575 | 2589215.1514 | 1169955.08
21 | 2589033.6792 | 1170027.2015 | 2589039.2957 | 1170058.7417
22 | 2589032.6033 | 1170021.1599 | 2589033.6792 | 1170027.2015
23 | 2589091.027 | 1170010.7889 | 2589100.4255 | 1170026.0555
24 | 2589167.0778 | 1170022.7815 | 2589132.1615 | 1170031.8535
25 | 2589190.4909 | 1169935.0061 | 2589188.0145 | 1169932.1758
26 | 2589190.4909 | 1169935.0061 | 2589188.9593 | 1169938.4661 | 2589190.8864 | 1169946.1163
27 | 2589188.0145 | 1169932.1758 | 2589209.0946 | 1169914.2382
28 | 2589190.8864 | 1169946.1163 | 2589194.269 | 1169959.5449 | 2589190.2335 | 1169974.493 | 2589186.668 | 1169984.5586
29 | 2589180.5383 | 1170001.8632 | 2589186.668 | 1169984.5586
30 | 2589086.079 | 1170002.7515 | 2589091.027 | 1170010.7889
31 | 2589081.8208 | 1169995.8346 | 2589086.079 | 1170002.7515
32 | 2589167.0778 | 1170022.7815 | 2589173.3492 | 1170017.3118 | 2589177.514 | 1170010.4008 | 2589180.3338 | 1170002.4404
33 | 2589167.0778 | 1170022.7815 | 2589158.4667 | 1170008.7868
34 | 2589180.3338 | 1170002.4404 | 2589180.5383 | 1170001.8632
35 | 2589158.4667 | 1170008.7868 | 2589146.8698 | 1169989.9396
36 | 2589146.8698 | 1169989.9396 | 2589144.3006 | 1169985.7642
37 | 2589136.383 | 1169976.8365 | 2589143.0135 | 1169983.6723 | 2589144.3006 | 1169985.7642

## bus_geodata
| x | y | coords
0 | 2589005.2419 | 1170140.0324
1 | 2588963.8017 | 1170167.1157
2 | 2588972.4969 | 1170185.1546
3 | 2588971.4894 | 1170121.0228
4 | 2589001.6505 | 1170245.6359
5 | 2589031.6882 | 1170094.1618
6 | 2589156.305 | 1170170.8649
7 | 2589093.1352 | 1170049.4853
8 | 2589109.1238 | 1170040.1847
9 | 2589045.9156 | 1170083.4778
10 | 2589013.437 | 1170270.0877
11 | 2589040.6073 | 1170325.4758
12 | 2589057.4817 | 1170317.8214
13 | 2589458.0217 | 1169886.6285
14 | 2589242.3634 | 1169985.1835
15 | 2589233.5845 | 1169975.4793
16 | 2589229.74 | 1169971.2295
17 | 2589218.6457 | 1169958.966
18 | 2589215.1514 | 1169955.08
19 | 2589039.2957 | 1170058.7417
20 | 2589033.6792 | 1170027.2015
21 | 2589032.6033 | 1170021.1599
22 | 2589100.4255 | 1170026.0555
23 | 2589132.1615 | 1170031.8535
24 | 2589190.4909 | 1169935.0061
25 | 2589188.0145 | 1169932.1758
26 | 2589190.8864 | 1169946.1163
27 | 2589209.0946 | 1169914.2382
28 | 2589186.668 | 1169984.5586
29 | 2589086.079 | 1170002.7515
30 | 2589091.027 | 1170010.7889
31 | 2589081.8208 | 1169995.8346
32 | 2589167.0778 | 1170022.7815
33 | 2589180.3338 | 1170002.4404
34 | 2589158.4667 | 1170008.7868
35 | 2589180.5383 | 1170001.8632
36 | 2589146.8698 | 1169989.9396
37 | 2589144.3006 | 1169985.7642
38 | 2589136.383 | 1169976.8365
39 | 2589081.8208 | 1169995.8346

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9931 | -0.048419 | 0.0015448 | 0.00038717
1 | 0.99321 | -0.047642 | 0 | 0
2 | 0.99295 | -0.049464 | 0.00066914 | 0.0001677
3 | 0.99409 | -0.041424 | 0 | 0
4 | 0.99215 | -0.055118 | 0.0014287 | 0.00035808
5 | 0.9951 | -0.034325 | 0.0077977 | 0.0019543
6 | 0.99637 | -0.025447 | 0.011676 | 0.0029264
7 | 0.99865 | -0.0094124 | 0.0022383 | 0.00056097
8 | 1 | 0 | -0.10253 | -0.025538
9 | 0.99557 | -0.031036 | 0 | 0
10 | 0.99188 | -0.057011 | 0.0013555 | 0.00033972
11 | 0.99139 | -0.060468 | 0 | 0
12 | 0.99125 | -0.061505 | 0.0055148 | 0.0013821
13 | 0.99212 | -0.055404 | 0.0042899 | 0.0010751
14 | 0.99358 | -0.045078 | 0.0023135 | 0.00057981
15 | 0.9937 | -0.044201 | 0.0015058 | 0.0003774
16 | 0.99377 | -0.04373 | 0.0016726 | 0.0004192
17 | 0.994 | -0.042092 | 0.0014064 | 0.00035248
18 | 0.99409 | -0.0415 | 0.0018507 | 0.00046383
19 | 0.99488 | -0.035864 | 0.0062981 | 0.0015785
20 | 0.99431 | -0.039851 | 0.0062009 | 0.0015541
21 | 0.99426 | -0.04023 | 0.0061305 | 0.0015365
22 | 0.99958 | -0.0029551 | 0.0030845 | 0.00077304
23 | 0.99885 | -0.0080049 | 0.0012311 | 0.00030854
24 | 0.99471 | -0.037099 | 0 | 0
25 | 0.9947 | -0.037172 | 0 | 0
26 | 0.99496 | -0.035333 | 0.0021089 | 0.00052854
27 | 0.99462 | -0.037711 | 0.0019301 | 0.00048372
28 | 0.99594 | -0.028436 | 0.0019419 | 0.00048669
29 | 0.99903 | -0.0067708 | 0.0073941 | 0.0018531
30 | 0.9992 | -0.0055978 | 0.0023199 | 0.00058141
31 | 0.99897 | -0.0071799 | 0.0050354 | 0.001262
32 | 0.99723 | -0.019364 | 0 | 0
33 | 0.99646 | -0.024794 | 0.0016466 | 0.00041268
34 | 0.99701 | -0.020956 | 0.0018597 | 0.00046608
35 | 0.99644 | -0.024918 | 0.0010609 | 0.00026589
36 | 0.99676 | -0.022688 | 0.0018168 | 0.00045533
37 | 0.99672 | -0.022982 | 0.0018262 | 0.00045769
38 | 0.99665 | -0.023481 | 0.0041458 | 0.001039
39 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0015448 | -0.00038717 | 0.001545 | 0.00038659 | 1.6583e-07 | -5.7814e-07 | 0.0023147 | 0.0023145 | 0.0023147 | 0.9931 | -0.048419 | 0.99321 | -0.047642 | 0.85729
1 | 0.0089822 | 0.0022505 | -0.0089799 | -0.0022499 | 2.2628e-06 | 6.1122e-07 | 0.013457 | 0.013457 | 0.013457 | 0.99321 | -0.047642 | 0.99295 | -0.049464 | 4.984
2 | -0.010527 | -0.0026371 | 0.010536 | 0.0026398 | 9.059e-06 | 2.7282e-06 | 0.015771 | 0.015771 | 0.015771 | 0.99321 | -0.047642 | 0.99409 | -0.041424 | 5.8412
3 | 0.0083108 | 0.0020822 | -0.0083043 | -0.0020806 | 6.4984e-06 | 1.6316e-06 | 0.012454 | 0.012454 | 0.012454 | 0.99295 | -0.049464 | 0.99215 | -0.055118 | 4.6128
4 | -0.010536 | -0.0026398 | 0.010547 | 0.0026429 | 1.0356e-05 | 3.1172e-06 | 0.015771 | 0.015771 | 0.015771 | 0.99409 | -0.041424 | 0.9951 | -0.034325 | 5.8411
5 | 0.0068755 | 0.0017225 | -0.0068737 | -0.0017221 | 1.801e-06 | 3.4225e-07 | 0.010312 | 0.010312 | 0.010312 | 0.99215 | -0.055118 | 0.99188 | -0.057011 | 3.8192
6 | -0.018344 | -0.0045972 | 0.018353 | 0.0046002 | 8.3541e-06 | 2.9819e-06 | 0.027431 | 0.027431 | 0.027431 | 0.9951 | -0.034325 | 0.99557 | -0.031036 | 10.1596
7 | -0.011676 | -0.0029264 | 0.011702 | 0.0029346 | 2.5963e-05 | 8.1994e-06 | 0.017438 | 0.017437 | 0.017438 | 0.99637 | -0.025447 | 0.99865 | -0.0094124 | 6.4585
8 | -0.051054 | -0.012813 | 0.05112 | 0.012839 | 6.6803e-05 | 2.5451e-05 | 0.076077 | 0.076077 | 0.076077 | 0.99865 | -0.0094124 | 1 | 0 | 28.1768
9 | 0.037113 | 0.0093179 | -0.037002 | -0.0092759 | 0.00011116 | 4.1994e-05 | 0.055305 | 0.055305 | 0.055305 | 0.99865 | -0.0094124 | 0.99557 | -0.031036 | 20.4834
10 | 0.017849 | 0.0044747 | -0.017841 | -0.0044721 | 7.3035e-06 | 2.5915e-06 | 0.02656 | 0.02656 | 0.02656 | 1 | 0 | 0.99958 | -0.0029551 | 9.837
11 | 0.032762 | 0.0082245 | -0.032726 | -0.0082109 | 3.6386e-05 | 1.3673e-05 | 0.048755 | 0.048755 | 0.048755 | 1 | 0 | 0.99885 | -0.0080049 | 18.0575
12 | 0.018649 | 0.0046757 | -0.018637 | -0.0046712 | 1.2467e-05 | 4.4607e-06 | 0.027874 | 0.027874 | 0.027874 | 0.99557 | -0.031036 | 0.99488 | -0.035864 | 10.3239
13 | 0.0055183 | 0.0013824 | -0.0055156 | -0.0013822 | 2.6383e-06 | 2.1882e-07 | 0.0082782 | 0.0082785 | 0.0082785 | 0.99188 | -0.057011 | 0.99139 | -0.060468 | 3.0661
14 | 0.0055156 | 0.0013822 | -0.0055148 | -0.0013821 | 7.9242e-07 | 6.5887e-08 | 0.0082785 | 0.0082786 | 0.0082786 | 0.99139 | -0.060468 | 0.99125 | -0.061505 | 3.0662
15 | -0.0042899 | -0.0010751 | 0.004296 | 0.0010744 | 6.1241e-06 | -7.1098e-07 | 0.0064341 | 0.006433 | 0.0064341 | 0.99212 | -0.055404 | 0.99358 | -0.045078 | 2.383
16 | -0.0066095 | -0.0016542 | 0.0066103 | 0.0016544 | 7.9994e-07 | 1.3817e-07 | 0.0098978 | 0.0098977 | 0.0098978 | 0.99358 | -0.045078 | 0.9937 | -0.044201 | 3.6658
17 | -0.0081161 | -0.0020318 | 0.0081166 | 0.0020319 | 5.2811e-07 | 1.2888e-07 | 0.012153 | 0.012153 | 0.012153 | 0.9937 | -0.044201 | 0.99377 | -0.04373 | 4.501
18 | -0.0097893 | -0.0024511 | 0.0097915 | 0.0024517 | 2.2168e-06 | 6.3832e-07 | 0.014657 | 0.014657 | 0.014657 | 0.99377 | -0.04373 | 0.994 | -0.042092 | 5.4285
19 | -0.011198 | -0.0028042 | 0.011199 | 0.0028045 | 9.163e-07 | 2.8467e-07 | 0.016762 | 0.016762 | 0.016762 | 0.994 | -0.042092 | 0.99409 | -0.0415 | 6.2083
20 | -0.01305 | -0.0032683 | 0.013057 | 0.003271 | 7.9441e-06 | 2.6225e-06 | 0.019533 | 0.019533 | 0.019533 | 0.99409 | -0.0415 | 0.99471 | -0.037099 | 7.2343
21 | 0.012339 | 0.0030928 | -0.012332 | -0.0030906 | 6.8083e-06 | 2.2028e-06 | 0.018455 | 0.018455 | 0.018455 | 0.99488 | -0.035864 | 0.99431 | -0.039851 | 6.8351
22 | 0.0061309 | 0.0015365 | -0.0061305 | -0.0015365 | 3.2235e-07 | 4.439e-08 | 0.009175 | 0.009175 | 0.009175 | 0.99431 | -0.039851 | 0.99426 | -0.04023 | 3.3982
23 | 0.014757 | 0.003699 | -0.014752 | -0.0036972 | 5.3988e-06 | 1.8416e-06 | 0.021968 | 0.021968 | 0.021968 | 0.99958 | -0.0029551 | 0.9992 | -0.0055978 | 8.1364
24 | 0.031495 | 0.0079023 | -0.031445 | -0.0078837 | 4.9561e-05 | 1.8591e-05 | 0.046921 | 0.046922 | 0.046922 | 0.99885 | -0.0080049 | 0.99723 | -0.019364 | 17.3783
25 | 0.0019302 | 0.00048338 | -0.0019302 | -0.00048342 | 1.9545e-08 | -4.1251e-08 | 0.0028874 | 0.0028874 | 0.0028874 | 0.99471 | -0.037099 | 0.9947 | -0.037172 | 1.0694
26 | -0.014988 | -0.0037543 | 0.014991 | 0.0037556 | 3.6613e-06 | 1.2566e-06 | 0.02242 | 0.02242 | 0.02242 | 0.99471 | -0.037099 | 0.99496 | -0.035333 | 8.3037
27 | 0.0019302 | 0.00048342 | -0.0019301 | -0.00048372 | 1.44e-07 | -3.0388e-07 | 0.0028874 | 0.0028875 | 0.0028875 | 0.9947 | -0.037172 | 0.99462 | -0.037711 | 1.0694
28 | -0.0171 | -0.0042841 | 0.017117 | 0.0042899 | 1.6328e-05 | 5.7599e-06 | 0.025574 | 0.025574 | 0.025574 | 0.99496 | -0.035333 | 0.99594 | -0.028436 | 9.4718
29 | -0.019059 | -0.0047766 | 0.019068 | 0.0047799 | 9.2884e-06 | 3.3334e-06 | 0.028475 | 0.028475 | 0.028475 | 0.99594 | -0.028436 | 0.99644 | -0.024918 | 10.5463
30 | -0.01243 | -0.0031151 | 0.012432 | 0.0031158 | 2.0186e-06 | 6.5279e-07 | 0.018514 | 0.018513 | 0.018514 | 0.99903 | -0.0067708 | 0.9992 | -0.0055978 | 6.8569
31 | 0.0050356 | 0.001262 | -0.0050354 | -0.001262 | 2.8513e-07 | 3.3149e-09 | 0.0075003 | 0.0075004 | 0.0075004 | 0.99903 | -0.0067708 | 0.99897 | -0.0071799 | 2.7779
32 | 0.021792 | 0.0054646 | -0.021776 | -0.0054586 | 1.6387e-05 | 5.979e-06 | 0.032518 | 0.032518 | 0.032518 | 0.99723 | -0.019364 | 0.99646 | -0.024794 | 12.0437
33 | 0.009653 | 0.0024191 | -0.0096509 | -0.0024185 | 2.1272e-06 | 6.0383e-07 | 0.014404 | 0.014404 | 0.014404 | 0.99723 | -0.019364 | 0.99701 | -0.020956 | 5.3347
34 | 0.020129 | 0.0050459 | -0.020129 | -0.0050458 | 3.4524e-07 | 1.2481e-07 | 0.030059 | 0.030059 | 0.030059 | 0.99646 | -0.024794 | 0.99644 | -0.024918 | 11.133
35 | 0.0077912 | 0.0019525 | -0.0077893 | -0.001952 | 1.8671e-06 | 4.2962e-07 | 0.011628 | 0.011628 | 0.011628 | 0.99701 | -0.020956 | 0.99676 | -0.022688 | 4.3068
36 | 0.0059725 | 0.0014967 | -0.0059723 | -0.0014967 | 2.4319e-07 | 2.9636e-08 | 0.008916 | 0.008916 | 0.008916 | 0.99676 | -0.022688 | 0.99672 | -0.022982 | 3.3022
37 | 0.0041461 | 0.001039 | -0.0041458 | -0.001039 | 2.8639e-07 | -4.5969e-08 | 0.0061897 | 0.0061898 | 0.0061898 | 0.99672 | -0.022982 | 0.99665 | -0.023481 | 2.2925

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10253 | 0.025538

## res_load
| p_mw | q_mvar
0 | 0.0015448 | 0.00038717
1 | 0.00066914 | 0.0001677
2 | 0.0014287 | 0.00035808
3 | 0.0077977 | 0.0019543
4 | 0.011676 | 0.0029264
5 | 0.0022383 | 0.00056097
6 | 0.0013555 | 0.00033972
7 | 0.0055148 | 0.0013821
8 | 0.0042899 | 0.0010751
9 | 0.0023135 | 0.00057981
10 | 0.0015058 | 0.0003774
11 | 0.0016726 | 0.0004192
12 | 0.0014064 | 0.00035248
13 | 0.0018507 | 0.00046383
14 | 0.0062981 | 0.0015785
15 | 0.0062009 | 0.0015541
16 | 0.0061305 | 0.0015365
17 | 0.0030845 | 0.00077304
18 | 0.0012311 | 0.00030854
19 | 0.0021089 | 0.00052854
20 | 0.0019301 | 0.00048372
21 | 0.0019419 | 0.00048669
22 | 0.0073941 | 0.0018531
23 | 0.0023199 | 0.00058141
24 | 0.0050354 | 0.001262
25 | 0.0016466 | 0.00041268
26 | 0.0018597 | 0.00046608
27 | 0.0010609 | 0.00026589
28 | 0.0018168 | 0.00045533
29 | 0.0018262 | 0.00045769
30 | 0.0041458 | 0.001039

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1