## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2299-2_1_2_node_90 | 0.4 | n |  | TRUE
1 | bus_LV_2299-2_1_2_node_91 | 0.4 | n |  | TRUE
2 | bus_LV_2299-2_1_2_node_39 | 0.4 | n |  | TRUE
3 | bus_LV_2299-2_1_2_node_40 | 0.4 | n |  | TRUE
4 | bus_LV_2299-2_1_2_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_2299-2_1_2_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_2299-2_1_2_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_2299-2_1_2_node_96 | 0.4 | n |  | TRUE
8 | bus_LV_2299-2_1_2_node_60 | 0.4 | n |  | TRUE
9 | bus_LV_2299-2_1_2_node_94 | 0.4 | n |  | TRUE
10 | bus_LV_2299-2_1_2_node_43 | 0.4 | n |  | TRUE
11 | bus_LV_2299-2_1_2_node_72 | 0.4 | n |  | TRUE
12 | bus_LV_2299-2_1_2_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_2299-2_1_2_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_2299-2_1_2_node_59 | 0.4 | n |  | TRUE
15 | bus_LV_2299-2_1_2_node_75 | 0.4 | n |  | TRUE
16 | bus_LV_2299-2_1_2_node_73 | 0.4 | n |  | TRUE
17 | bus_LV_2299-2_1_2_node_54 | 0.4 | n |  | TRUE
18 | bus_LV_2299-2_1_2_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_2299-2_1_2_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_2299-2_1_2_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_2299-2_1_2_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_2299-2_1_2_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_2299-2_1_2_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_2299-2_1_2_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_2299-2_1_2_node_116 | 0.4 | n |  | TRUE
26 | bus_LV_2299-2_1_2_node_55 | 0.4 | n |  | TRUE
27 | bus_LV_2299-2_1_2_node_66 | 0.4 | n |  | TRUE
28 | bus_LV_2299-2_1_2_node_67 | 0.4 | n |  | TRUE
29 | bus_LV_2299-2_1_2_node_115 | 0.4 | n |  | TRUE
30 | bus_LV_2299-2_1_2_node_117 | 0.4 | n |  | TRUE
31 | bus_LV_2299-2_1_2_node_99 | 0.4 | n |  | TRUE
32 | bus_LV_2299-2_1_2_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_2299-2_1_2_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_2299-2_1_2_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_2299-2_1_2_node_63 | 0.4 | n |  | TRUE
36 | bus_LV_2299-2_1_2_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_2299-2_1_2_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_2299-2_1_2_node_69 | 0.4 | n |  | TRUE
39 | bus_LV_2299-2_1_2_node_106 | 0.4 | n |  | TRUE
40 | bus_LV_2299-2_1_2_node_110 | 0.4 | n |  | TRUE
41 | bus_LV_2299-2_1_2_node_68 | 0.4 | n |  | TRUE
42 | bus_LV_2299-2_1_2_node_70 | 0.4 | n |  | TRUE
43 | bus_LV_2299-2_1_2_node_71 | 0.4 | n |  | TRUE
44 | bus_LV_2299-2_1_2_node_108 | 0.4 | n |  | TRUE
45 | bus_LV_2299-2_1_2_node_105 | 0.4 | n |  | TRUE
46 | bus_LV_2299-2_1_2_node_79 | 0.4 | n |  | TRUE
47 | bus_LV_2299-2_1_2_node_80 | 0.4 | n |  | TRUE
48 | bus_LV_2299-2_1_2_node_81 | 0.4 | n |  | TRUE
49 | bus_LV_2299-2_1_2_node_82 | 0.4 | n |  | TRUE
50 | bus_LV_2299-2_1_2_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_2299-2_1_2_node_84 | 0.4 | n |  | TRUE
52 | bus_LV_2299-2_1_2_node_89 | 0.4 | n |  | TRUE
53 | bus_LV_2299-2_1_2_node_98 | 0.4 | n |  | TRUE
54 | bus_LV_2299-2_1_2_node_100 | 0.4 | n |  | TRUE
55 | bus_LV_2299-2_1_2_node_93 | 0.4 | n |  | TRUE
56 | bus_LV_2299-2_1_2_node_87 | 0.4 | n |  | TRUE
57 | bus_LV_2299-2_1_2_node_97 | 0.4 | n |  | TRUE
58 | bus_LV_2299-2_1_2_node_85 | 0.4 | n |  | TRUE
59 | bus_LV_2299-2_1_2_node_86 | 0.4 | n |  | TRUE
60 | bus_LV_2299-2_1_2_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_2299-2_1_2_node_92 | 0.4 | n |  | TRUE
62 | bus_LV_2299-2_1_2_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_2299-2_1_2_node_107 | 0.4 | n |  | TRUE
64 | bus_LV_2299-2_1_2_node_109 | 0.4 | n |  | TRUE
65 | bus_MV_0_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2299-2_1_2_load_90 | 0 | 7.6303e-05 | 1.9123e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2299-2_1_2_load_91 | 1 | 0.00017892 | 4.4843e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2299-2_1_2_load_39 | 2 | 0.00079799 | 0.00019999 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2299-2_1_2_load_41 | 4 | 0.0027117 | 0.00067961 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2299-2_1_2_load_42 | 5 | 0.0031581 | 0.0007915 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2299-2_1_2_load_96 | 7 | 8.0911e-05 | 2.0278e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2299-2_1_2_load_60 | 8 | 0.0027447 | 0.0006879 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2299-2_1_2_load_94 | 9 | 8.1486e-05 | 2.0422e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2299-2_1_2_load_72 | 11 | 0.0042597 | 0.0010676 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2299-2_1_2_load_59 | 14 | 0.00097778 | 0.00024505 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2299-2_1_2_load_75 | 15 | 0.0023508 | 0.00058917 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2299-2_1_2_load_73 | 16 | 0.0024319 | 0.00060949 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2299-2_1_2_load_54 | 17 | 0.00016729 | 4.1927e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2299-2_1_2_load_52 | 18 | 0.00040727 | 0.00010207 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2299-2_1_2_load_46 | 19 | 0.00059316 | 0.00014866 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2299-2_1_2_load_48 | 21 | 0.0012539 | 0.00031425 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2299-2_1_2_load_49 | 22 | 0.00046008 | 0.00011531 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2299-2_1_2_load_116 | 25 | 0.0016969 | 0.00042527 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2299-2_1_2_load_55 | 26 | 0.0014383 | 0.00036048 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2299-2_1_2_load_115 | 29 | 0.00019395 | 4.8607e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2299-2_1_2_load_117 | 30 | 0.0022147 | 0.00055506 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2299-2_1_2_load_57 | 33 | 0.0028356 | 0.00071067 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2299-2_1_2_load_58 | 34 | 0.0011708 | 0.00029342 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2299-2_1_2_load_64 | 36 | 0.0011062 | 0.00027723 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2299-2_1_2_load_69 | 38 | 0.0013386 | 0.00033548 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2299-2_1_2_load_110 | 40 | 0.00056062 | 0.0001405 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2299-2_1_2_load_68 | 41 | 0.0020827 | 0.00052198 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2299-2_1_2_load_70 | 42 | 0.00098851 | 0.00024774 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2299-2_1_2_load_71 | 43 | 0.0030626 | 0.00076757 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2299-2_1_2_load_108 | 44 | 0.0010361 | 0.00025966 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2299-2_1_2_load_105 | 45 | 0.00044746 | 0.00011214 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2299-2_1_2_load_79 | 46 | 0.00039234 | 9.8329e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2299-2_1_2_load_80 | 47 | 9.3869e-05 | 2.3526e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2299-2_1_2_load_84 | 51 | 8.7375e-05 | 2.1898e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2299-2_1_2_load_98 | 53 | 0.00010798 | 2.7063e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2299-2_1_2_load_100 | 54 | 7.6894e-05 | 1.9271e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2299-2_1_2_load_93 | 55 | 0.00014908 | 3.7362e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2299-2_1_2_load_87 | 56 | 0.0001232 | 3.0876e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2299-2_1_2_load_97 | 57 | 8.5785e-05 | 2.15e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2299-2_1_2_load_85 | 58 | 0.00012612 | 3.1609e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2299-2_1_2_load_86 | 59 | 9.7688e-05 | 2.4483e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2299-2_1_2_load_88 | 60 | 0.00013037 | 3.2675e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2299-2_1_2_load_92 | 61 | 9.84e-05 | 2.4661e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2299-2_1_2_load_95 | 62 | 8.1383e-05 | 2.0396e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2299-2_1_2_load_109 | 64 | 0.0025662 | 0.00064315 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2299-2_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2299-2_1_2_line_1 | NAYY 4x150 SE | 1 | 61 | 0.028605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2299-2_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.02986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2299-2_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2299-2_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.08077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2299-2_1_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.28721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2299-2_1_2_line_6 | NAYY 4x150 SE | 6 | 15 | 0.31682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2299-2_1_2_line_7 | NAYY 4x150 SE | 6 | 10 | 0.30758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2299-2_1_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.20038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2299-2_1_2_line_9 | NAYY 4x150 SE | 7 | 9 | 0.011414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2299-2_1_2_line_10 | NAYY 4x150 SE | 8 | 33 | 0.18508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2299-2_1_2_line_11 | NAYY 4x150 SE | 9 | 62 | 0.002543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2299-2_1_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.050976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2299-2_1_2_line_13 | NAYY 4x150 SE | 11 | 16 | 0.014085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2299-2_1_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.058691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2299-2_1_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.042472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_2299-2_1_2_line_16 | NAYY 4x150 SE | 13 | 17 | 0.20717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2299-2_1_2_line_17 | NAYY 4x150 SE | 13 | 18 | 0.12929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_2299-2_1_2_line_18 | NAYY 4x150 SE | 16 | 43 | 0.027982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2299-2_1_2_line_19 | NAYY 4x150 SE | 17 | 32 | 0.2023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2299-2_1_2_line_20 | NAYY 4x150 SE | 18 | 23 | 0.077327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_2299-2_1_2_line_21 | NAYY 4x150 SE | 19 | 20 | 0.041083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2299-2_1_2_line_22 | NAYY 4x150 SE | 19 | 21 | 0.038195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2299-2_1_2_line_23 | NAYY 4x150 SE | 20 | 22 | 0.10003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2299-2_1_2_line_24 | NAYY 4x150 SE | 20 | 23 | 0.069418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2299-2_1_2_line_25 | NAYY 4x150 SE | 23 | 26 | 0.046646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2299-2_1_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.15659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2299-2_1_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.055298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2299-2_1_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.086924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_2299-2_1_2_line_29 | NAYY 4x150 SE | 27 | 28 | 0.15823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_2299-2_1_2_line_30 | NAYY 4x150 SE | 28 | 37 | 0.075809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2299-2_1_2_line_31 | NAYY 4x150 SE | 28 | 38 | 0.15067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_2299-2_1_2_line_32 | NAYY 4x150 SE | 29 | 30 | 0.2876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2299-2_1_2_line_33 | NAYY 4x150 SE | 29 | 31 | 0.020284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2299-2_1_2_line_34 | NAYY 4x150 SE | 31 | 49 | 0.042766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2299-2_1_2_line_35 | NAYY 4x150 SE | 32 | 33 | 0.042835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2299-2_1_2_line_36 | NAYY 4x150 SE | 32 | 34 | 0.044542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2299-2_1_2_line_37 | NAYY 4x150 SE | 34 | 35 | 0.018844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2299-2_1_2_line_38 | NAYY 4x150 SE | 35 | 36 | 0.036976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2299-2_1_2_line_39 | NAYY 4x150 SE | 37 | 39 | 0.024551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2299-2_1_2_line_40 | NAYY 4x150 SE | 37 | 40 | 0.026887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2299-2_1_2_line_41 | NAYY 4x150 SE | 38 | 41 | 0.0099752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2299-2_1_2_line_42 | NAYY 4x150 SE | 39 | 44 | 0.020131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2299-2_1_2_line_43 | NAYY 4x150 SE | 39 | 45 | 0.041278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2299-2_1_2_line_44 | NAYY 4x150 SE | 41 | 42 | 0.12793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2299-2_1_2_line_45 | NAYY 4x150 SE | 42 | 43 | 0.0069052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2299-2_1_2_line_46 | NAYY 4x150 SE | 45 | 63 | 0.030982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2299-2_1_2_line_47 | NAYY 4x150 SE | 46 | 47 | 0.0085286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2299-2_1_2_line_48 | NAYY 4x150 SE | 46 | 48 | 0.016703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2299-2_1_2_line_49 | NAYY 4x150 SE | 47 | 49 | 0.0035537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2299-2_1_2_line_50 | NAYY 4x150 SE | 48 | 50 | 0.022707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2299-2_1_2_line_51 | NAYY 4x150 SE | 48 | 51 | 0.0060584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2299-2_1_2_line_52 | NAYY 4x150 SE | 49 | 52 | 0.030498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2299-2_1_2_line_53 | NAYY 4x150 SE | 50 | 53 | 0.014938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2299-2_1_2_line_54 | NAYY 4x150 SE | 51 | 54 | 0.020992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2299-2_1_2_line_55 | NAYY 4x150 SE | 52 | 55 | 0.011512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2299-2_1_2_line_56 | NAYY 4x150 SE | 52 | 56 | 0.032066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2299-2_1_2_line_57 | NAYY 4x150 SE | 53 | 57 | 0.046668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2299-2_1_2_line_58 | NAYY 4x150 SE | 55 | 61 | 0.016017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2299-2_1_2_line_59 | NAYY 4x150 SE | 56 | 58 | 0.012877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2299-2_1_2_line_60 | NAYY 4x150 SE | 57 | 62 | 0.0079988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2299-2_1_2_line_61 | NAYY 4x150 SE | 58 | 59 | 0.026198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2299-2_1_2_line_62 | NAYY 4x150 SE | 59 | 60 | 0.02689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2299-2_1_2_line_63 | NAYY 4x150 SE | 63 | 64 | 0.029199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2299-2_1_2_trafo_59 | 0.25 MVA 20/0.4 kV | 65 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26
0 | 2589427.6897 | 1177815.5805 | 2589432.8512 | 1177831.077
1 | 2589432.8512 | 1177831.077 | 2589441.8906 | 1177858.2163
2 | 2589388.1273 | 1178854.7302 | 2589400.8037 | 1178877.4414 | 2589400.6308 | 1178881.2882
3 | 2589399.6427 | 1178903.2677 | 2589400.6308 | 1178881.2882
4 | 2589388.1273 | 1178854.7302 | 2589395.0738 | 1178847.3251 | 2589406.8665 | 1178837.1545 | 2589417.6624 | 1178829.1868 | 2589428.323 | 1178822.4644 | 2589451.7378 | 1178809.1605 | 2589453.6058 | 1178808.2173
5 | 2589267.6483 | 1179094.6686 | 2589274.206 | 1179092.1778 | 2589279.4258 | 1179089.1446 | 2589286.0232 | 1179083.2853 | 2589289.6284 | 1179074.4854 | 2589291.3748 | 1179064.2993 | 2589291.3518 | 1179038.8085 | 2589298.2792 | 1179037.9734 | 2589305.1657 | 1179035.6376 | 2589314.1259 | 1179030.9525 | 2589320.7181 | 1179026.3939 | 2589327.0331 | 1179020.5574 | 2589333.4848 | 1179014.3204 | 2589337.5302 | 1179008.1322 | 2589341.5026 | 1178999.5429 | 2589344.785 | 1178989.5764 | 2589350.7838 | 1178965.0309 | 2589367.772 | 1178895.5429 | 2589372.5217 | 1178881.5161 | 2589377.4155 | 1178871.2355 | 2589382.0763 | 1178863.0452 | 2589388.1273 | 1178854.7302
6 | 2589267.6483 | 1179094.6686 | 2589259.2823 | 1179094.1279 | 2589254.9859 | 1179092.3681 | 2589249.9829 | 1179088.5752 | 2589246.2179 | 1179085.0024 | 2589240.8666 | 1179078.6755 | 2589218.7637 | 1179052.0686 | 2589211.6035 | 1179042.4322 | 2589205.9638 | 1179032.982 | 2589201.2083 | 1179022.4964 | 2589194.3949 | 1179006.1337 | 2589185.3198 | 1178993.8328 | 2589177.2441 | 1178984.9763 | 2589152.7517 | 1178968.0122 | 2589141.8258 | 1178963.0074 | 2589138.5171 | 1178962.5576 | 2589133.4986 | 1178962.8781 | 2589128.8494 | 1178964.643 | 2589121.3356 | 1178970.682 | 2589117.5557 | 1178975.7582 | 2589115.8144 | 1178980.197 | 2589115.0403 | 1178987.1686 | 2589115.851 | 1178991.8473 | 2589117.3806 | 1178997.0027 | 2589125.6315 | 1179026.4026 | 2589124.0428 | 1179055.8206 | 2589115.9113 | 1179070.6434
7 | 2589190.1948 | 1178834.5983 | 2589230.2259 | 1178893.4335 | 2589233.1572 | 1178896.4075 | 2589236.3626 | 1178898.8363 | 2589245.4133 | 1178901.877 | 2589251.563 | 1178918.7078 | 2589254.3489 | 1178930.0197 | 2589257.1028 | 1178944.7667 | 2589264.6291 | 1178992.1217 | 2589268.7201 | 1179015.4596 | 2589271.0873 | 1179023.3483 | 2589274.2836 | 1179029.3011 | 2589278.7466 | 1179034.4068 | 2589283.4112 | 1179036.9775 | 2589291.3518 | 1179038.8085 | 2589291.3748 | 1179064.2993 | 2589289.6284 | 1179074.4854 | 2589286.0232 | 1179083.2853 | 2589279.4258 | 1179089.1446 | 2589274.206 | 1179092.1778 | 2589267.6483 | 1179094.6686
8 | 2589503.3814 | 1177998.0445 | 2589409.5508 | 1178175.0945
9 | 2589502.8228 | 1177986.6441 | 2589503.3814 | 1177998.0445
10 | 2589417.5161 | 1178331.8996 | 2589414.1918 | 1178325.5583 | 2589409.7927 | 1178305.0557 | 2589409.1052 | 1178266.5262 | 2589420.8704 | 1178223.0053 | 2589434.5407 | 1178198.1239 | 2589432.6302 | 1178176.3829 | 2589409.5508 | 1178175.0945
11 | 2589502.8228 | 1177986.6441 | 2589502.6983 | 1177984.1041
12 | 2589190.1948 | 1178834.5983 | 2589166.8304 | 1178799.6896 | 2589161.3003 | 1178792.6274
13 | 2589161.3003 | 1178792.6274 | 2589157.4423 | 1178787.7006 | 2589152.3816 | 1178781.729 | 2589152.3816 | 1178781.729
14 | 2589148.3811 | 1178678.4725 | 2589119.7221 | 1178627.2208
15 | 2589148.3811 | 1178678.4725 | 2589156.592 | 1178677.457 | 2589167.809 | 1178674.2349 | 2589175.606 | 1178668.2399 | 2589181.449 | 1178656.9725
16 | 2589119.7221 | 1178627.2208 | 2589154.7569 | 1178601.177 | 2589177.1659 | 1178584.9835 | 2589199.5973 | 1178576.8608 | 2589210.7992 | 1178569.3811 | 2589217.0064 | 1178554.4623 | 2589223.8231 | 1178530.2153 | 2589234.3872 | 1178512.1759 | 2589249.3041 | 1178488.7592 | 2589255.4951 | 1178482.8937
17 | 2589119.7221 | 1178627.2208 | 2589080.392 | 1178560.6589 | 2589055.8528 | 1178527.6204 | 2589048.6944 | 1178519.5035
18 | 2589152.3816 | 1178781.729 | 2589147.4375 | 1178776.8911 | 2589142.2572 | 1178772.3649 | 2589136.0386 | 1178768.2296 | 2589130.0011 | 1178765.2838
19 | 2589417.0651 | 1178373.1219 | 2589389.9468 | 1178379.9292 | 2589368.0149 | 1178385.9269 | 2589342.898 | 1178396.7107 | 2589329.3419 | 1178403.8942 | 2589317.401 | 1178417.0445 | 2589305.066 | 1178436.1542 | 2589294.3178 | 1178449.7027 | 2589271.6055 | 1178467.6305 | 2589255.4951 | 1178482.8937
20 | 2588992.2371 | 1178467.0846 | 2589026.8212 | 1178494.7015 | 2589048.6944 | 1178519.5035
21 | 2589053.9327 | 1178463.9804 | 2589064.3087 | 1178468.5414 | 2589070.958 | 1178474.0098 | 2589077.4541 | 1178483.436 | 2589081.9789 | 1178492.0072
22 | 2589104.2647 | 1178521.8954 | 2589099.6385 | 1178511.3763 | 2589093.273 | 1178506.4854 | 2589086.5008 | 1178500.5726 | 2589081.9789 | 1178492.0072
23 | 2589102.6974 | 1178383.6277 | 2589092.1256 | 1178389.0054 | 2589079.9523 | 1178400.1334 | 2589074.65 | 1178408.4696 | 2589069.832 | 1178418.3946 | 2589068.2976 | 1178427.3575 | 2589067.2919 | 1178445.5131 | 2589065.22 | 1178453.0652 | 2589060.2945 | 1178458.5437 | 2589053.9327 | 1178463.9804
24 | 2588992.2371 | 1178467.0846 | 2588989.5055 | 1178464.8885 | 2588995.7471 | 1178460.597 | 2589017.0597 | 1178462.9255 | 2589043.3972 | 1178464.0776 | 2589053.9327 | 1178463.9804
25 | 2588992.2371 | 1178467.0846 | 2588954.1688 | 1178484.7864 | 2588949.6951 | 1178486.1011
26 | 2588898.4774 | 1178348.0647 | 2588902.0366 | 1178367.9237 | 2588913.8061 | 1178394.4153 | 2588945.8638 | 1178431.1744 | 2588989.5055 | 1178464.8885 | 2588992.2371 | 1178467.0846
27 | 2588943.849 | 1178378.896 | 2588938.6564 | 1178372.1466 | 2588926.2751 | 1178365.7997 | 2588898.4774 | 1178348.0647
28 | 2588866.334 | 1178478.2688 | 2588872.8785 | 1178484.771 | 2588880.7684 | 1178487.6689 | 2588941.1878 | 1178488.6013 | 2588949.6951 | 1178486.1011
29 | 2588866.334 | 1178478.2688 | 2588863.8564 | 1178509.734 | 2588861.4548 | 1178520.5884 | 2588858.3656 | 1178547.7192 | 2588858.4756 | 1178577.9122 | 2588859.0991 | 1178588.5831 | 2588867.3368 | 1178626.298 | 2588865.8096 | 1178634.8942
30 | 2588865.8096 | 1178634.8942 | 2588846.2671 | 1178651.3614 | 2588838.5633 | 1178658.0125 | 2588829.1314 | 1178663.8443 | 2588819.5357 | 1178667.8866 | 2588813.4733 | 1178669.7878 | 2588808.5474 | 1178670.742 | 2588801.1898 | 1178670.5224
31 | 2588865.8096 | 1178634.8942 | 2588873.8508 | 1178637.058 | 2588879.5391 | 1178639.3263 | 2588899.6395 | 1178647.493 | 2588928.0322 | 1178661.3917 | 2588938.7247 | 1178667.8417 | 2588964.6106 | 1178685.5138 | 2588985.7589 | 1178698.6036 | 2588998.2625 | 1178705.3617 | 2588998.2625 | 1178705.3617
32 | 2589395.7681 | 1177895.1607 | 2589253.6802 | 1178145.2095
33 | 2589395.7681 | 1177895.1607 | 2589403.036 | 1177900.3282 | 2589413.1694 | 1177905.5684
34 | 2589413.1694 | 1177905.5684 | 2589437.3187 | 1177912.3178 | 2589454.9731 | 1177914.6544
35 | 2589417.0651 | 1178373.1219 | 2589422.3257 | 1178341.074 | 2589417.5161 | 1178331.8996
36 | 2589417.0651 | 1178373.1219 | 2589435.4055 | 1178366.7194 | 2589453.7382 | 1178355.9481 | 2589456.6907 | 1178353.4714
37 | 2589469.4487 | 1178339.9343 | 2589466.0894 | 1178345.5876 | 2589456.6907 | 1178353.4714
38 | 2589469.4487 | 1178339.9343 | 2589473.9737 | 1178336.7247 | 2589480.368 | 1178332.0999 | 2589503.744 | 1178329.3516
39 | 2588801.1898 | 1178670.5224 | 2588798.4159 | 1178682.3781 | 2588798.2768 | 1178685.5911 | 2588799.9516 | 1178694.5926
40 | 2588801.1898 | 1178670.5224 | 2588790.4416 | 1178666.9964 | 2588782.8822 | 1178665.1208 | 2588775.163 | 1178664.0984
41 | 2589007.4593 | 1178709.2248 | 2588998.2625 | 1178705.3617
42 | 2588799.9516 | 1178694.5926 | 2588804.6359 | 1178695.1952 | 2588810.5518 | 1178696.6293 | 2588818.4648 | 1178699.6826 | 2588819.2886 | 1178699.8404
43 | 2588799.9516 | 1178694.5926 | 2588804.6442 | 1178719.9078 | 2588805.4001 | 1178727.7771 | 2588805.3738 | 1178735.4029
44 | 2589007.4593 | 1178709.2248 | 2589011.0155 | 1178710.7186 | 2589052.4616 | 1178727.4508 | 2589123.7952 | 1178762.2559
45 | 2589123.7952 | 1178762.2559 | 2589130.0011 | 1178765.2838
46 | 2588802.2178 | 1178766.1693 | 2588805.3457 | 1178743.5408 | 2588805.3738 | 1178735.4029
47 | 2589466.7746 | 1177917.2442 | 2589458.4442 | 1177915.4161
48 | 2589477.3519 | 1177927.0322 | 2589474.9233 | 1177919.0324 | 2589466.7746 | 1177917.2442
49 | 2589454.9731 | 1177914.6544 | 2589458.4442 | 1177915.4161
50 | 2589496.1121 | 1177915.2264 | 2589485.6992 | 1177924.7162 | 2589477.3519 | 1177927.0322
51 | 2589477.3519 | 1177927.0322 | 2589477.6262 | 1177933.0843
52 | 2589449.5408 | 1177884.6487 | 2589454.9731 | 1177914.6544
53 | 2589496.1121 | 1177915.2264 | 2589499.8205 | 1177925.3694 | 2589500.023 | 1177929.5028
54 | 2589478.5764 | 1177954.0549 | 2589477.6262 | 1177933.0843
55 | 2589449.5408 | 1177884.6487 | 2589446.5739 | 1177873.5257
56 | 2589449.5408 | 1177884.6487 | 2589457.3255 | 1177883.9345 | 2589466.2121 | 1177879.8167 | 2589475.3231 | 1177868.5949
57 | 2589500.023 | 1177929.5028 | 2589502.3069 | 1177976.1149
58 | 2589441.8906 | 1177858.2163 | 2589444.9025 | 1177867.2592 | 2589446.5739 | 1177873.5257
59 | 2589477.7611 | 1177855.9508 | 2589477.7611 | 1177855.9508 | 2589475.3231 | 1177868.5949 | 2589475.3231 | 1177868.5949
60 | 2589502.3069 | 1177976.1149 | 2589502.6983 | 1177984.1041
61 | 2589477.7611 | 1177855.9508 | 2589476.3608 | 1177829.7899
62 | 2589474.4194 | 1177802.9741 | 2589475.6828 | 1177817.1236 | 2589476.3608 | 1177829.7899
63 | 2588819.3114 | 1178788.4263 | 2588808.8454 | 1178780.4753 | 2588803.7054 | 1178773.1367 | 2588802.2178 | 1178766.1693

## bus_geodata
| x | y | coords
0 | 2589427.6897 | 1177815.5805
1 | 2589432.8512 | 1177831.077
2 | 2589400.6308 | 1178881.2882
3 | 2589388.1273 | 1178854.7302
4 | 2589399.6427 | 1178903.2677
5 | 2589453.6058 | 1178808.2173
6 | 2589267.6483 | 1179094.6686
7 | 2589503.3814 | 1177998.0445
8 | 2589409.5508 | 1178175.0945
9 | 2589502.8228 | 1177986.6441
10 | 2589190.1948 | 1178834.5983
11 | 2589161.3003 | 1178792.6274
12 | 2589148.3811 | 1178678.4725
13 | 2589119.7221 | 1178627.2208
14 | 2589181.449 | 1178656.9725
15 | 2589115.9113 | 1179070.6434
16 | 2589152.3816 | 1178781.729
17 | 2589255.4951 | 1178482.8937
18 | 2589048.6944 | 1178519.5035
19 | 2589081.9789 | 1178492.0072
20 | 2589053.9327 | 1178463.9804
21 | 2589104.2647 | 1178521.8954
22 | 2589102.6974 | 1178383.6277
23 | 2588992.2371 | 1178467.0846
24 | 2588898.4774 | 1178348.0647
25 | 2588943.849 | 1178378.896
26 | 2588949.6951 | 1178486.1011
27 | 2588866.334 | 1178478.2688
28 | 2588865.8096 | 1178634.8942
29 | 2589395.7681 | 1177895.1607
30 | 2589253.6802 | 1178145.2095
31 | 2589413.1694 | 1177905.5684
32 | 2589417.0651 | 1178373.1219
33 | 2589417.5161 | 1178331.8996
34 | 2589456.6907 | 1178353.4714
35 | 2589469.4487 | 1178339.9343
36 | 2589503.744 | 1178329.3516
37 | 2588801.1898 | 1178670.5224
38 | 2588998.2625 | 1178705.3617
39 | 2588799.9516 | 1178694.5926
40 | 2588775.163 | 1178664.0984
41 | 2589007.4593 | 1178709.2248
42 | 2589123.7952 | 1178762.2559
43 | 2589130.0011 | 1178765.2838
44 | 2588819.2886 | 1178699.8404
45 | 2588805.3738 | 1178735.4029
46 | 2589466.7746 | 1177917.2442
47 | 2589458.4442 | 1177915.4161
48 | 2589477.3519 | 1177927.0322
49 | 2589454.9731 | 1177914.6544
50 | 2589496.1121 | 1177915.2264
51 | 2589477.6262 | 1177933.0843
52 | 2589449.5408 | 1177884.6487
53 | 2589500.023 | 1177929.5028
54 | 2589478.5764 | 1177954.0549
55 | 2589446.5739 | 1177873.5257
56 | 2589475.3231 | 1177868.5949
57 | 2589502.3069 | 1177976.1149
58 | 2589477.7611 | 1177855.9508
59 | 2589476.3608 | 1177829.7899
60 | 2589474.4194 | 1177802.9741
61 | 2589441.8906 | 1177858.2163
62 | 2589502.6983 | 1177984.1041
63 | 2588802.2178 | 1178766.1693
64 | 2588819.3114 | 1178788.4263
65 | 2589181.449 | 1178656.9725

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98455 | -0.10956 | 7.6303e-05 | 1.9123e-05
1 | 0.98455 | -0.10955 | 0.00017892 | 4.4843e-05
2 | 0.97023 | -0.21123 | 0.00079799 | 0.00019999
3 | 0.97039 | -0.21012 | 0 | 0
4 | 0.97015 | -0.21186 | 0.0027117 | 0.00067961
5 | 0.97001 | -0.21283 | 0.0031581 | 0.0007915
6 | 0.9732 | -0.1898 | 0 | 0
7 | 0.98542 | -0.10333 | 8.0911e-05 | 2.0278e-05
8 | 0.98671 | -0.093961 | 0.0027447 | 0.0006879
9 | 0.98534 | -0.10385 | 8.1486e-05 | 2.0422e-05
10 | 0.97727 | -0.16043 | 0 | 0
11 | 0.97795 | -0.15557 | 0.0042597 | 0.0010676
12 | 0.99858 | -0.0098966 | 0 | 0
13 | 0.99661 | -0.023616 | 0 | 0
14 | 1 | 0 | -0.047779 | -0.011821
15 | 0.97211 | -0.19771 | 0.0023508 | 0.00058917
16 | 0.97822 | -0.15361 | 0.0024319 | 0.00060949
17 | 0.99287 | -0.050047 | 0.00016729 | 4.1927e-05
18 | 0.99345 | -0.045734 | 0.00040727 | 0.00010207
19 | 0.99124 | -0.061276 | 0.00059316 | 0.00014866
20 | 0.99135 | -0.060502 | 0 | 0
21 | 0.99117 | -0.061763 | 0.0012539 | 0.00031425
22 | 0.99128 | -0.060975 | 0.00046008 | 0.00011531
23 | 0.99158 | -0.058862 | 0 | 0
24 | 0.9912 | -0.061581 | 0 | 0
25 | 0.99106 | -0.062535 | 0.0016969 | 0.00042527
26 | 0.99059 | -0.065842 | 0.0014383 | 0.00036048
27 | 0.98883 | -0.078243 | 0 | 0
28 | 0.98562 | -0.10091 | 0 | 0
29 | 0.9844 | -0.11062 | 0.00019395 | 4.8607e-05
30 | 0.98348 | -0.11723 | 0.0022147 | 0.00055506
31 | 0.98448 | -0.11011 | 0 | 0
32 | 0.98927 | -0.075663 | 0 | 0
33 | 0.98865 | -0.080106 | 0.0028356 | 0.00071067
34 | 0.98912 | -0.076701 | 0.0011708 | 0.00029342
35 | 0.98909 | -0.076915 | 0 | 0
36 | 0.98903 | -0.077333 | 0.0011062 | 0.00027723
37 | 0.98511 | -0.10452 | 0 | 0
38 | 0.98307 | -0.119 | 0.0013386 | 0.00033548
39 | 0.98497 | -0.10554 | 0 | 0
40 | 0.98509 | -0.10467 | 0.00056062 | 0.0001405
41 | 0.98275 | -0.12127 | 0.0020827 | 0.00052198
42 | 0.97906 | -0.14764 | 0.00098851 | 0.00024774
43 | 0.97887 | -0.149 | 0.0030626 | 0.00076757
44 | 0.98494 | -0.10576 | 0.0010361 | 0.00025966
45 | 0.98479 | -0.10683 | 0.00044746 | 0.00011214
46 | 0.98468 | -0.1086 | 0.00039234 | 9.8329e-05
47 | 0.98464 | -0.10891 | 9.3869e-05 | 2.3526e-05
48 | 0.98478 | -0.10793 | 0 | 0
49 | 0.98462 | -0.10904 | 0 | 0
50 | 0.98491 | -0.10697 | 0 | 0
51 | 0.98478 | -0.10794 | 8.7375e-05 | 2.1898e-05
52 | 0.98458 | -0.10935 | 0 | 0
53 | 0.985 | -0.10634 | 0.00010798 | 2.7063e-05
54 | 0.98477 | -0.10795 | 7.6894e-05 | 1.9271e-05
55 | 0.98457 | -0.10941 | 0.00014908 | 3.7362e-05
56 | 0.98456 | -0.10951 | 0.0001232 | 3.0876e-05
57 | 0.98528 | -0.10432 | 8.5785e-05 | 2.15e-05
58 | 0.98455 | -0.10956 | 0.00012612 | 3.1609e-05
59 | 0.98454 | -0.10962 | 9.7688e-05 | 2.4483e-05
60 | 0.98454 | -0.10966 | 0.00013037 | 3.2675e-05
61 | 0.98456 | -0.10947 | 9.84e-05 | 2.4661e-05
62 | 0.98533 | -0.10397 | 8.1383e-05 | 2.0396e-05
63 | 0.98467 | -0.10765 | 0 | 0
64 | 0.98457 | -0.10842 | 0.0025662 | 0.00064315
65 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -7.6303e-05 | -1.9123e-05 | 7.6304e-05 | 1.8916e-05 | 1.3546e-10 | -2.0766e-07 | 0.00011532 | 0.00011525 | 0.00011532 | 0.98455 | -0.10956 | 0.98455 | -0.10955 | 0.042712
1 | -0.00025523 | -6.3758e-05 | 0.00025523 | 6.3396e-05 | 2.654e-09 | -3.6276e-07 | 0.00038567 | 0.00038554 | 0.00038567 | 0.98455 | -0.10955 | 0.98456 | -0.10947 | 0.14284
2 | -0.0035099 | -0.00087943 | 0.0035104 | 0.00087926 | 5.3989e-07 | -1.6118e-07 | 0.0053829 | 0.0053828 | 0.0053829 | 0.97023 | -0.21123 | 0.97039 | -0.21012 | 1.9937
3 | 0.0027119 | 0.00067943 | -0.0027117 | -0.00067961 | 2.3749e-07 | -1.8035e-07 | 0.0041591 | 0.0041592 | 0.0041592 | 0.97023 | -0.21123 | 0.97015 | -0.21186 | 1.5404
4 | 0.0031593 | 0.00079096 | -0.0031581 | -0.0007915 | 1.1828e-06 | -5.425e-07 | 0.0048443 | 0.0048446 | 0.0048446 | 0.97039 | -0.21012 | 0.97001 | -0.21283 | 1.7943
5 | -0.0066698 | -0.0016702 | 0.0066885 | 0.0016739 | 1.8743e-05 | 3.6503e-06 | 0.010227 | 0.010226 | 0.010227 | 0.97039 | -0.21012 | 0.9732 | -0.1898 | 3.7878
6 | 0.0023534 | 0.00058622 | -0.0023508 | -0.00058917 | 2.5589e-06 | -2.9481e-06 | 0.003597 | 0.0035984 | 0.0035984 | 0.9732 | -0.1898 | 0.97211 | -0.19771 | 1.3327
7 | -0.0090419 | -0.0022601 | 0.0090786 | 0.0022704 | 3.6669e-05 | 1.0265e-05 | 0.013823 | 0.013821 | 0.013823 | 0.9732 | -0.1898 | 0.97727 | -0.16043 | 5.1196
8 | -0.0044825 | -0.0011151 | 0.0044883 | 0.0011148 | 5.7229e-06 | -3.5492e-07 | 0.0067658 | 0.0067649 | 0.0067658 | 0.98542 | -0.10333 | 0.98671 | -0.093961 | 2.5059
9 | 0.0044016 | 0.0010948 | -0.0044013 | -0.0010949 | 3.1437e-07 | -2.4486e-08 | 0.0066437 | 0.0066437 | 0.0066437 | 0.98542 | -0.10333 | 0.98534 | -0.10385 | 2.4606
10 | -0.007233 | -0.0018027 | 0.0072467 | 0.0018056 | 1.3731e-05 | 2.9123e-06 | 0.010904 | 0.010903 | 0.010904 | 0.98671 | -0.093961 | 0.98865 | -0.080106 | 4.0386
11 | 0.0043198 | 0.0010745 | -0.0043197 | -0.0010745 | 6.7471e-08 | -6.4408e-09 | 0.0065207 | 0.0065207 | 0.0065207 | 0.98534 | -0.10385 | 0.98533 | -0.10397 | 2.4151
12 | -0.0090786 | -0.0022704 | 0.0090846 | 0.0022721 | 6.0764e-06 | 1.6979e-06 | 0.013821 | 0.013821 | 0.013821 | 0.97727 | -0.16043 | 0.97795 | -0.15557 | 5.119
13 | -0.013344 | -0.0033396 | 0.013348 | 0.0033409 | 3.6229e-06 | 1.2166e-06 | 0.020303 | 0.020303 | 0.020303 | 0.97795 | -0.15557 | 0.97822 | -0.15361 | 7.5195
14 | 0.046914 | 0.011797 | -0.046825 | -0.011764 | 8.9528e-05 | 3.2901e-05 | 0.069922 | 0.069923 | 0.069923 | 0.99858 | -0.0098966 | 0.99661 | -0.023616 | 12.9487
15 | -0.046914 | -0.011797 | 0.046979 | 0.01182 | 6.4786e-05 | 2.3805e-05 | 0.069922 | 0.069922 | 0.069922 | 0.99858 | -0.0098966 | 1 | 0 | 12.9486
16 | 0.012623 | 0.0031587 | -0.012577 | -0.0031437 | 4.5912e-05 | 1.4969e-05 | 0.018845 | 0.018846 | 0.018846 | 0.99661 | -0.023616 | 0.99287 | -0.050047 | 6.9799
17 | 0.034202 | 0.0086051 | -0.034097 | -0.0085679 | 0.00010524 | 3.712e-05 | 0.051078 | 0.051079 | 0.051079 | 0.99661 | -0.023616 | 0.99345 | -0.045734 | 9.4591
18 | -0.01578 | -0.0039504 | 0.01579 | 0.0039539 | 1.0059e-05 | 3.5173e-06 | 0.024002 | 0.024002 | 0.024002 | 0.97822 | -0.15361 | 0.97887 | -0.149 | 8.8896
19 | 0.012409 | 0.0031018 | -0.012366 | -0.0030876 | 4.3652e-05 | 1.4182e-05 | 0.018595 | 0.018596 | 0.018596 | 0.99287 | -0.050047 | 0.98927 | -0.075663 | 6.8874
20 | 0.03369 | 0.0084659 | -0.033628 | -0.0084442 | 6.1453e-05 | 2.1637e-05 | 0.050469 | 0.05047 | 0.05047 | 0.99345 | -0.045734 | 0.99158 | -0.058862 | 9.3463
21 | -0.0018471 | -0.00046245 | 0.0018473 | 0.00046199 | 1.9706e-07 | -4.5385e-07 | 0.0027726 | 0.0027724 | 0.0027726 | 0.99124 | -0.061276 | 0.99135 | -0.060502 | 1.0269
22 | 0.0012539 | 0.00031379 | -0.0012539 | -0.00031425 | 8.4443e-08 | -4.5984e-07 | 0.0018822 | 0.0018824 | 0.0018824 | 0.99124 | -0.061276 | 0.99117 | -0.061763 | 0.69718
23 | 0.00046011 | 0.00011403 | -0.00046008 | -0.00011531 | 2.9753e-08 | -1.2782e-06 | 0.00069018 | 0.00069063 | 0.00069063 | 0.99135 | -0.060502 | 0.99128 | -0.060975 | 0.25579
24 | -0.0023074 | -0.00057602 | 0.0023079 | 0.00057533 | 5.1931e-07 | -6.9549e-07 | 0.0034626 | 0.0034623 | 0.0034626 | 0.99135 | -0.060502 | 0.99158 | -0.058862 | 1.2825
25 | 0.029622 | 0.007446 | -0.029594 | -0.0074362 | 2.8769e-05 | 9.8628e-06 | 0.044461 | 0.044461 | 0.044461 | 0.99158 | -0.058862 | 0.99059 | -0.065842 | 8.2336
26 | 0.0016977 | 0.00042287 | -0.0016971 | -0.00042465 | 6.3393e-07 | -1.7753e-06 | 0.0025468 | 0.0025475 | 0.0025475 | 0.99158 | -0.058862 | 0.9912 | -0.061581 | 0.94351
27 | 0.0016971 | 0.00042465 | -0.0016969 | -0.00042527 | 2.2395e-07 | -6.2652e-07 | 0.0025475 | 0.0025477 | 0.0025477 | 0.9912 | -0.061581 | 0.99106 | -0.062535 | 0.9436
28 | 0.028155 | 0.0070757 | -0.028107 | -0.0070593 | 4.8528e-05 | 1.6431e-05 | 0.042301 | 0.042301 | 0.042301 | 0.99059 | -0.065842 | 0.98883 | -0.078243 | 7.8336
29 | 0.028107 | 0.0070593 | -0.028018 | -0.0070293 | 8.8344e-05 | 2.9932e-05 | 0.042301 | 0.042303 | 0.042303 | 0.98883 | -0.078243 | 0.98562 | -0.10091 | 7.8339
30 | 0.0046143 | 0.0011538 | -0.004612 | -0.0011539 | 2.2952e-06 | -8.2883e-08 | 0.0069655 | 0.0069658 | 0.0069658 | 0.98562 | -0.10091 | 0.98511 | -0.10452 | 2.5799
31 | 0.023404 | 0.0058755 | -0.023345 | -0.0058568 | 5.8705e-05 | 1.8748e-05 | 0.035337 | 0.035339 | 0.035339 | 0.98562 | -0.10091 | 0.98307 | -0.119 | 6.5442
32 | 0.0022167 | 0.00055218 | -0.0022147 | -0.00055506 | 2.0143e-06 | -2.8782e-06 | 0.0033496 | 0.0033509 | 0.0033509 | 0.9844 | -0.11062 | 0.98348 | -0.11723 | 1.2411
33 | -0.0024107 | -0.00060079 | 0.0024108 | 0.00060059 | 1.6795e-07 | -1.933e-07 | 0.0036427 | 0.0036426 | 0.0036427 | 0.9844 | -0.11062 | 0.98448 | -0.11011 | 1.3492
34 | -0.0024108 | -0.00060059 | 0.0024112 | 0.00060018 | 3.5407e-07 | -4.0767e-07 | 0.0036426 | 0.0036424 | 0.0036426 | 0.98448 | -0.11011 | 0.98462 | -0.10904 | 1.3491
35 | 0.010088 | 0.0025181 | -0.010082 | -0.0025163 | 6.1521e-06 | 1.8166e-06 | 0.015171 | 0.015171 | 0.015171 | 0.98927 | -0.075663 | 0.98865 | -0.080106 | 5.619
36 | 0.0022773 | 0.00056952 | -0.002277 | -0.00056997 | 3.2607e-07 | -4.4639e-07 | 0.003425 | 0.0034252 | 0.0034252 | 0.98927 | -0.075663 | 0.98912 | -0.076701 | 1.2686
37 | 0.0011062 | 0.00027655 | -0.0011062 | -0.00027678 | 3.2558e-08 | -2.2934e-07 | 0.001664 | 0.0016641 | 0.0016641 | 0.98912 | -0.076701 | 0.98909 | -0.076915 | 0.61632
38 | 0.0011062 | 0.00027678 | -0.0011062 | -0.00027723 | 6.3898e-08 | -4.4997e-07 | 0.0016641 | 0.0016642 | 0.0016642 | 0.98909 | -0.076915 | 0.98903 | -0.077333 | 0.61638
39 | 0.0040514 | 0.0010138 | -0.0040508 | -0.0010138 | 5.7364e-07 | -9.1898e-08 | 0.0061191 | 0.0061192 | 0.0061192 | 0.98511 | -0.10452 | 0.98497 | -0.10554 | 2.2664
40 | 0.00056063 | 0.00014017 | -0.00056062 | -0.0001405 | 1.203e-08 | -3.3768e-07 | 0.00084671 | 0.00084683 | 0.00084683 | 0.98511 | -0.10452 | 0.98509 | -0.10467 | 0.31364
41 | 0.022007 | 0.0055213 | -0.022 | -0.0055187 | 6.9075e-06 | 2.5303e-06 | 0.033313 | 0.033313 | 0.033313 | 0.98307 | -0.119 | 0.98275 | -0.12127 | 12.338
42 | 0.0010361 | 0.00025942 | -0.0010361 | -0.00025966 | 3.0774e-08 | -2.4438e-07 | 0.0015652 | 0.0015653 | 0.0015653 | 0.98497 | -0.10554 | 0.98494 | -0.10576 | 0.57973
43 | 0.0030147 | 0.00075442 | -0.0030142 | -0.00075474 | 5.3421e-07 | -3.1982e-07 | 0.004554 | 0.0045542 | 0.0045542 | 0.98497 | -0.10554 | 0.98479 | -0.10683 | 1.6867
44 | 0.019917 | 0.0049968 | -0.019845 | -0.0049705 | 7.2608e-05 | 2.6311e-05 | 0.030159 | 0.03016 | 0.03016 | 0.98275 | -0.12127 | 0.97906 | -0.14764 | 11.1703
45 | 0.018856 | 0.0047227 | -0.018853 | -0.0047214 | 3.5386e-06 | 1.2742e-06 | 0.028657 | 0.028657 | 0.028657 | 0.97906 | -0.14764 | 0.97887 | -0.149 | 10.6138
46 | 0.0025668 | 0.0006426 | -0.0025665 | -0.00064288 | 2.9077e-07 | -2.8231e-07 | 0.0038781 | 0.0038783 | 0.0038783 | 0.98479 | -0.10683 | 0.98467 | -0.10765 | 1.4364
47 | 0.0034854 | 0.00086674 | -0.0034853 | -0.00086679 | 1.475e-07 | -5.1752e-08 | 0.0052646 | 0.0052646 | 0.0052646 | 0.98468 | -0.1086 | 0.98464 | -0.10891 | 1.9499
48 | -0.0038777 | -0.00096507 | 0.0038781 | 0.00096499 | 3.576e-07 | -7.4953e-08 | 0.0058575 | 0.0058574 | 0.0058575 | 0.98468 | -0.1086 | 0.98478 | -0.10793 | 2.1694
49 | 0.0033914 | 0.00084326 | -0.0033913 | -0.00084329 | 5.8194e-08 | -2.2818e-08 | 0.0051228 | 0.0051228 | 0.0051228 | 0.98464 | -0.10891 | 0.98462 | -0.10904 | 1.8973
50 | -0.0040424 | -0.0010058 | 0.0040429 | 0.0010057 | 5.2818e-07 | -8.5793e-08 | 0.0061055 | 0.0061054 | 0.0061055 | 0.98478 | -0.10793 | 0.98491 | -0.10697 | 2.2613
51 | 0.00016427 | 4.0826e-05 | -0.00016427 | -4.0903e-05 | 2.327e-10 | -7.6991e-08 | 0.00024809 | 0.00024812 | 0.00024812 | 0.98478 | -0.10793 | 0.98478 | -0.10794 | 0.091896
52 | 0.00098015 | 0.0002431 | -0.00098011 | -0.00024347 | 4.1709e-08 | -3.7184e-07 | 0.0014804 | 0.0014805 | 0.0014805 | 0.98462 | -0.10904 | 0.98458 | -0.10935 | 0.54833
53 | -0.0040429 | -0.0010057 | 0.0040433 | 0.0010057 | 3.4746e-07 | -5.6486e-08 | 0.0061054 | 0.0061053 | 0.0061054 | 0.98491 | -0.10697 | 0.985 | -0.10634 | 2.2613
54 | 7.6894e-05 | 1.9004e-05 | -7.6894e-05 | -1.9271e-05 | 1.7669e-10 | -2.6701e-07 | 0.00011609 | 0.00011619 | 0.00011619 | 0.98478 | -0.10794 | 0.98477 | -0.10795 | 0.043033
55 | 0.00050272 | 0.00012507 | -0.00050271 | -0.00012522 | 4.1433e-09 | -1.4481e-07 | 0.00075944 | 0.00075949 | 0.00075949 | 0.98458 | -0.10935 | 0.98457 | -0.10941 | 0.28129
56 | 0.0004774 | 0.0001184 | -0.00047739 | -0.00011881 | 1.0405e-08 | -4.038e-07 | 0.00072106 | 0.0007212 | 0.0007212 | 0.98458 | -0.10935 | 0.98456 | -0.10951 | 0.26711
57 | -0.0041512 | -0.0010327 | 0.0041524 | 0.0010326 | 1.1442e-06 | -1.541e-07 | 0.0062685 | 0.0062683 | 0.0062685 | 0.985 | -0.10634 | 0.98528 | -0.10432 | 2.3217
58 | 0.00035363 | 8.7854e-05 | -0.00035363 | -8.8057e-05 | 2.8523e-09 | -2.026e-07 | 0.00053418 | 0.00053425 | 0.00053425 | 0.98457 | -0.10941 | 0.98456 | -0.10947 | 0.19787
59 | 0.00035419 | 8.793e-05 | -0.00035419 | -8.8093e-05 | 2.3002e-09 | -1.6287e-07 | 0.00053501 | 0.00053506 | 0.00053506 | 0.98456 | -0.10951 | 0.98455 | -0.10956 | 0.19817
60 | -0.0042382 | -0.0010541 | 0.0042384 | 0.0010541 | 2.043e-07 | -2.33e-08 | 0.0063978 | 0.0063978 | 0.0063978 | 0.98528 | -0.10432 | 0.98533 | -0.10397 | 2.3696
61 | 0.00022806 | 5.6484e-05 | -0.00022806 | -5.6816e-05 | 1.9403e-09 | -3.3242e-07 | 0.00034445 | 0.00034457 | 0.00034457 | 0.98455 | -0.10956 | 0.98454 | -0.10962 | 0.12762
62 | 0.00013037 | 3.2333e-05 | -0.00013037 | -3.2675e-05 | 6.5109e-10 | -3.4171e-07 | 0.00019692 | 0.00019705 | 0.00019705 | 0.98454 | -0.10962 | 0.98454 | -0.10966 | 0.07298
63 | 0.0025665 | 0.00064288 | -0.0025662 | -0.00064315 | 2.7406e-07 | -2.6597e-07 | 0.0038783 | 0.0038784 | 0.0038784 | 0.98467 | -0.10765 | 0.98457 | -0.10842 | 1.4364

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.048757 | 0.012066

## res_load
| p_mw | q_mvar
0 | 7.6303e-05 | 1.9123e-05
1 | 0.00017892 | 4.4843e-05
2 | 0.00079799 | 0.00019999
3 | 0.0027117 | 0.00067961
4 | 0.0031581 | 0.0007915
5 | 8.0911e-05 | 2.0278e-05
6 | 0.0027447 | 0.0006879
7 | 8.1486e-05 | 2.0422e-05
8 | 0.0042597 | 0.0010676
9 | 0.00097778 | 0.00024505
10 | 0.0023508 | 0.00058917
11 | 0.0024319 | 0.00060949
12 | 0.00016729 | 4.1927e-05
13 | 0.00040727 | 0.00010207
14 | 0.00059316 | 0.00014866
15 | 0.0012539 | 0.00031425
16 | 0.00046008 | 0.00011531
17 | 0.0016969 | 0.00042527
18 | 0.0014383 | 0.00036048
19 | 0.00019395 | 4.8607e-05
20 | 0.0022147 | 0.00055506
21 | 0.0028356 | 0.00071067
22 | 0.0011708 | 0.00029342
23 | 0.0011062 | 0.00027723
24 | 0.0013386 | 0.00033548
25 | 0.00056062 | 0.0001405
26 | 0.0020827 | 0.00052198
27 | 0.00098851 | 0.00024774
28 | 0.0030626 | 0.00076757
29 | 0.0010361 | 0.00025966
30 | 0.00044746 | 0.00011214
31 | 0.00039234 | 9.8329e-05
32 | 9.3869e-05 | 2.3526e-05
33 | 8.7375e-05 | 2.1898e-05
34 | 0.00010798 | 2.7063e-05
35 | 7.6894e-05 | 1.9271e-05
36 | 0.00014908 | 3.7362e-05
37 | 0.0001232 | 3.0876e-05
38 | 8.5785e-05 | 2.15e-05
39 | 0.00012612 | 3.1609e-05
40 | 9.7688e-05 | 2.4483e-05
41 | 0.00013037 | 3.2675e-05
42 | 9.84e-05 | 2.4661e-05
43 | 8.1383e-05 | 2.0396e-05
44 | 0.0025662 | 0.00064315

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1