## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_297-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_297-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_297-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_297-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_297-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_297-20_0_3_node_91 | 0.4 | n |  | TRUE
6 | bus_LV_297-20_0_3_node_92 | 0.4 | n |  | TRUE
7 | bus_LV_297-20_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_297-20_0_3_node_93 | 0.4 | n |  | TRUE
9 | bus_LV_297-20_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_297-20_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_297-20_0_3_node_118 | 0.4 | n |  | TRUE
12 | bus_LV_297-20_0_3_node_108 | 0.4 | n |  | TRUE
13 | bus_LV_297-20_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_297-20_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_297-20_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_297-20_0_3_node_106 | 0.4 | n |  | TRUE
17 | bus_LV_297-20_0_3_node_113 | 0.4 | n |  | TRUE
18 | bus_LV_297-20_0_3_node_111 | 0.4 | n |  | TRUE
19 | bus_LV_297-20_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_297-20_0_3_node_107 | 0.4 | n |  | TRUE
21 | bus_LV_297-20_0_3_node_105 | 0.4 | n |  | TRUE
22 | bus_LV_297-20_0_3_node_117 | 0.4 | n |  | TRUE
23 | bus_LV_297-20_0_3_node_110 | 0.4 | n |  | TRUE
24 | bus_LV_297-20_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_297-20_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_297-20_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_297-20_0_3_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_297-20_0_3_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_297-20_0_3_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_297-20_0_3_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_297-20_0_3_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_297-20_0_3_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_297-20_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_297-20_0_3_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_297-20_0_3_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_297-20_0_3_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_297-20_0_3_node_83 | 0.4 | n |  | TRUE
38 | bus_LV_297-20_0_3_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_297-20_0_3_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_297-20_0_3_node_84 | 0.4 | n |  | TRUE
41 | bus_LV_297-20_0_3_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_297-20_0_3_node_90 | 0.4 | n |  | TRUE
43 | bus_LV_297-20_0_3_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_297-20_0_3_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_297-20_0_3_node_85 | 0.4 | n |  | TRUE
46 | bus_LV_297-20_0_3_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_297-20_0_3_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_297-20_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_297-20_0_3_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_297-20_0_3_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_297-20_0_3_node_80 | 0.4 | n |  | TRUE
52 | bus_LV_297-20_0_3_node_81 | 0.4 | n |  | TRUE
53 | bus_LV_297-20_0_3_node_82 | 0.4 | n |  | TRUE
54 | bus_LV_297-20_0_3_node_115 | 0.4 | n |  | TRUE
55 | bus_LV_297-20_0_3_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_297-20_0_3_node_114 | 0.4 | n |  | TRUE
57 | bus_LV_297-20_0_3_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_297-20_0_3_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_297-20_0_3_node_101 | 0.4 | n |  | TRUE
60 | bus_LV_297-20_0_3_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_297-20_0_3_node_73 | 0.4 | n |  | TRUE
62 | bus_LV_297-20_0_3_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_297-20_0_3_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_297-20_0_3_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_297-20_0_3_node_102 | 0.4 | n |  | TRUE
66 | bus_LV_297-20_0_3_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_297-20_0_3_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_297-20_0_3_node_37 | 0.4 | n |  | TRUE
69 | bus_LV_297-20_0_3_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_297-20_0_3_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_297-20_0_3_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_297-20_0_3_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_297-20_0_3_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_297-20_0_3_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_297-20_0_3_node_151 | 0.4 | n |  | TRUE
76 | bus_LV_297-20_0_3_node_152 | 0.4 | n |  | TRUE
77 | bus_LV_297-20_0_3_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_297-20_0_3_node_104 | 0.4 | n |  | TRUE
79 | bus_LV_297-20_0_3_node_43 | 0.4 | n |  | TRUE
80 | bus_LV_297-20_0_3_node_129 | 0.4 | n |  | TRUE
81 | bus_LV_297-20_0_3_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_297-20_0_3_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_297-20_0_3_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_297-20_0_3_node_130 | 0.4 | n |  | TRUE
85 | bus_LV_297-20_0_3_node_165 | 0.4 | n |  | TRUE
86 | bus_LV_297-20_0_3_node_124 | 0.4 | n |  | TRUE
87 | bus_LV_297-20_0_3_node_156 | 0.4 | n |  | TRUE
88 | bus_LV_297-20_0_3_node_157 | 0.4 | n |  | TRUE
89 | bus_LV_297-20_0_3_node_49 | 0.4 | n |  | TRUE
90 | bus_LV_297-20_0_3_node_103 | 0.4 | n |  | TRUE
91 | bus_LV_297-20_0_3_node_127 | 0.4 | n |  | TRUE
92 | bus_LV_297-20_0_3_node_169 | 0.4 | n |  | TRUE
93 | bus_LV_297-20_0_3_node_166 | 0.4 | n |  | TRUE
94 | bus_LV_297-20_0_3_node_131 | 0.4 | n |  | TRUE
95 | bus_LV_297-20_0_3_node_125 | 0.4 | n |  | TRUE
96 | bus_LV_297-20_0_3_node_48 | 0.4 | n |  | TRUE
97 | bus_LV_297-20_0_3_node_55 | 0.4 | n |  | TRUE
98 | bus_LV_297-20_0_3_node_57 | 0.4 | n |  | TRUE
99 | bus_LV_297-20_0_3_node_60 | 0.4 | n |  | TRUE
100 | bus_LV_297-20_0_3_node_61 | 0.4 | n |  | TRUE
101 | bus_LV_297-20_0_3_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_297-20_0_3_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_297-20_0_3_node_74 | 0.4 | n |  | TRUE
104 | bus_LV_297-20_0_3_node_112 | 0.4 | n |  | TRUE
105 | bus_LV_297-20_0_3_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_297-20_0_3_node_63 | 0.4 | n |  | TRUE
107 | bus_LV_297-20_0_3_node_64 | 0.4 | n |  | TRUE
108 | bus_LV_297-20_0_3_node_137 | 0.4 | n |  | TRUE
109 | bus_LV_297-20_0_3_node_135 | 0.4 | n |  | TRUE
110 | bus_LV_297-20_0_3_node_65 | 0.4 | n |  | TRUE
111 | bus_LV_297-20_0_3_node_66 | 0.4 | n |  | TRUE
112 | bus_LV_297-20_0_3_node_67 | 0.4 | n |  | TRUE
113 | bus_LV_297-20_0_3_node_68 | 0.4 | n |  | TRUE
114 | bus_LV_297-20_0_3_node_69 | 0.4 | n |  | TRUE
115 | bus_LV_297-20_0_3_node_70 | 0.4 | n |  | TRUE
116 | bus_LV_297-20_0_3_node_71 | 0.4 | n |  | TRUE
117 | bus_LV_297-20_0_3_node_72 | 0.4 | n |  | TRUE
118 | bus_LV_297-20_0_3_node_87 | 0.4 | n |  | TRUE
119 | bus_LV_297-20_0_3_node_89 | 0.4 | n |  | TRUE
120 | bus_LV_297-20_0_3_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_297-20_0_3_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_297-20_0_3_node_75 | 0.4 | n |  | TRUE
123 | bus_LV_297-20_0_3_node_77 | 0.4 | n |  | TRUE
124 | bus_LV_297-20_0_3_node_78 | 0.4 | n |  | TRUE
125 | bus_LV_297-20_0_3_node_79 | 0.4 | n |  | TRUE
126 | bus_LV_297-20_0_3_node_141 | 0.4 | n |  | TRUE
127 | bus_LV_297-20_0_3_node_142 | 0.4 | n |  | TRUE
128 | bus_LV_297-20_0_3_node_168 | 0.4 | n |  | TRUE
129 | bus_LV_297-20_0_3_node_121 | 0.4 | n |  | TRUE
130 | bus_LV_297-20_0_3_node_94 | 0.4 | n |  | TRUE
131 | bus_LV_297-20_0_3_node_98 | 0.4 | n |  | TRUE
132 | bus_LV_297-20_0_3_node_96 | 0.4 | n |  | TRUE
133 | bus_LV_297-20_0_3_node_95 | 0.4 | n |  | TRUE
134 | bus_LV_297-20_0_3_node_97 | 0.4 | n |  | TRUE
135 | bus_LV_297-20_0_3_node_99 | 0.4 | n |  | TRUE
136 | bus_LV_297-20_0_3_node_100 | 0.4 | n |  | TRUE
137 | bus_LV_297-20_0_3_node_109 | 0.4 | n |  | TRUE
138 | bus_LV_297-20_0_3_node_167 | 0.4 | n |  | TRUE
139 | bus_LV_297-20_0_3_node_122 | 0.4 | n |  | TRUE
140 | bus_LV_297-20_0_3_node_123 | 0.4 | n |  | TRUE
141 | bus_LV_297-20_0_3_node_126 | 0.4 | n |  | TRUE
142 | bus_LV_297-20_0_3_node_128 | 0.4 | n |  | TRUE
143 | bus_LV_297-20_0_3_node_148 | 0.4 | n |  | TRUE
144 | bus_LV_297-20_0_3_node_164 | 0.4 | n |  | TRUE
145 | bus_LV_297-20_0_3_node_145 | 0.4 | n |  | TRUE
146 | bus_LV_297-20_0_3_node_132 | 0.4 | n |  | TRUE
147 | bus_LV_297-20_0_3_node_133 | 0.4 | n |  | TRUE
148 | bus_LV_297-20_0_3_node_143 | 0.4 | n |  | TRUE
149 | bus_LV_297-20_0_3_node_139 | 0.4 | n |  | TRUE
150 | bus_LV_297-20_0_3_node_134 | 0.4 | n |  | TRUE
151 | bus_LV_297-20_0_3_node_136 | 0.4 | n |  | TRUE
152 | bus_LV_297-20_0_3_node_138 | 0.4 | n |  | TRUE
153 | bus_LV_297-20_0_3_node_140 | 0.4 | n |  | TRUE
154 | bus_LV_297-20_0_3_node_144 | 0.4 | n |  | TRUE
155 | bus_LV_297-20_0_3_node_146 | 0.4 | n |  | TRUE
156 | bus_LV_297-20_0_3_node_147 | 0.4 | n |  | TRUE
157 | bus_LV_297-20_0_3_node_149 | 0.4 | n |  | TRUE
158 | bus_LV_297-20_0_3_node_150 | 0.4 | n |  | TRUE
159 | bus_LV_297-20_0_3_node_154 | 0.4 | n |  | TRUE
160 | bus_LV_297-20_0_3_node_158 | 0.4 | n |  | TRUE
161 | bus_LV_297-20_0_3_node_153 | 0.4 | n |  | TRUE
162 | bus_LV_297-20_0_3_node_155 | 0.4 | n |  | TRUE
163 | bus_LV_297-20_0_3_node_159 | 0.4 | n |  | TRUE
164 | bus_LV_297-20_0_3_node_160 | 0.4 | n |  | TRUE
165 | bus_LV_297-20_0_3_node_161 | 0.4 | n |  | TRUE
166 | bus_LV_297-20_0_3_node_162 | 0.4 | n |  | TRUE
167 | bus_LV_297-20_0_3_node_163 | 0.4 | n |  | TRUE
168 | bus_MV_7_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_297-20_0_3_load_0 | 0 | 0.00020869 | 5.2304e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_297-20_0_3_load_1 | 1 | 0.00047477 | 0.00011899 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_297-20_0_3_load_4 | 4 | 0.0002263 | 5.6715e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_297-20_0_3_load_91 | 5 | 0.0017733 | 0.00044444 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_297-20_0_3_load_92 | 6 | 0.00038099 | 9.5485e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_297-20_0_3_load_93 | 8 | 0.0011576 | 0.00029011 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_297-20_0_3_load_12 | 9 | 0.00056794 | 0.00014234 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_297-20_0_3_load_11 | 10 | 0.00027297 | 6.8412e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_297-20_0_3_load_108 | 12 | 0.00014129 | 3.5411e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_297-20_0_3_load_7 | 14 | 0.00078924 | 0.0001978 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_297-20_0_3_load_106 | 16 | 0.00031037 | 7.7785e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_297-20_0_3_load_113 | 17 | 0.00010389 | 2.6037e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_297-20_0_3_load_107 | 20 | 0.00028745 | 7.2041e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_297-20_0_3_load_105 | 21 | 0.00032388 | 8.1171e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_297-20_0_3_load_117 | 22 | 0.00021313 | 5.3415e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_297-20_0_3_load_13 | 24 | 0.00026032 | 6.5242e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_297-20_0_3_load_14 | 25 | 0.0035001 | 0.0008772 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_297-20_0_3_load_15 | 26 | 0.00036737 | 9.2072e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_297-20_0_3_load_16 | 27 | 0.00060333 | 0.00015121 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_297-20_0_3_load_17 | 28 | 0.0010522 | 0.00026371 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_297-20_0_3_load_29 | 34 | 0.0017542 | 0.00043965 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_297-20_0_3_load_20 | 35 | 0.0018976 | 0.00047558 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_297-20_0_3_load_83 | 37 | 0.0014399 | 0.00036087 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_297-20_0_3_load_84 | 40 | 0.00096122 | 0.00024091 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_297-20_0_3_load_90 | 42 | 0.00208 | 0.00052129 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_297-20_0_3_load_85 | 45 | 0.0015422 | 0.00038651 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_297-20_0_3_load_32 | 47 | 0.0014917 | 0.00037385 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_297-20_0_3_load_31 | 48 | 0.0026283 | 0.00065871 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_297-20_0_3_load_80 | 51 | 0.003006 | 0.00075336 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_297-20_0_3_load_82 | 53 | 0.0014055 | 0.00035225 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_297-20_0_3_load_115 | 54 | 0.0025943 | 0.00065019 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_297-20_0_3_load_52 | 55 | 0.0014917 | 0.00037385 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_297-20_0_3_load_114 | 56 | 0.00058542 | 0.00014672 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_297-20_0_3_load_50 | 57 | 0.0016404 | 0.00041112 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_297-20_0_3_load_101 | 59 | 0.0019228 | 0.0004819 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_297-20_0_3_load_76 | 60 | 0.0014352 | 0.00035969 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_297-20_0_3_load_73 | 61 | 0.0059937 | 0.0015022 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_297-20_0_3_load_54 | 62 | 0.0028481 | 0.00071381 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_297-20_0_3_load_53 | 63 | 0.0028283 | 0.00070885 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_297-20_0_3_load_102 | 65 | 0.00027318 | 6.8464e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_297-20_0_3_load_36 | 67 | 0.0017609 | 0.00044132 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_297-20_0_3_load_37 | 68 | 0.002465 | 0.00061778 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_297-20_0_3_load_38 | 69 | 0.00064295 | 0.00016114 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_297-20_0_3_load_40 | 71 | 0.00099712 | 0.0002499 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_297-20_0_3_load_47 | 74 | 0.001658 | 0.00041553 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_297-20_0_3_load_151 | 75 | 0.002095 | 0.00052507 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_297-20_0_3_load_152 | 76 | 0.003305 | 0.00082831 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_297-20_0_3_load_51 | 77 | 0.0016912 | 0.00042384 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_297-20_0_3_load_129 | 80 | 0.0012403 | 0.00031084 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_297-20_0_3_load_130 | 84 | 0.0052399 | 0.0013132 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_297-20_0_3_load_165 | 85 | 0.00085947 | 0.0002154 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_297-20_0_3_load_124 | 86 | 0.00043144 | 0.00010813 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_297-20_0_3_load_156 | 87 | 0.0023915 | 0.00059936 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_297-20_0_3_load_157 | 88 | 0.00050524 | 0.00012663 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_297-20_0_3_load_49 | 89 | 0.0015156 | 0.00037985 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_297-20_0_3_load_103 | 90 | 0.00092774 | 0.00023251 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_297-20_0_3_load_169 | 92 | 0.0015113 | 0.00037876 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_297-20_0_3_load_131 | 94 | 0.0036037 | 0.00090317 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_297-20_0_3_load_125 | 95 | 0.00065446 | 0.00016402 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_297-20_0_3_load_48 | 96 | 0.0070951 | 0.0017782 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_297-20_0_3_load_57 | 98 | 0.00026004 | 6.5173e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_297-20_0_3_load_60 | 99 | 0.00041615 | 0.0001043 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_297-20_0_3_load_61 | 100 | 0.0075798 | 0.0018997 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_297-20_0_3_load_88 | 101 | 0.00016131 | 4.0429e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_297-20_0_3_load_62 | 102 | 0.00022197 | 5.5631e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_297-20_0_3_load_74 | 103 | 0.001972 | 0.00049424 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_297-20_0_3_load_86 | 105 | 0.00035131 | 8.8046e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_297-20_0_3_load_63 | 106 | 0.0013894 | 0.00034821 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_297-20_0_3_load_64 | 107 | 0.0023163 | 0.00058052 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_297-20_0_3_load_137 | 108 | 0.00065164 | 0.00016332 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_297-20_0_3_load_135 | 109 | 0.0022368 | 0.00056061 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_297-20_0_3_load_65 | 110 | 0.00013071 | 3.2758e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_297-20_0_3_load_66 | 111 | 0.00021691 | 5.4363e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_297-20_0_3_load_67 | 112 | 0.00025033 | 6.2738e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_297-20_0_3_load_69 | 114 | 0.00035037 | 8.7811e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_297-20_0_3_load_70 | 115 | 0.00012666 | 3.1743e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_297-20_0_3_load_71 | 116 | 0.0004681 | 0.00011732 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_297-20_0_3_load_72 | 117 | 0.00025039 | 6.2753e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_297-20_0_3_load_87 | 118 | 0.00014738 | 3.6938e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_297-20_0_3_load_119 | 120 | 0.00023577 | 5.9091e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_297-20_0_3_load_120 | 121 | 0.00065019 | 0.00016295 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_297-20_0_3_load_75 | 122 | 0.0069183 | 0.0017339 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_297-20_0_3_load_77 | 123 | 0.0031843 | 0.00079806 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_297-20_0_3_load_78 | 124 | 0.0017626 | 0.00044176 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_297-20_0_3_load_79 | 125 | 0.0022403 | 0.00056148 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_297-20_0_3_load_141 | 126 | 0.0018248 | 0.00045733 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_297-20_0_3_load_142 | 127 | 0.0036054 | 0.00090359 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_297-20_0_3_load_168 | 128 | 0.00029741 | 7.4539e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_297-20_0_3_load_121 | 129 | 0.0001137 | 2.8496e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_297-20_0_3_load_98 | 131 | 0.00024416 | 6.1192e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_297-20_0_3_load_96 | 132 | 0.00012821 | 3.2134e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_297-20_0_3_load_95 | 133 | 0.00025233 | 6.3239e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_297-20_0_3_load_97 | 134 | 0.00014244 | 3.5699e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_297-20_0_3_load_99 | 135 | 0.00011168 | 2.799e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_297-20_0_3_load_100 | 136 | 0.00053313 | 0.00013361 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_297-20_0_3_load_109 | 137 | 0.00030332 | 7.6019e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_297-20_0_3_load_123 | 140 | 0.00014361 | 3.5992e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_297-20_0_3_load_126 | 141 | 0.00071276 | 0.00017863 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_297-20_0_3_load_128 | 142 | 0.00080269 | 0.00020117 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_297-20_0_3_load_148 | 143 | 0.0016473 | 0.00041286 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_297-20_0_3_load_164 | 144 | 0.0018699 | 0.00046864 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_297-20_0_3_load_132 | 146 | 0.0029014 | 0.00072715 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_297-20_0_3_load_133 | 147 | 0.0063183 | 0.0015835 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_297-20_0_3_load_143 | 148 | 0.0007586 | 0.00019012 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_297-20_0_3_load_139 | 149 | 0.00049217 | 0.00012335 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_297-20_0_3_load_134 | 150 | 0.0010029 | 0.00025134 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_297-20_0_3_load_136 | 151 | 0.00044726 | 0.0001121 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_297-20_0_3_load_140 | 153 | 0.001954 | 0.00048972 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_297-20_0_3_load_144 | 154 | 0.0017825 | 0.00044673 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_297-20_0_3_load_146 | 155 | 0.00037801 | 9.4739e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_297-20_0_3_load_147 | 156 | 0.0024783 | 0.00062111 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_297-20_0_3_load_150 | 158 | 0.00274 | 0.0006867 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_297-20_0_3_load_154 | 159 | 0.0017416 | 0.00043648 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_297-20_0_3_load_158 | 160 | 0.00071777 | 0.00017989 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_297-20_0_3_load_153 | 161 | 0.0022347 | 0.00056008 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_297-20_0_3_load_155 | 162 | 0.0091869 | 0.0023024 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_297-20_0_3_load_159 | 163 | 0.0015704 | 0.00039359 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_297-20_0_3_load_160 | 164 | 0.0020617 | 0.0005167 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_297-20_0_3_load_161 | 165 | 0.0017657 | 0.00044253 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_297-20_0_3_load_162 | 166 | 0.0014073 | 0.0003527 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_297-20_0_3_load_163 | 167 | 0.0016594 | 0.00041589 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_297-20_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_297-20_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.033976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_297-20_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.022223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_297-20_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.046248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_297-20_0_3_line_4 | NAYY 4x150 SE | 3 | 7 | 0.25793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_297-20_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.24546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_297-20_0_3_line_6 | NAYY 4x150 SE | 6 | 8 | 0.0012898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_297-20_0_3_line_7 | NAYY 4x150 SE | 7 | 9 | 0.014285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_297-20_0_3_line_8 | NAYY 4x150 SE | 8 | 130 | 0.043659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_297-20_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.020803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_297-20_0_3_line_10 | NAYY 4x150 SE | 10 | 24 | 0.16232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_297-20_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.18088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_297-20_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.11105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_297-20_0_3_line_13 | NAYY 4x150 SE | 12 | 20 | 0.0060421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_297-20_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.049034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_297-20_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.10802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_297-20_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.00015326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_297-20_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.018109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_297-20_0_3_line_18 | NAYY 4x150 SE | 15 | 18 | 0.22155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_297-20_0_3_line_19 | NAYY 4x150 SE | 16 | 21 | 0.029815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_297-20_0_3_line_20 | NAYY 4x150 SE | 17 | 22 | 0.013784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_297-20_0_3_line_21 | NAYY 4x150 SE | 18 | 23 | 0.15892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_297-20_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.023156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_297-20_0_3_line_23 | NAYY 4x150 SE | 19 | 21 | 0.016984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_297-20_0_3_line_24 | NAYY 4x150 SE | 22 | 136 | 0.025307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_297-20_0_3_line_25 | NAYY 4x150 SE | 23 | 104 | 0.12277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_297-20_0_3_line_26 | NAYY 4x150 SE | 23 | 137 | 0.14658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_297-20_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.0128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_297-20_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.010229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_297-20_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.0057305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_297-20_0_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.060666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_297-20_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.052346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_297-20_0_3_line_32 | NAYY 4x150 SE | 29 | 31 | 0.014231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_297-20_0_3_line_33 | NAYY 4x150 SE | 30 | 37 | 0.011828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_297-20_0_3_line_34 | NAYY 4x150 SE | 31 | 38 | 0.009657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_297-20_0_3_line_35 | NAYY 4x150 SE | 31 | 34 | 0.013166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_297-20_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.026996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_297-20_0_3_line_37 | NAYY 4x150 SE | 32 | 34 | 0.029343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_297-20_0_3_line_38 | NAYY 4x150 SE | 33 | 47 | 0.022214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_297-20_0_3_line_39 | NAYY 4x150 SE | 33 | 48 | 0.031361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_297-20_0_3_line_40 | NAYY 4x150 SE | 35 | 36 | 0.05503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_297-20_0_3_line_41 | NAYY 4x150 SE | 36 | 49 | 0.016098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_297-20_0_3_line_42 | NAYY 4x150 SE | 36 | 50 | 0.17024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_297-20_0_3_line_43 | NAYY 4x150 SE | 37 | 41 | 0.027343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_297-20_0_3_line_44 | NAYY 4x150 SE | 38 | 46 | 0.004839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_297-20_0_3_line_45 | NAYY 4x150 SE | 39 | 40 | 0.032952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_297-20_0_3_line_46 | NAYY 4x150 SE | 39 | 41 | 0.023121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_297-20_0_3_line_47 | NAYY 4x150 SE | 39 | 42 | 0.010215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_297-20_0_3_line_48 | NAYY 4x150 SE | 40 | 53 | 0.010392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_297-20_0_3_line_49 | NAYY 4x150 SE | 42 | 44 | 0.0090544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_297-20_0_3_line_50 | NAYY 4x150 SE | 43 | 44 | 0.024616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_297-20_0_3_line_51 | NAYY 4x150 SE | 43 | 45 | 0.018363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_297-20_0_3_line_52 | NAYY 4x150 SE | 46 | 54 | 0.011321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_297-20_0_3_line_53 | NAYY 4x150 SE | 47 | 55 | 0.00027575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_297-20_0_3_line_54 | NAYY 4x150 SE | 49 | 58 | 0.025496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_297-20_0_3_line_55 | NAYY 4x150 SE | 50 | 59 | 0.012917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_297-20_0_3_line_56 | NAYY 4x150 SE | 51 | 52 | 0.0087851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_297-20_0_3_line_57 | NAYY 4x150 SE | 52 | 53 | 0.020789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_297-20_0_3_line_58 | NAYY 4x150 SE | 54 | 56 | 0.0138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_297-20_0_3_line_59 | NAYY 4x150 SE | 55 | 57 | 6.2851e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_297-20_0_3_line_60 | NAYY 4x150 SE | 57 | 96 | 0.017095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_297-20_0_3_line_61 | NAYY 4x150 SE | 58 | 60 | 0.037027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_297-20_0_3_line_62 | NAYY 4x150 SE | 58 | 61 | 0.0036843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_297-20_0_3_line_63 | NAYY 4x150 SE | 61 | 103 | 0.025485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_297-20_0_3_line_64 | NAYY 4x150 SE | 62 | 63 | 0.032826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_297-20_0_3_line_65 | NAYY 4x150 SE | 63 | 97 | 0.031599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_297-20_0_3_line_66 | NAYY 4x150 SE | 64 | 65 | 0.07936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_297-20_0_3_line_67 | NAYY 4x150 SE | 64 | 66 | 0.18097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_297-20_0_3_line_68 | NAYY 4x150 SE | 65 | 104 | 0.078189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_297-20_0_3_line_69 | NAYY 4x150 SE | 66 | 99 | 0.018614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_297-20_0_3_line_70 | NAYY 4x150 SE | 66 | 97 | 0.00935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_297-20_0_3_line_71 | NAYY 4x150 SE | 67 | 68 | 0.025442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_297-20_0_3_line_72 | NAYY 4x150 SE | 67 | 69 | 0.031131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_297-20_0_3_line_73 | NAYY 4x150 SE | 68 | 70 | 0.024693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_297-20_0_3_line_74 | NAYY 4x150 SE | 69 | 71 | 0.0084378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_297-20_0_3_line_75 | NAYY 4x150 SE | 70 | 72 | 0.025063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_297-20_0_3_line_76 | NAYY 4x150 SE | 70 | 73 | 0.034468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_297-20_0_3_line_77 | NAYY 4x150 SE | 71 | 74 | 0.024786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_297-20_0_3_line_78 | NAYY 4x150 SE | 72 | 75 | 0.018124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_297-20_0_3_line_79 | NAYY 4x150 SE | 72 | 76 | 0.015311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_297-20_0_3_line_80 | NAYY 4x150 SE | 73 | 77 | 0.013198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_297-20_0_3_line_81 | NAYY 4x150 SE | 73 | 78 | 0.029842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_297-20_0_3_line_82 | NAYY 4x150 SE | 74 | 85 | 0.014696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_297-20_0_3_line_83 | NAYY 4x150 SE | 75 | 87 | 0.002918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_297-20_0_3_line_84 | NAYY 4x150 SE | 76 | 88 | 0.022637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_297-20_0_3_line_85 | NAYY 4x150 SE | 77 | 89 | 0.0063762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_297-20_0_3_line_86 | NAYY 4x150 SE | 78 | 90 | 0.029538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_297-20_0_3_line_87 | NAYY 4x150 SE | 79 | 80 | 0.0029237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_297-20_0_3_line_88 | NAYY 4x150 SE | 79 | 81 | 0.037205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_297-20_0_3_line_89 | NAYY 4x150 SE | 79 | 82 | 0.026713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_297-20_0_3_line_90 | NAYY 4x150 SE | 80 | 83 | 0.012515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_297-20_0_3_line_91 | NAYY 4x150 SE | 81 | 85 | 0.013122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_297-20_0_3_line_92 | NAYY 4x150 SE | 82 | 86 | 0.019285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_297-20_0_3_line_93 | NAYY 4x150 SE | 83 | 84 | 0.015376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_297-20_0_3_line_94 | NAYY 4x150 SE | 84 | 94 | 0.015269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_297-20_0_3_line_95 | NAYY 4x150 SE | 86 | 95 | 0.012034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_297-20_0_3_line_96 | NAYY 4x150 SE | 87 | 159 | 0.00060002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_297-20_0_3_line_97 | NAYY 4x150 SE | 88 | 160 | 0.00149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_297-20_0_3_line_98 | NAYY 4x150 SE | 89 | 96 | 0.010319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_297-20_0_3_line_99 | NAYY 4x150 SE | 91 | 92 | 0.03679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_297-20_0_3_line_100 | NAYY 4x150 SE | 91 | 93 | 0.14523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_297-20_0_3_line_101 | NAYY 4x150 SE | 93 | 144 | 0.051282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_297-20_0_3_line_102 | NAYY 4x150 SE | 94 | 146 | 0.0042429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_297-20_0_3_line_103 | NAYY 4x150 SE | 95 | 141 | 0.0074665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_297-20_0_3_line_104 | NAYY 4x150 SE | 97 | 98 | 0.0065037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_297-20_0_3_line_105 | NAYY 4x150 SE | 98 | 100 | 0.048398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_297-20_0_3_line_106 | NAYY 4x150 SE | 99 | 101 | 0.002302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_297-20_0_3_line_107 | NAYY 4x150 SE | 100 | 102 | 0.00013965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_297-20_0_3_line_108 | NAYY 4x150 SE | 101 | 105 | 0.0079147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_297-20_0_3_line_109 | NAYY 4x150 SE | 102 | 106 | 0.019901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_297-20_0_3_line_110 | NAYY 4x150 SE | 103 | 122 | 0.00040627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_297-20_0_3_line_111 | NAYY 4x150 SE | 105 | 118 | 0.058093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_297-20_0_3_line_112 | NAYY 4x150 SE | 106 | 107 | 0.0019511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_297-20_0_3_line_113 | NAYY 4x150 SE | 107 | 108 | 0.0071266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_297-20_0_3_line_114 | NAYY 4x150 SE | 108 | 109 | 0.0038394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_297-20_0_3_line_115 | NAYY 4x150 SE | 109 | 150 | 0.0040686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_297-20_0_3_line_116 | NAYY 4x150 SE | 110 | 111 | 0.006391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_297-20_0_3_line_117 | NAYY 4x150 SE | 110 | 112 | 0.0062491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_297-20_0_3_line_118 | NAYY 4x150 SE | 111 | 113 | 0.015734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_297-20_0_3_line_119 | NAYY 4x150 SE | 112 | 114 | 0.0095465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_297-20_0_3_line_120 | NAYY 4x150 SE | 113 | 115 | 0.050049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_297-20_0_3_line_121 | NAYY 4x150 SE | 113 | 116 | 0.011921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_297-20_0_3_line_122 | NAYY 4x150 SE | 114 | 117 | 0.055376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_297-20_0_3_line_123 | NAYY 4x150 SE | 116 | 118 | 0.0023878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_297-20_0_3_line_124 | NAYY 4x150 SE | 119 | 120 | 0.054297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_297-20_0_3_line_125 | NAYY 4x150 SE | 119 | 121 | 0.2453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_297-20_0_3_line_126 | NAYY 4x150 SE | 120 | 128 | 0.13334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_297-20_0_3_line_127 | NAYY 4x150 SE | 121 | 129 | 0.037765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_297-20_0_3_line_128 | NAYY 4x150 SE | 122 | 123 | 0.019337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_297-20_0_3_line_129 | NAYY 4x150 SE | 123 | 124 | 0.008397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
130 | LV_297-20_0_3_line_130 | NAYY 4x150 SE | 124 | 125 | 0.00023649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_297-20_0_3_line_131 | NAYY 4x150 SE | 125 | 126 | 0.0089481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
132 | LV_297-20_0_3_line_132 | NAYY 4x150 SE | 126 | 127 | 0.0023945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
133 | LV_297-20_0_3_line_133 | NAYY 4x150 SE | 127 | 153 | 0.002519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
134 | LV_297-20_0_3_line_134 | NAYY 4x150 SE | 128 | 138 | 0.049168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_297-20_0_3_line_135 | NAYY 4x150 SE | 129 | 139 | 0.051463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_297-20_0_3_line_136 | NAYY 4x150 SE | 130 | 131 | 0.037293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_297-20_0_3_line_137 | NAYY 4x150 SE | 131 | 132 | 0.013344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_297-20_0_3_line_138 | NAYY 4x150 SE | 132 | 133 | 0.02259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_297-20_0_3_line_139 | NAYY 4x150 SE | 133 | 134 | 0.011917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_297-20_0_3_line_140 | NAYY 4x150 SE | 134 | 135 | 0.0023179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_297-20_0_3_line_141 | NAYY 4x150 SE | 135 | 136 | 0.020158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_297-20_0_3_line_142 | NAYY 4x150 SE | 138 | 158 | 0.13644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_297-20_0_3_line_143 | NAYY 4x150 SE | 139 | 140 | 0.13016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_297-20_0_3_line_144 | NAYY 4x150 SE | 141 | 142 | 0.0075995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_297-20_0_3_line_145 | NAYY 4x150 SE | 142 | 143 | 0.008886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_297-20_0_3_line_146 | NAYY 4x150 SE | 143 | 145 | 0.061745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_297-20_0_3_line_147 | NAYY 4x150 SE | 144 | 167 | 0.026771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_297-20_0_3_line_148 | NAYY 4x150 SE | 145 | 156 | 0.013378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_297-20_0_3_line_149 | NAYY 4x150 SE | 145 | 154 | 0.053566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_297-20_0_3_line_150 | NAYY 4x150 SE | 146 | 147 | 0.0087545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
151 | LV_297-20_0_3_line_151 | NAYY 4x150 SE | 147 | 148 | 0.0076063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
152 | LV_297-20_0_3_line_152 | NAYY 4x150 SE | 148 | 149 | 0.0053707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
153 | LV_297-20_0_3_line_153 | NAYY 4x150 SE | 149 | 152 | 0.0078357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
154 | LV_297-20_0_3_line_154 | NAYY 4x150 SE | 150 | 151 | 0.011692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_297-20_0_3_line_155 | NAYY 4x150 SE | 151 | 152 | 0.011248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_297-20_0_3_line_156 | NAYY 4x150 SE | 152 | 153 | 0.018859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
157 | LV_297-20_0_3_line_157 | NAYY 4x150 SE | 154 | 155 | 0.0094745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_297-20_0_3_line_158 | NAYY 4x150 SE | 156 | 157 | 0.065039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_297-20_0_3_line_159 | NAYY 4x150 SE | 157 | 158 | 0.077586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_297-20_0_3_line_160 | NAYY 4x150 SE | 159 | 161 | 0.015816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_297-20_0_3_line_161 | NAYY 4x150 SE | 160 | 163 | 0.026092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_297-20_0_3_line_162 | NAYY 4x150 SE | 161 | 162 | 0.0096683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_297-20_0_3_line_163 | NAYY 4x150 SE | 163 | 164 | 0.02404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_297-20_0_3_line_164 | NAYY 4x150 SE | 164 | 165 | 0.0050209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_297-20_0_3_line_165 | NAYY 4x150 SE | 165 | 166 | 0.024205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_297-20_0_3_line_166 | NAYY 4x150 SE | 166 | 167 | 0.0030025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_297-20_0_3_trafo_76 | 0.25 MVA 20/0.4 kV | 168 | 60 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2709382.6675 | 1245896.0477 | 2709384.2679 | 1245902.5548 | 2709389.8328 | 1245920.4057
1 | 2709374.5535 | 1245863.0551 | 2709382.6675 | 1245896.0477
2 | 2709398.9429 | 1245940.6227 | 2709395.5188 | 1245934.5325 | 2709390.4532 | 1245922.396 | 2709389.8328 | 1245920.4057
3 | 2709374.5535 | 1245863.0551 | 2709384.0688 | 1245861.3403 | 2709389.9219 | 1245861.1147 | 2709392.7389 | 1245861.6115 | 2709394.887 | 1245862.7298 | 2709396.6218 | 1245864.541 | 2709398.2525 | 1245867.0843 | 2709399.2515 | 1245869.4602 | 2709399.795 | 1245871.5385 | 2709400.4301 | 1245875.6091 | 2709401.102 | 1245880.1473 | 2709401.9534 | 1245882.3314 | 2709402.852 | 1245883.5935 | 2709404.1182 | 1245884.5954 | 2709404.9627 | 1245885.0714
4 | 2709398.9429 | 1245940.6227 | 2709402.2447 | 1245945.9657 | 2709407.0646 | 1245952.1707 | 2709485.0521 | 1246044.4172 | 2709490.2284 | 1246051.3627 | 2709493.6508 | 1246056.3077 | 2709496.6629 | 1246062.1902 | 2709508.0791 | 1246093.3594 | 2709520.3655 | 1246123.2214 | 2709523.6088 | 1246129.6753 | 2709526.6506 | 1246134.7689 | 2709534.5388 | 1246145.0228 | 2709541.3289 | 1246152.5432
5 | 2709263.1144 | 1246188.9007 | 2709099.3431 | 1246006.0631
6 | 2709263.1755 | 1246190.1891 | 2709263.1144 | 1246188.9007
7 | 2709541.3289 | 1246152.5432 | 2709550.9056 | 1246163.1432
8 | 2709237.948 | 1246220.3246 | 2709246.7183 | 1246215.1264 | 2709256.8255 | 1246210.3754 | 2709261.6778 | 1246204.9827 | 2709263.5394 | 1246197.8668 | 2709263.1755 | 1246190.1891
9 | 2709564.214 | 1246179.0425 | 2709562.366 | 1246175.8282 | 2709550.9056 | 1246163.1432
10 | 2709564.214 | 1246179.0425 | 2709568.7571 | 1246186.9441 | 2709596.9897 | 1246251.7846 | 2709603.2887 | 1246265.0116 | 2709610.4005 | 1246278.0091 | 2709619.468 | 1246292.2992 | 2709634.1067 | 1246313.409 | 2709640.7903 | 1246321.3901
11 | 2709448.8378 | 1246318.3468 | 2709564.214 | 1246179.0425
12 | 2709448.8378 | 1246318.3468 | 2709445.9931 | 1246317.3157 | 2709441.5447 | 1246316.3773 | 2709437.7684 | 1246316.2853 | 2709432.8675 | 1246316.9399 | 2709429.0279 | 1246318.2256 | 2709422.9052 | 1246320.8036 | 2709412.0903 | 1246326.2418 | 2709403.4546 | 1246329.8743 | 2709387.8287 | 1246335.1904 | 2709376.839 | 1246339.0464 | 2709364.1594 | 1246342.3485 | 2709350.2381 | 1246345.3832 | 2709343.2649 | 1246346.6685
13 | 2709343.2649 | 1246346.6685 | 2709337.3229 | 1246347.7638
14 | 2709248.3689 | 1246303.4833 | 2709244.1016 | 1246308.7089 | 2709246.8021 | 1246317.5658 | 2709255.0457 | 1246326.5915 | 2709262.6758 | 1246332.0031 | 2709273.1843 | 1246336.5496
15 | 2709248.3689 | 1246303.4833 | 2709222.7564 | 1246319.3243 | 2709204.8463 | 1246334.2065 | 2709188.633 | 1246350.0874 | 2709186.962 | 1246369.4277 | 2709175.0324 | 1246365.6607
16 | 2709273.3249 | 1246336.6105 | 2709273.1843 | 1246336.5496
17 | 2709175.0324 | 1246365.6607 | 2709176.7104 | 1246360.2984 | 2709177.5723 | 1246347.8376
18 | 2709004.7144 | 1246442.7566 | 2709015.0614 | 1246427.8125 | 2709024.5826 | 1246401.0772 | 2709038.1549 | 1246371.8254 | 2709046.7393 | 1246361.1079 | 2709058.0994 | 1246356.8134 | 2709078.5771 | 1246357.5906 | 2709159.9753 | 1246363.9043 | 2709175.0324 | 1246365.6607
19 | 2709300.3598 | 1246345.3659 | 2709289.9389 | 1246339.3335 | 2709283.6428 | 1246341.0745 | 2709273.3249 | 1246336.6105
20 | 2709177.5723 | 1246347.8376 | 2709178.3582 | 1246336.4762 | 2709179.1589 | 1246334.2187
21 | 2709010.5804 | 1246549.4167 | 2709016.1468 | 1246531.8716 | 2709043.0023 | 1246487.8188 | 2709051.6408 | 1246467.995 | 2709054.4436 | 1246453.6462 | 2709041.9074 | 1246449.5902 | 2709026.4056 | 1246452.7188 | 2709004.7144 | 1246442.7566
22 | 2709315.0591 | 1246353.8748 | 2709327.1513 | 1246349.6388 | 2709337.3229 | 1246347.7638
23 | 2709315.0591 | 1246353.8748 | 2709300.3598 | 1246345.3659
24 | 2709179.1589 | 1246334.2187 | 2709186.3283 | 1246314.0049 | 2709187.193 | 1246310.2438
25 | 2709069.2912 | 1246655.6149 | 2709062.0148 | 1246626.0684 | 2709048.9398 | 1246602.8649 | 2709010.5804 | 1246549.4167
26 | 2709010.5804 | 1246549.4167 | 2709003.0949 | 1246543.9525 | 2708993.3498 | 1246542.6168 | 2708982.5926 | 1246547.423 | 2708966.9636 | 1246559.5344 | 2708947.0093 | 1246569.7872 | 2708940.4447 | 1246579.163 | 2708931.5112 | 1246611.3693 | 2708923.9646 | 1246621.1496 | 2708916.6966 | 1246625.2305 | 2708908.8613 | 1246626.4654
27 | 2709323.333 | 1247046.3917 | 2709332.9546 | 1247037.9492
28 | 2709340.6433 | 1247031.2028 | 2709332.9546 | 1247037.9492
29 | 2709323.333 | 1247046.3917 | 2709322.3353 | 1247047.2671 | 2709317.9538 | 1247046.8304
30 | 2709340.6433 | 1247031.2028 | 2709350.8556 | 1247042.7893 | 2709353.2616 | 1247049.1499 | 2709355.6809 | 1247071.1678 | 2709358.8387 | 1247087.1501
31 | 2709372.4407 | 1247036.6491 | 2709365.0562 | 1247059.7426 | 2709358.8387 | 1247087.1501
32 | 2709358.2146 | 1247101.3166 | 2709359.0401 | 1247095.883 | 2709358.8387 | 1247087.1501
33 | 2709372.4407 | 1247036.6491 | 2709383.7475 | 1247040.1212
34 | 2709358.2146 | 1247101.3166 | 2709356.6109 | 1247110.8392
35 | 2709358.2146 | 1247101.3166 | 2709345.0644 | 1247101.9592
36 | 2709316.4449 | 1247097.0876 | 2709305.8865 | 1247096.8928 | 2709298.371 | 1247098.0218 | 2709293.8627 | 1247105.6894
37 | 2709316.4449 | 1247097.0876 | 2709326.643 | 1247100.4338 | 2709336.9051 | 1247102.3579 | 2709345.0644 | 1247101.9592
38 | 2709293.8627 | 1247105.6894 | 2709283.8944 | 1247105.4499 | 2709271.6517 | 1247105.423
39 | 2709293.8627 | 1247105.6894 | 2709307.1277 | 1247107.0127 | 2709325.057 | 1247108.9187
40 | 2709199.2311 | 1246957.0931 | 2709222.9586 | 1246966.7155 | 2709234.6418 | 1246973.5362 | 2709246.8497 | 1246983.7186
41 | 2709199.2311 | 1246957.0931 | 2709198.5308 | 1246961.884 | 2709194.0416 | 1246972.2097
42 | 2709199.2311 | 1246957.0931 | 2709199.4529 | 1246949.1574 | 2709198.0814 | 1246935.0208 | 2709197.5469 | 1246924.2578 | 2709198.6159 | 1246912.1678 | 2709202.1286 | 1246901.535 | 2709212.1511 | 1246884.5059 | 2709214.5944 | 1246874.9209 | 2709220.7116 | 1246796.3592 | 2709226.217 | 1246796.9055
43 | 2709408.0312 | 1247052.3071 | 2709391.9359 | 1247042.6357 | 2709383.7475 | 1247040.1212
44 | 2709355.775 | 1247115.6054 | 2709356.6109 | 1247110.8392
45 | 2709419.076 | 1247064.2205 | 2709419.857 | 1247031.2774
46 | 2709419.076 | 1247064.2205 | 2709408.1016 | 1247064.4515 | 2709408.0312 | 1247052.3071
47 | 2709419.076 | 1247064.2205 | 2709421.6916 | 1247074.0949
48 | 2709419.857 | 1247031.2774 | 2709420.0328 | 1247023.8611 | 2709419.5213 | 1247020.9319
49 | 2709424.5985 | 1247082.6483 | 2709422.8263 | 1247078.3789 | 2709421.6916 | 1247074.0949
50 | 2709424.5985 | 1247082.6483 | 2709427.4086 | 1247086.7591 | 2709428.3134 | 1247088.0879 | 2709430.6227 | 1247092.7232 | 2709436.6367 | 1247089.4426 | 2709439.234 | 1247094.8505
51 | 2709439.234 | 1247094.8505 | 2709443.4239 | 1247104.4355 | 2709444.738 | 1247112.2276
52 | 2709355.775 | 1247115.6054 | 2709359.5674 | 1247120.1234 | 2709364.4517 | 1247122.4791
53 | 2709271.3759 | 1247105.4224 | 2709271.6517 | 1247105.423
54 | 2709174.0446 | 1246987.287 | 2709184.1036 | 1246982.2014 | 2709190.7252 | 1246977.1081 | 2709194.0416 | 1246972.2097
55 | 2709226.217 | 1246796.9055 | 2709228.3216 | 1246784.1608
56 | 2709411.0479 | 1247003.0897 | 2709402.5467 | 1247005.3049
57 | 2709411.0479 | 1247003.0897 | 2709414.4974 | 1247005.3107 | 2709417.7028 | 1247010.5185 | 2709419.5213 | 1247020.9319
58 | 2709375.0836 | 1247130.3975 | 2709372.8968 | 1247126.5522 | 2709364.4517 | 1247122.4791
59 | 2709271.3131 | 1247105.4222 | 2709271.3759 | 1247105.4224
60 | 2709271.3131 | 1247105.4222 | 2709268.8301 | 1247105.4167 | 2709254.2258 | 1247105.8951
61 | 2709174.0446 | 1246987.287 | 2709175.7909 | 1246990.5106 | 2709182.8689 | 1247004.1074 | 2709191.3056 | 1247020.0436
62 | 2709174.0446 | 1246987.287 | 2709170.7597 | 1246988.9555
63 | 2709170.7597 | 1246988.9555 | 2709155.306 | 1246996.8053 | 2709148.4293 | 1247001.1836
64 | 2709134.3174 | 1246944.9854 | 2709109.9214 | 1246939.7909 | 2709102.0627 | 1246939.1725
65 | 2709070.9154 | 1246935.1696 | 2709075.7907 | 1246937.1053 | 2709102.0627 | 1246939.1725
66 | 2709108.8809 | 1246806.7313 | 2709104.8892 | 1246785.93 | 2709083.2609 | 1246731.9199
67 | 2709108.8809 | 1246806.7313 | 2709093.826 | 1246798.759 | 2709066.2802 | 1246811.407 | 2709075.7489 | 1246835.5339 | 2709075.7455 | 1246856.2394 | 2709067.1091 | 1246891.1642 | 2709067.5112 | 1246895.9977 | 2709076.2049 | 1246928.5616 | 2709063.6099 | 1246929.3973
68 | 2709069.2912 | 1246655.6149 | 2709072.6527 | 1246699.5787 | 2709077.3895 | 1246717.2578 | 2709083.2609 | 1246731.9199
69 | 2709063.6099 | 1246929.3973 | 2709060.7528 | 1246927.4098 | 2709050.9179 | 1246915.9071
70 | 2709070.9154 | 1246935.1696 | 2709068.4171 | 1246933.8003 | 2709063.6099 | 1246929.3973
71 | 2709158.1959 | 1247118.9209 | 2709172.4515 | 1247117.6293 | 2709180.5955 | 1247118.4688 | 2709183.4414 | 1247119.2103
72 | 2709127.1901 | 1247121.6803 | 2709127.6735 | 1247121.6862 | 2709158.1959 | 1247118.9209
73 | 2709207.5505 | 1247124.292 | 2709199.3328 | 1247123.3511 | 2709183.4414 | 1247119.2103
74 | 2709127.1901 | 1247121.6803 | 2709118.7529 | 1247121.5775
75 | 2709205.024 | 1247149.0544 | 2709206.8758 | 1247142.4498 | 2709207.587 | 1247135.8354 | 2709207.7622 | 1247129.6113 | 2709207.5505 | 1247124.292
76 | 2709207.5505 | 1247124.292 | 2709206.6192 | 1247107.5948 | 2709208.0256 | 1247107.5317 | 2709224.3491 | 1247106.8763
77 | 2709094.3144 | 1247121.339 | 2709100.4229 | 1247120.0168 | 2709111.2681 | 1247119.8161 | 2709118.7529 | 1247121.5775 | 2709118.7529 | 1247121.5775
78 | 2709205.024 | 1247149.0544 | 2709222.3381 | 1247154.4114
79 | 2709205.024 | 1247149.0544 | 2709201.5813 | 1247158.7655 | 2709199.0711 | 1247163.0988
80 | 2709224.3491 | 1247106.8763 | 2709237.5396 | 1247106.4422
81 | 2709223.539 | 1247077.0484 | 2709224.3491 | 1247106.8763
82 | 2709094.3144 | 1247121.339 | 2709091.9956 | 1247121.841 | 2709081.3649 | 1247126.3935 | 2709080.6671 | 1247126.6921
83 | 2709225.1257 | 1247155.2738 | 2709222.3381 | 1247154.4114
84 | 2709199.0711 | 1247163.0988 | 2709195.8069 | 1247168.7338 | 2709187.2068 | 1247182.3733
85 | 2709237.5396 | 1247106.4422 | 2709241.0257 | 1247106.3275 | 2709243.9123 | 1247106.2329
86 | 2709223.539 | 1247077.0484 | 2709233.9358 | 1247051.1746 | 2709235.5883 | 1247051.133
87 | 2709087.4037 | 1247108.2122 | 2709090.2284 | 1247107.4578
88 | 2709068.4362 | 1247131.4265 | 2709073.1345 | 1247127.3763 | 2709084.0597 | 1247122.0063 | 2709090.5379 | 1247119.7681 | 2709088.8564 | 1247113.8435 | 2709087.4037 | 1247108.2122
89 | 2709087.4037 | 1247108.2122 | 2709079.9946 | 1247110.133 | 2709070.0689 | 1247115.7884 | 2709064.442 | 1247121.0335
90 | 2709102.0909 | 1247104.9242 | 2709096.4138 | 1247104.6862 | 2709092.7791 | 1247106.7766 | 2709090.2284 | 1247107.4578
91 | 2709068.4362 | 1247131.4265 | 2709074.9607 | 1247129.1335 | 2709080.6671 | 1247126.6921
92 | 2709064.442 | 1247121.0335 | 2709053.9497 | 1247111.911 | 2709050.1395 | 1247108.1103
93 | 2709102.0909 | 1247104.9242 | 2709102.2651 | 1247097.9218 | 2709103.4995 | 1247089.6418
94 | 2709103.4995 | 1247089.6418 | 2709104.8855 | 1247080.3447 | 2709104.973 | 1247074.4764
95 | 2709050.1395 | 1247108.1103 | 2709043.1033 | 1247101.0917 | 2709041.9824 | 1247099.3203
96 | 2709225.6989 | 1247155.4512 | 2709225.1257 | 1247155.2738
97 | 2709186.4121 | 1247183.6337 | 2709187.2068 | 1247182.3733
98 | 2709243.9123 | 1247106.2329 | 2709254.2258 | 1247105.8951
99 | 2709110.748 | 1247206.7322 | 2709131.8343 | 1247209.9895 | 2709147.2546 | 1247207.9049
100 | 2709110.748 | 1247206.7322 | 2709108.6134 | 1247220.0814 | 2709106.6894 | 1247243.7429 | 2709121.9116 | 1247249.5387 | 2709144.7639 | 1247258.2218 | 2709169.6029 | 1247264.4507 | 2709177.5666 | 1247266.4545 | 2709180.207 | 1247267.8932 | 2709182.4486 | 1247270.0584 | 2709195.4421 | 1247285.2766 | 2709199.5775 | 1247291.2687
101 | 2709199.5775 | 1247291.2687 | 2709203.232 | 1247291.3805 | 2709226.1735 | 1247271.0311 | 2709236.0892 | 1247257.2717
102 | 2709104.7753 | 1247070.2531 | 2709105.014 | 1247071.729 | 2709104.973 | 1247074.4764
103 | 2709041.9824 | 1247099.3203 | 2709037.9899 | 1247093.0109
104 | 2709070.9154 | 1246935.1696 | 2709070.2245 | 1246938.226 | 2709072.4804 | 1246940.4471 | 2709072.6392 | 1246940.5758
105 | 2709093.8668 | 1246982.8139 | 2709093.1691 | 1246976.8458 | 2709087.1587 | 1246961.8788 | 2709078.8378 | 1246945.6015 | 2709072.6392 | 1246940.5758
106 | 2709050.9179 | 1246915.9071 | 2709049.4219 | 1246914.1574 | 2709049.4219 | 1246914.1574
107 | 2709093.883 | 1246982.9526 | 2709093.8668 | 1246982.8139
108 | 2709045.6386 | 1246907.2055 | 2709049.4219 | 1246914.1574
109 | 2709096.1938 | 1247002.7194 | 2709093.883 | 1246982.9526
110 | 2709148.0866 | 1247001.4018 | 2709148.4293 | 1247001.1836
111 | 2709045.6386 | 1246907.2055 | 2709038.9566 | 1246894.9273 | 2709030.8407 | 1246879.8104 | 2709022.1186 | 1246870.1311 | 2709012.3231 | 1246860.2305
112 | 2709096.1938 | 1247002.7194 | 2709096.4203 | 1247004.6572
113 | 2709097.2478 | 1247011.7356 | 2709096.4203 | 1247004.6572
114 | 2709097.2478 | 1247011.7356 | 2709097.6936 | 1247015.549
115 | 2709098.166 | 1247019.5901 | 2709097.6936 | 1247015.549
116 | 2708978.8251 | 1246850.2099 | 2708984.9945 | 1246851.8785
117 | 2708978.8251 | 1246850.2099 | 2708972.7928 | 1246848.5784
118 | 2709000.3272 | 1246852.5609 | 2708992.6706 | 1246853.9546 | 2708984.9945 | 1246851.8785
119 | 2708972.7928 | 1246848.5784 | 2708969.6429 | 1246847.7265 | 2708963.4287 | 1246846.7966
120 | 2709000.3272 | 1246852.5609 | 2708994.1507 | 1246849.8897 | 2708980.6402 | 1246845.4489 | 2708968.0905 | 1246838.8797 | 2708957.3751 | 1246828.4795
121 | 2709000.3272 | 1246852.5609 | 2709010.6438 | 1246858.5331
122 | 2708963.4287 | 1246846.7966 | 2708949.985 | 1246844.7851 | 2708946.3704 | 1246846.598 | 2708943.6101 | 1246855.7769 | 2708944.606 | 1246858.7309 | 2708948.0602 | 1246861.5299 | 2708967.9578 | 1246866.8273
123 | 2709010.6438 | 1246858.5331 | 2709012.3231 | 1246860.2305
124 | 2708839.736 | 1246714.823 | 2708847.1385 | 1246718.2171 | 2708851.4453 | 1246723.1446 | 2708857.8971 | 1246739.2204 | 2708865.0612 | 1246751.4839 | 2708871.4574 | 1246756.4275
125 | 2708839.736 | 1246714.823 | 2708834.3903 | 1246700.2243 | 2708806.8671 | 1246639.2258 | 2708799.4196 | 1246627.1573 | 2708792.3251 | 1246605.7433 | 2708785.2138 | 1246560.1317 | 2708784.6472 | 1246542.4294 | 2708787.1525 | 1246526.14 | 2708793.7215 | 1246511.571 | 2708800.8633 | 1246495.4335 | 2708808.0004 | 1246485.6513
126 | 2708871.4574 | 1246756.4275 | 2708821.3498 | 1246879.9961
127 | 2708833.6829 | 1246457.9976 | 2708827.0039 | 1246465.5447 | 2708809.3816 | 1246483.7582 | 2708808.0004 | 1246485.6513
128 | 2709148.0866 | 1247001.4018 | 2709131.7752 | 1247011.7869
129 | 2709124.692 | 1247016.2967 | 2709131.7752 | 1247011.7869
130 | 2709124.4925 | 1247016.4237 | 2709124.692 | 1247016.2967
131 | 2709117.2855 | 1247021.6595 | 2709119.1841 | 1247019.8035 | 2709124.4925 | 1247016.4237
132 | 2709117.2855 | 1247021.6595 | 2709115.5732 | 1247023.3334
133 | 2709115.5732 | 1247023.3334 | 2709113.772 | 1247025.0943
134 | 2708821.3498 | 1246879.9961 | 2708818.6328 | 1246882.3037 | 2708819.1878 | 1246886.2281 | 2708823.2247 | 1246888.9822 | 2708829.757 | 1246895.7297 | 2708832.5293 | 1246907.2788 | 2708832.5176 | 1246917.787 | 2708827.8018 | 1246919.5018
135 | 2708863.4096 | 1246416.1065 | 2708857.0445 | 1246427.3765 | 2708850.4626 | 1246436.0515 | 2708834.7507 | 1246456.7909 | 2708833.6829 | 1246457.9976
136 | 2709237.948 | 1246220.3246 | 2709233.4334 | 1246222.9769 | 2709220.3417 | 1246231.4092 | 2709214.3024 | 1246238.8929 | 2709211.1548 | 1246244.9974
137 | 2709205.0392 | 1246256.8576 | 2709211.1548 | 1246244.9974
138 | 2709194.6864 | 1246276.9356 | 2709205.0392 | 1246256.8576
139 | 2709194.6864 | 1246276.9356 | 2709192.1338 | 1246281.886 | 2709190.9057 | 1246288.1137
140 | 2709190.5972 | 1246290.4093 | 2709190.7835 | 1246288.7333 | 2709190.9057 | 1246288.1137
141 | 2709190.5972 | 1246290.4093 | 2709189.5155 | 1246300.1413 | 2709187.193 | 1246310.2438
142 | 2708919.718 | 1247020.3406 | 2708827.8018 | 1246919.5018
143 | 2708863.4096 | 1246416.1065 | 2708875.1381 | 1246404.5013 | 2708909.1118 | 1246380.5392 | 2708937.6163 | 1246356.1097 | 2708953.1976 | 1246340.8615 | 2708961.2024 | 1246330.9447
144 | 2709037.9899 | 1247093.0109 | 2709033.9263 | 1247086.5891
145 | 2709030.8945 | 1247078.2363 | 2709033.9263 | 1247086.5891 | 2709033.9263 | 1247086.5891
146 | 2709000.0173 | 1247033.701 | 2709009.4289 | 1247033.8185 | 2709018.1328 | 1247038.7269 | 2709023.5841 | 1247045.8995 | 2709026.7166 | 1247057.144 | 2709028.0588 | 1247070.4238 | 2709030.8945 | 1247078.2363
147 | 2709236.0892 | 1247257.2717 | 2709242.3467 | 1247248.5887 | 2709242.4968 | 1247239.6287 | 2709238.8774 | 1247233.5126
148 | 2709000.0173 | 1247033.701 | 2708989.7064 | 1247038.5264 | 2708988.2927 | 1247039.9322
149 | 2709000.0173 | 1247033.701 | 2708998.1381 | 1247027.0166 | 2708994.6553 | 1247020.8476 | 2708971.1486 | 1246989.0554
150 | 2709104.7753 | 1247070.2531 | 2709103.3782 | 1247061.6107
151 | 2709103.3782 | 1247061.6107 | 2709102.5654 | 1247056.5829 | 2709102.472 | 1247054.0715
152 | 2709102.472 | 1247054.0715 | 2709102.2723 | 1247048.7045 | 2709102.2723 | 1247048.7045
153 | 2709103.9544 | 1247041.0515 | 2709102.2723 | 1247048.7045
154 | 2709098.166 | 1247019.5901 | 2709099.5236 | 1247031.2031
155 | 2709103.9544 | 1247041.0515 | 2709100.1271 | 1247036.3662 | 2709099.5236 | 1247031.2031
156 | 2709103.9544 | 1247041.0515 | 2709106.9697 | 1247034.4461 | 2709112.329 | 1247026.505 | 2709113.772 | 1247025.0943
157 | 2708971.2047 | 1246980.1395 | 2708969.6842 | 1246984.3482 | 2708970.5494 | 1246988.245 | 2708971.1486 | 1246989.0554
158 | 2708948.4695 | 1247091.1666 | 2708978.1779 | 1247049.9905 | 2708988.2927 | 1247039.9322
159 | 2708948.4695 | 1247091.1666 | 2708941.9622 | 1247084.7197 | 2708935.5347 | 1247071.4687 | 2708921.3484 | 1247022.4354 | 2708919.718 | 1247020.3406
160 | 2709240.8082 | 1247160.126 | 2709225.6989 | 1247155.4512
161 | 2709186.4121 | 1247183.6337 | 2709183.137 | 1247188.8278 | 2709182.0779 | 1247191.7774 | 2709181.9446 | 1247194.9108 | 2709182.7501 | 1247197.9392 | 2709184.4161 | 1247200.5942 | 2709186.8036 | 1247202.6398 | 2709190.4756 | 1247204.8168
162 | 2709250.0445 | 1247162.9837 | 2709240.8082 | 1247160.126
163 | 2709190.4756 | 1247204.8168 | 2709211.1546 | 1247217.0767
164 | 2709215.4735 | 1247219.6372 | 2709211.1546 | 1247217.0767
165 | 2709215.4735 | 1247219.6372 | 2709236.2947 | 1247231.9814
166 | 2709236.2947 | 1247231.9814 | 2709238.8774 | 1247233.5126 | 2709238.8774 | 1247233.5126

## bus_geodata
| x | y | coords
0 | 2709382.6675 | 1245896.0477
1 | 2709389.8328 | 1245920.4056
2 | 2709374.5535 | 1245863.0551
3 | 2709398.9429 | 1245940.6227
4 | 2709404.9627 | 1245885.0714
5 | 2709099.3431 | 1246006.0631
6 | 2709263.1144 | 1246188.9007
7 | 2709541.3289 | 1246152.5432
8 | 2709263.1755 | 1246190.1891
9 | 2709550.9056 | 1246163.1432
10 | 2709564.214 | 1246179.0425
11 | 2709448.8378 | 1246318.3468
12 | 2709343.2649 | 1246346.6685
13 | 2709248.3689 | 1246303.4833
14 | 2709273.1843 | 1246336.5496
15 | 2709175.0324 | 1246365.6607
16 | 2709273.3249 | 1246336.6105
17 | 2709177.5723 | 1246347.8376
18 | 2709004.7144 | 1246442.7566
19 | 2709315.0591 | 1246353.8748
20 | 2709337.3229 | 1246347.7638
21 | 2709300.3598 | 1246345.3659
22 | 2709179.1589 | 1246334.2187
23 | 2709010.5804 | 1246549.4167
24 | 2709640.7903 | 1246321.3901
25 | 2709332.9546 | 1247037.9492
26 | 2709323.333 | 1247046.3917
27 | 2709340.6433 | 1247031.2028
28 | 2709317.9538 | 1247046.8304
29 | 2709358.8387 | 1247087.1501
30 | 2709372.4407 | 1247036.6491
31 | 2709358.2146 | 1247101.3166
32 | 2709316.4449 | 1247097.0876
33 | 2709293.8627 | 1247105.6894
34 | 2709345.0644 | 1247101.9592
35 | 2709246.8497 | 1246983.7186
36 | 2709199.2311 | 1246957.0931
37 | 2709383.7475 | 1247040.1212
38 | 2709356.6109 | 1247110.8392
39 | 2709419.076 | 1247064.2205
40 | 2709419.857 | 1247031.2774
41 | 2709408.0312 | 1247052.3071
42 | 2709421.6916 | 1247074.0949
43 | 2709439.234 | 1247094.8505
44 | 2709424.5985 | 1247082.6483
45 | 2709444.738 | 1247112.2276
46 | 2709355.775 | 1247115.6054
47 | 2709271.6517 | 1247105.423
48 | 2709325.057 | 1247108.9187
49 | 2709194.0416 | 1246972.2097
50 | 2709226.217 | 1246796.9055
51 | 2709402.5467 | 1247005.3049
52 | 2709411.0479 | 1247003.0897
53 | 2709419.5213 | 1247020.9319
54 | 2709364.4517 | 1247122.4791
55 | 2709271.3759 | 1247105.4224
56 | 2709375.0836 | 1247130.3975
57 | 2709271.3131 | 1247105.4222
58 | 2709174.0446 | 1246987.287
59 | 2709228.3216 | 1246784.1608
60 | 2709191.3056 | 1247020.0436
61 | 2709170.7597 | 1246988.9555
62 | 2709134.3174 | 1246944.9854
63 | 2709102.0627 | 1246939.1725
64 | 2709108.8809 | 1246806.7313
65 | 2709083.2609 | 1246731.9199
66 | 2709063.6099 | 1246929.3973
67 | 2709158.1959 | 1247118.9209
68 | 2709183.4414 | 1247119.2103
69 | 2709127.1901 | 1247121.6803
70 | 2709207.5505 | 1247124.292
71 | 2709118.7529 | 1247121.5775
72 | 2709205.024 | 1247149.0544
73 | 2709224.3491 | 1247106.8763
74 | 2709094.3144 | 1247121.339
75 | 2709222.3381 | 1247154.4114
76 | 2709199.0711 | 1247163.0988
77 | 2709237.5396 | 1247106.4422
78 | 2709223.539 | 1247077.0484
79 | 2709087.4037 | 1247108.2122
80 | 2709090.2284 | 1247107.4578
81 | 2709068.4362 | 1247131.4265
82 | 2709064.442 | 1247121.0335
83 | 2709102.0909 | 1247104.9242
84 | 2709103.4995 | 1247089.6418
85 | 2709080.6671 | 1247126.6921
86 | 2709050.1395 | 1247108.1103
87 | 2709225.1257 | 1247155.2738
88 | 2709187.2068 | 1247182.3733
89 | 2709243.9123 | 1247106.2329
90 | 2709235.5883 | 1247051.133
91 | 2709110.748 | 1247206.7322
92 | 2709147.2546 | 1247207.9049
93 | 2709199.5775 | 1247291.2687
94 | 2709104.973 | 1247074.4764
95 | 2709041.9824 | 1247099.3203
96 | 2709254.2258 | 1247105.8951
97 | 2709070.9154 | 1246935.1696
98 | 2709072.6392 | 1246940.5758
99 | 2709050.9179 | 1246915.9071
100 | 2709093.8668 | 1246982.8139
101 | 2709049.4219 | 1246914.1574
102 | 2709093.883 | 1246982.9526
103 | 2709148.4293 | 1247001.1836
104 | 2709069.2912 | 1246655.6149
105 | 2709045.6386 | 1246907.2055
106 | 2709096.1938 | 1247002.7194
107 | 2709096.4203 | 1247004.6572
108 | 2709097.2478 | 1247011.7356
109 | 2709097.6936 | 1247015.549
110 | 2708978.8251 | 1246850.2099
111 | 2708984.9945 | 1246851.8785
112 | 2708972.7928 | 1246848.5784
113 | 2709000.3272 | 1246852.5609
114 | 2708963.4287 | 1246846.7966
115 | 2708957.3751 | 1246828.4795
116 | 2709010.6438 | 1246858.5331
117 | 2708967.9578 | 1246866.8273
118 | 2709012.3231 | 1246860.2305
119 | 2708839.736 | 1246714.823
120 | 2708871.4574 | 1246756.4275
121 | 2708808.0004 | 1246485.6513
122 | 2709148.0866 | 1247001.4018
123 | 2709131.7752 | 1247011.7869
124 | 2709124.692 | 1247016.2967
125 | 2709124.4925 | 1247016.4237
126 | 2709117.2855 | 1247021.6595
127 | 2709115.5732 | 1247023.3334
128 | 2708821.3498 | 1246879.9961
129 | 2708833.6829 | 1246457.9976
130 | 2709237.948 | 1246220.3246
131 | 2709211.1548 | 1246244.9973
132 | 2709205.0392 | 1246256.8576
133 | 2709194.6864 | 1246276.9356
134 | 2709190.9057 | 1246288.1137
135 | 2709190.5972 | 1246290.4093
136 | 2709187.193 | 1246310.2438
137 | 2708908.8613 | 1246626.4654
138 | 2708827.8018 | 1246919.5018
139 | 2708863.4096 | 1246416.1065
140 | 2708961.2024 | 1246330.9447
141 | 2709037.9899 | 1247093.0109
142 | 2709033.9263 | 1247086.5891
143 | 2709030.8945 | 1247078.2363
144 | 2709236.0892 | 1247257.2717
145 | 2709000.0173 | 1247033.701
146 | 2709104.7753 | 1247070.2531
147 | 2709103.3782 | 1247061.6107
148 | 2709102.472 | 1247054.0715
149 | 2709102.2723 | 1247048.7045
150 | 2709098.166 | 1247019.5901
151 | 2709099.5236 | 1247031.2031
152 | 2709103.9544 | 1247041.0515
153 | 2709113.772 | 1247025.0943
154 | 2708971.1486 | 1246989.0554
155 | 2708971.2047 | 1246980.1395
156 | 2708988.2927 | 1247039.9322
157 | 2708948.4695 | 1247091.1666
158 | 2708919.718 | 1247020.3406
159 | 2709225.6989 | 1247155.4512
160 | 2709186.4121 | 1247183.6337
161 | 2709240.8082 | 1247160.126
162 | 2709250.0445 | 1247162.9837
163 | 2709190.4756 | 1247204.8168
164 | 2709211.1546 | 1247217.0767
165 | 2709215.4735 | 1247219.6372
166 | 2709236.2947 | 1247231.9814
167 | 2709238.8774 | 1247233.5126
168 | 2709194.8719 | 1247026.78

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1