## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_297-9_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_297-9_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_297-9_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_297-9_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_297-9_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_297-9_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_297-9_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_297-9_0_5_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_297-9_0_5_node_189 | 0.4 | n |  | TRUE
9 | bus_LV_297-9_0_5_node_175 | 0.4 | n |  | TRUE
10 | bus_LV_297-9_0_5_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_297-9_0_5_node_174 | 0.4 | n |  | TRUE
12 | bus_LV_297-9_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_297-9_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_297-9_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_297-9_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_297-9_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_297-9_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_297-9_0_5_node_93 | 0.4 | n |  | TRUE
19 | bus_LV_297-9_0_5_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_297-9_0_5_node_329 | 0.4 | n |  | TRUE
21 | bus_LV_297-9_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_297-9_0_5_node_120 | 0.4 | n |  | TRUE
23 | bus_LV_297-9_0_5_node_118 | 0.4 | n |  | TRUE
24 | bus_LV_297-9_0_5_node_92 | 0.4 | n |  | TRUE
25 | bus_LV_297-9_0_5_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_297-9_0_5_node_325 | 0.4 | n |  | TRUE
27 | bus_LV_297-9_0_5_node_121 | 0.4 | n |  | TRUE
28 | bus_LV_297-9_0_5_node_324 | 0.4 | n |  | TRUE
29 | bus_LV_297-9_0_5_node_134 | 0.4 | n |  | TRUE
30 | bus_LV_297-9_0_5_node_132 | 0.4 | n |  | TRUE
31 | bus_LV_297-9_0_5_node_119 | 0.4 | n |  | TRUE
32 | bus_LV_297-9_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_297-9_0_5_node_68 | 0.4 | n |  | TRUE
34 | bus_LV_297-9_0_5_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_297-9_0_5_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_297-9_0_5_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_297-9_0_5_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_297-9_0_5_node_138 | 0.4 | n |  | TRUE
39 | bus_LV_297-9_0_5_node_139 | 0.4 | n |  | TRUE
40 | bus_LV_297-9_0_5_node_137 | 0.4 | n |  | TRUE
41 | bus_LV_297-9_0_5_node_73 | 0.4 | n |  | TRUE
42 | bus_LV_297-9_0_5_node_74 | 0.4 | n |  | TRUE
43 | bus_LV_297-9_0_5_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_297-9_0_5_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_297-9_0_5_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_297-9_0_5_node_81 | 0.4 | n |  | TRUE
47 | bus_LV_297-9_0_5_node_79 | 0.4 | n |  | TRUE
48 | bus_LV_297-9_0_5_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_297-9_0_5_node_168 | 0.4 | n |  | TRUE
50 | bus_LV_297-9_0_5_node_84 | 0.4 | n |  | TRUE
51 | bus_LV_297-9_0_5_node_80 | 0.4 | n |  | TRUE
52 | bus_LV_297-9_0_5_node_218 | 0.4 | n |  | TRUE
53 | bus_LV_297-9_0_5_node_86 | 0.4 | n |  | TRUE
54 | bus_LV_297-9_0_5_node_83 | 0.4 | n |  | TRUE
55 | bus_LV_297-9_0_5_node_82 | 0.4 | n |  | TRUE
56 | bus_LV_297-9_0_5_node_305 | 0.4 | n |  | TRUE
57 | bus_LV_297-9_0_5_node_321 | 0.4 | n |  | TRUE
58 | bus_LV_297-9_0_5_node_207 | 0.4 | n |  | TRUE
59 | bus_LV_297-9_0_5_node_208 | 0.4 | n |  | TRUE
60 | bus_LV_297-9_0_5_node_209 | 0.4 | n |  | TRUE
61 | bus_LV_297-9_0_5_node_334 | 0.4 | n |  | TRUE
62 | bus_LV_297-9_0_5_node_302 | 0.4 | n |  | TRUE
63 | bus_LV_297-9_0_5_node_322 | 0.4 | n |  | TRUE
64 | bus_LV_297-9_0_5_node_85 | 0.4 | n |  | TRUE
65 | bus_LV_297-9_0_5_node_145 | 0.4 | n |  | TRUE
66 | bus_LV_297-9_0_5_node_146 | 0.4 | n |  | TRUE
67 | bus_LV_297-9_0_5_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_297-9_0_5_node_95 | 0.4 | n |  | TRUE
69 | bus_LV_297-9_0_5_node_122 | 0.4 | n |  | TRUE
70 | bus_LV_297-9_0_5_node_123 | 0.4 | n |  | TRUE
71 | bus_LV_297-9_0_5_node_148 | 0.4 | n |  | TRUE
72 | bus_LV_297-9_0_5_node_185 | 0.4 | n |  | TRUE
73 | bus_LV_297-9_0_5_node_153 | 0.4 | n |  | TRUE
74 | bus_LV_297-9_0_5_node_155 | 0.4 | n |  | TRUE
75 | bus_LV_297-9_0_5_node_152 | 0.4 | n |  | TRUE
76 | bus_LV_297-9_0_5_node_330 | 0.4 | n |  | TRUE
77 | bus_LV_297-9_0_5_node_133 | 0.4 | n |  | TRUE
78 | bus_LV_297-9_0_5_node_125 | 0.4 | n |  | TRUE
79 | bus_LV_297-9_0_5_node_126 | 0.4 | n |  | TRUE
80 | bus_LV_297-9_0_5_node_127 | 0.4 | n |  | TRUE
81 | bus_LV_297-9_0_5_node_128 | 0.4 | n |  | TRUE
82 | bus_LV_297-9_0_5_node_129 | 0.4 | n |  | TRUE
83 | bus_LV_297-9_0_5_node_130 | 0.4 | n |  | TRUE
84 | bus_LV_297-9_0_5_node_156 | 0.4 | n |  | TRUE
85 | bus_LV_297-9_0_5_node_149 | 0.4 | n |  | TRUE
86 | bus_LV_297-9_0_5_node_173 | 0.4 | n |  | TRUE
87 | bus_LV_297-9_0_5_node_172 | 0.4 | n |  | TRUE
88 | bus_LV_297-9_0_5_node_154 | 0.4 | n |  | TRUE
89 | bus_LV_297-9_0_5_node_150 | 0.4 | n |  | TRUE
90 | bus_LV_297-9_0_5_node_181 | 0.4 | n |  | TRUE
91 | bus_LV_297-9_0_5_node_135 | 0.4 | n |  | TRUE
92 | bus_LV_297-9_0_5_node_331 | 0.4 | n |  | TRUE
93 | bus_LV_297-9_0_5_node_332 | 0.4 | n |  | TRUE
94 | bus_LV_297-9_0_5_node_136 | 0.4 | n |  | TRUE
95 | bus_LV_297-9_0_5_node_320 | 0.4 | n |  | TRUE
96 | bus_LV_297-9_0_5_node_323 | 0.4 | n |  | TRUE
97 | bus_LV_297-9_0_5_node_319 | 0.4 | n |  | TRUE
98 | bus_LV_297-9_0_5_node_147 | 0.4 | n |  | TRUE
99 | bus_LV_297-9_0_5_node_268 | 0.4 | n |  | TRUE
100 | bus_LV_297-9_0_5_node_269 | 0.4 | n |  | TRUE
101 | bus_LV_297-9_0_5_node_186 | 0.4 | n |  | TRUE
102 | bus_LV_297-9_0_5_node_151 | 0.4 | n |  | TRUE
103 | bus_LV_297-9_0_5_node_292 | 0.4 | n |  | TRUE
104 | bus_LV_297-9_0_5_node_290 | 0.4 | n |  | TRUE
105 | bus_LV_297-9_0_5_node_220 | 0.4 | n |  | TRUE
106 | bus_LV_297-9_0_5_node_190 | 0.4 | n |  | TRUE
107 | bus_LV_297-9_0_5_node_191 | 0.4 | n |  | TRUE
108 | bus_LV_297-9_0_5_node_194 | 0.4 | n |  | TRUE
109 | bus_LV_297-9_0_5_node_195 | 0.4 | n |  | TRUE
110 | bus_LV_297-9_0_5_node_212 | 0.4 | n |  | TRUE
111 | bus_LV_297-9_0_5_node_199 | 0.4 | n |  | TRUE
112 | bus_LV_297-9_0_5_node_221 | 0.4 | n |  | TRUE
113 | bus_LV_297-9_0_5_node_197 | 0.4 | n |  | TRUE
114 | bus_LV_297-9_0_5_node_200 | 0.4 | n |  | TRUE
115 | bus_LV_297-9_0_5_node_196 | 0.4 | n |  | TRUE
116 | bus_LV_297-9_0_5_node_201 | 0.4 | n |  | TRUE
117 | bus_LV_297-9_0_5_node_198 | 0.4 | n |  | TRUE
118 | bus_LV_297-9_0_5_node_210 | 0.4 | n |  | TRUE
119 | bus_LV_297-9_0_5_node_202 | 0.4 | n |  | TRUE
120 | bus_LV_297-9_0_5_node_203 | 0.4 | n |  | TRUE
121 | bus_LV_297-9_0_5_node_204 | 0.4 | n |  | TRUE
122 | bus_LV_297-9_0_5_node_205 | 0.4 | n |  | TRUE
123 | bus_LV_297-9_0_5_node_206 | 0.4 | n |  | TRUE
124 | bus_LV_297-9_0_5_node_224 | 0.4 | n |  | TRUE
125 | bus_LV_297-9_0_5_node_225 | 0.4 | n |  | TRUE
126 | bus_LV_297-9_0_5_node_228 | 0.4 | n |  | TRUE
127 | bus_LV_297-9_0_5_node_223 | 0.4 | n |  | TRUE
128 | bus_LV_297-9_0_5_node_226 | 0.4 | n |  | TRUE
129 | bus_LV_297-9_0_5_node_216 | 0.4 | n |  | TRUE
130 | bus_LV_297-9_0_5_node_284 | 0.4 | n |  | TRUE
131 | bus_LV_297-9_0_5_node_222 | 0.4 | n |  | TRUE
132 | bus_LV_297-9_0_5_node_215 | 0.4 | n |  | TRUE
133 | bus_LV_297-9_0_5_node_282 | 0.4 | n |  | TRUE
134 | bus_LV_297-9_0_5_node_211 | 0.4 | n |  | TRUE
135 | bus_LV_297-9_0_5_node_213 | 0.4 | n |  | TRUE
136 | bus_LV_297-9_0_5_node_214 | 0.4 | n |  | TRUE
137 | bus_LV_297-9_0_5_node_217 | 0.4 | n |  | TRUE
138 | bus_LV_297-9_0_5_node_219 | 0.4 | n |  | TRUE
139 | bus_LV_297-9_0_5_node_262 | 0.4 | n |  | TRUE
140 | bus_LV_297-9_0_5_node_259 | 0.4 | n |  | TRUE
141 | bus_LV_297-9_0_5_node_256 | 0.4 | n |  | TRUE
142 | bus_LV_297-9_0_5_node_260 | 0.4 | n |  | TRUE
143 | bus_LV_297-9_0_5_node_271 | 0.4 | n |  | TRUE
144 | bus_LV_297-9_0_5_node_257 | 0.4 | n |  | TRUE
145 | bus_LV_297-9_0_5_node_227 | 0.4 | n |  | TRUE
146 | bus_LV_297-9_0_5_node_278 | 0.4 | n |  | TRUE
147 | bus_LV_297-9_0_5_node_276 | 0.4 | n |  | TRUE
148 | bus_LV_297-9_0_5_node_258 | 0.4 | n |  | TRUE
149 | bus_LV_297-9_0_5_node_272 | 0.4 | n |  | TRUE
150 | bus_LV_297-9_0_5_node_263 | 0.4 | n |  | TRUE
151 | bus_LV_297-9_0_5_node_264 | 0.4 | n |  | TRUE
152 | bus_LV_297-9_0_5_node_265 | 0.4 | n |  | TRUE
153 | bus_LV_297-9_0_5_node_266 | 0.4 | n |  | TRUE
154 | bus_LV_297-9_0_5_node_267 | 0.4 | n |  | TRUE
155 | bus_LV_297-9_0_5_node_274 | 0.4 | n |  | TRUE
156 | bus_LV_297-9_0_5_node_275 | 0.4 | n |  | TRUE
157 | bus_LV_297-9_0_5_node_279 | 0.4 | n |  | TRUE
158 | bus_LV_297-9_0_5_node_280 | 0.4 | n |  | TRUE
159 | bus_LV_297-9_0_5_node_281 | 0.4 | n |  | TRUE
160 | bus_LV_297-9_0_5_node_288 | 0.4 | n |  | TRUE
161 | bus_LV_297-9_0_5_node_298 | 0.4 | n |  | TRUE
162 | bus_LV_297-9_0_5_node_309 | 0.4 | n |  | TRUE
163 | bus_LV_297-9_0_5_node_283 | 0.4 | n |  | TRUE
164 | bus_LV_297-9_0_5_node_285 | 0.4 | n |  | TRUE
165 | bus_LV_297-9_0_5_node_306 | 0.4 | n |  | TRUE
166 | bus_LV_297-9_0_5_node_310 | 0.4 | n |  | TRUE
167 | bus_LV_297-9_0_5_node_286 | 0.4 | n |  | TRUE
168 | bus_LV_297-9_0_5_node_295 | 0.4 | n |  | TRUE
169 | bus_LV_297-9_0_5_node_308 | 0.4 | n |  | TRUE
170 | bus_LV_297-9_0_5_node_311 | 0.4 | n |  | TRUE
171 | bus_LV_297-9_0_5_node_287 | 0.4 | n |  | TRUE
172 | bus_LV_297-9_0_5_node_293 | 0.4 | n |  | TRUE
173 | bus_LV_297-9_0_5_node_304 | 0.4 | n |  | TRUE
174 | bus_LV_297-9_0_5_node_291 | 0.4 | n |  | TRUE
175 | bus_LV_297-9_0_5_node_294 | 0.4 | n |  | TRUE
176 | bus_LV_297-9_0_5_node_289 | 0.4 | n |  | TRUE
177 | bus_LV_297-9_0_5_node_299 | 0.4 | n |  | TRUE
178 | bus_LV_297-9_0_5_node_307 | 0.4 | n |  | TRUE
179 | bus_LV_297-9_0_5_node_312 | 0.4 | n |  | TRUE
180 | bus_LV_297-9_0_5_node_297 | 0.4 | n |  | TRUE
181 | bus_LV_297-9_0_5_node_300 | 0.4 | n |  | TRUE
182 | bus_LV_297-9_0_5_node_301 | 0.4 | n |  | TRUE
183 | bus_LV_297-9_0_5_node_303 | 0.4 | n |  | TRUE
184 | bus_LV_297-9_0_5_node_313 | 0.4 | n |  | TRUE
185 | bus_LV_297-9_0_5_node_314 | 0.4 | n |  | TRUE
186 | bus_LV_297-9_0_5_node_315 | 0.4 | n |  | TRUE
187 | bus_LV_297-9_0_5_node_317 | 0.4 | n |  | TRUE
188 | bus_LV_297-9_0_5_node_318 | 0.4 | n |  | TRUE
189 | bus_MV_7_0_node_199 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_297-9_0_5_load_0 | 0 | 0.00065662 | 0.00016456 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_297-9_0_5_load_5 | 5 | 0.00053293 | 0.00013356 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_297-9_0_5_load_25 | 7 | 0.00053025 | 0.00013289 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_297-9_0_5_load_189 | 8 | 0.0013019 | 0.00032629 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_297-9_0_5_load_175 | 9 | 0.00013435 | 3.367e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_297-9_0_5_load_23 | 10 | 0.0012236 | 0.00030666 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_297-9_0_5_load_174 | 11 | 0.0001636 | 4.1002e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_297-9_0_5_load_7 | 12 | 0.00043624 | 0.00010933 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_297-9_0_5_load_10 | 15 | 0.00017525 | 4.3922e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_297-9_0_5_load_93 | 18 | 0.00025619 | 6.4206e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_297-9_0_5_load_329 | 20 | 4.826e-05 | 1.2095e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_297-9_0_5_load_118 | 23 | 0.00018206 | 4.5629e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_297-9_0_5_load_92 | 24 | 0.00013521 | 3.3886e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_297-9_0_5_load_19 | 25 | 0.00026952 | 6.7548e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_297-9_0_5_load_325 | 26 | 0.0002205 | 5.5262e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_297-9_0_5_load_324 | 28 | 0.00030166 | 7.5604e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_297-9_0_5_load_132 | 30 | 0.0002916 | 7.3082e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_297-9_0_5_load_119 | 31 | 0.00099006 | 0.00024813 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_297-9_0_5_load_22 | 32 | 0.0011947 | 0.00029942 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_297-9_0_5_load_68 | 33 | 0.00055101 | 0.0001381 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_297-9_0_5_load_69 | 34 | 0.00011883 | 2.9783e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_297-9_0_5_load_70 | 35 | 9.9342e-05 | 2.4897e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_297-9_0_5_load_71 | 36 | 0.00027712 | 6.9452e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_297-9_0_5_load_137 | 40 | 0.00016912 | 4.2387e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_297-9_0_5_load_73 | 41 | 0.00045323 | 0.00011359 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_297-9_0_5_load_74 | 42 | 0.00023718 | 5.9443e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_297-9_0_5_load_78 | 45 | 0.00020275 | 5.0814e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_297-9_0_5_load_81 | 46 | 6.3533e-05 | 1.5923e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_297-9_0_5_load_79 | 47 | 0.00020961 | 5.2534e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_297-9_0_5_load_168 | 49 | 0.00021109 | 5.2905e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_297-9_0_5_load_83 | 54 | 0.00062677 | 0.00015708 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_297-9_0_5_load_321 | 57 | 0.0001193 | 2.9901e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_297-9_0_5_load_207 | 58 | 0.00060726 | 0.00015219 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_297-9_0_5_load_208 | 59 | 0.00041914 | 0.00010505 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_297-9_0_5_load_334 | 61 | 0.00033879 | 8.4908e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_297-9_0_5_load_85 | 64 | 0.00024203 | 6.0657e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_297-9_0_5_load_145 | 65 | 0.00021676 | 5.4324e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_297-9_0_5_load_94 | 67 | 4.9544e-05 | 1.2417e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_297-9_0_5_load_95 | 68 | 4.3338e-05 | 1.0862e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_297-9_0_5_load_123 | 70 | 7.5111e-05 | 1.8825e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_297-9_0_5_load_185 | 72 | 0.00020513 | 5.141e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_297-9_0_5_load_152 | 75 | 4.8426e-05 | 1.2137e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_297-9_0_5_load_330 | 76 | 5.686e-05 | 1.4251e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_297-9_0_5_load_125 | 78 | 0.00049789 | 0.00012478 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_297-9_0_5_load_128 | 81 | 0.00052703 | 0.00013208 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_297-9_0_5_load_129 | 82 | 0.0035866 | 0.00089889 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_297-9_0_5_load_149 | 85 | 0.00073112 | 0.00018324 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_297-9_0_5_load_172 | 87 | 0.00062863 | 0.00015755 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_297-9_0_5_load_150 | 89 | 0.0011604 | 0.00029083 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_297-9_0_5_load_181 | 90 | 9.5162e-05 | 2.385e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_297-9_0_5_load_331 | 92 | 0.00010923 | 2.7377e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_297-9_0_5_load_332 | 93 | 0.000115 | 2.8822e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_297-9_0_5_load_136 | 94 | 6.7261e-05 | 1.6857e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_297-9_0_5_load_320 | 95 | 0.00019255 | 4.8257e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_297-9_0_5_load_323 | 96 | 0.0001896 | 4.7519e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_297-9_0_5_load_319 | 97 | 0.00013534 | 3.3919e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_297-9_0_5_load_147 | 98 | 9.8034e-05 | 2.457e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_297-9_0_5_load_268 | 99 | 0.00017221 | 4.316e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_297-9_0_5_load_186 | 101 | 5.9597e-05 | 1.4936e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_297-9_0_5_load_151 | 102 | 0.00062 | 0.00015539 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_297-9_0_5_load_292 | 103 | 0.0019847 | 0.00049741 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_297-9_0_5_load_190 | 106 | 0.0033736 | 0.00084549 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_297-9_0_5_load_194 | 108 | 0.00098909 | 0.00024789 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_297-9_0_5_load_195 | 109 | 0.0013302 | 0.00033338 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_297-9_0_5_load_221 | 112 | 0.00036072 | 9.0406e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_297-9_0_5_load_200 | 114 | 0.00096547 | 0.00024197 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_297-9_0_5_load_196 | 115 | 0.00068538 | 0.00017177 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_297-9_0_5_load_201 | 116 | 0.0017169 | 0.00043031 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_297-9_0_5_load_210 | 118 | 0.000773 | 0.00019373 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_297-9_0_5_load_202 | 119 | 0.00046009 | 0.00011531 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_297-9_0_5_load_206 | 123 | 0.0017362 | 0.00043512 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_297-9_0_5_load_224 | 124 | 0.0006561 | 0.00016443 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_297-9_0_5_load_225 | 125 | 0.0019542 | 0.00048978 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_297-9_0_5_load_226 | 128 | 0.001982 | 0.00049673 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_297-9_0_5_load_284 | 130 | 0.00066321 | 0.00016622 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_297-9_0_5_load_222 | 131 | 0.00039536 | 9.9087e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_297-9_0_5_load_282 | 133 | 0.00097948 | 0.00024548 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_297-9_0_5_load_213 | 135 | 0.00089756 | 0.00022495 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_297-9_0_5_load_214 | 136 | 0.00079683 | 0.0001997 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_297-9_0_5_load_217 | 137 | 0.0030887 | 0.00077409 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_297-9_0_5_load_219 | 138 | 8.4629e-05 | 2.121e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_297-9_0_5_load_259 | 140 | 0.00039104 | 9.8004e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_297-9_0_5_load_256 | 141 | 0.00024367 | 6.1069e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_297-9_0_5_load_260 | 142 | 0.001362 | 0.00034135 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_297-9_0_5_load_271 | 143 | 0.0001113 | 2.7895e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_297-9_0_5_load_257 | 144 | 0.00014836 | 3.7183e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_297-9_0_5_load_227 | 145 | 0.0016795 | 0.00042093 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_297-9_0_5_load_276 | 147 | 0.00010526 | 2.638e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_297-9_0_5_load_258 | 148 | 0.00010442 | 2.617e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_297-9_0_5_load_272 | 149 | 0.00017073 | 4.2788e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_297-9_0_5_load_263 | 150 | 0.00018536 | 4.6456e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_297-9_0_5_load_264 | 151 | 0.00062344 | 0.00015625 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_297-9_0_5_load_265 | 152 | 0.00026036 | 6.5253e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_297-9_0_5_load_274 | 155 | 7.3272e-05 | 1.8364e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_297-9_0_5_load_275 | 156 | 8.2368e-05 | 2.0643e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_297-9_0_5_load_279 | 157 | 0.00032594 | 8.1687e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_297-9_0_5_load_280 | 158 | 0.00030701 | 7.6945e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_297-9_0_5_load_298 | 161 | 0.0005171 | 0.0001296 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_297-9_0_5_load_309 | 162 | 0.00051713 | 0.0001296 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_297-9_0_5_load_310 | 166 | 0.0014697 | 0.00036834 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_297-9_0_5_load_308 | 169 | 0.0004168 | 0.00010446 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_297-9_0_5_load_311 | 170 | 0.00071017 | 0.00017798 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_297-9_0_5_load_293 | 172 | 0.0010479 | 0.00026262 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_297-9_0_5_load_304 | 173 | 0.0018292 | 0.00045843 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_297-9_0_5_load_289 | 176 | 0.00057675 | 0.00014455 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_297-9_0_5_load_299 | 177 | 0.00093334 | 0.00023392 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_297-9_0_5_load_307 | 178 | 0.00081867 | 0.00020518 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_297-9_0_5_load_312 | 179 | 0.00059956 | 0.00015026 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_297-9_0_5_load_297 | 180 | 0.00051701 | 0.00012958 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_297-9_0_5_load_300 | 181 | 0.00036834 | 9.2314e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_297-9_0_5_load_301 | 182 | 0.00063166 | 0.00015831 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_297-9_0_5_load_303 | 183 | 0.00060183 | 0.00015083 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_297-9_0_5_load_313 | 184 | 0.00050901 | 0.00012757 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_297-9_0_5_load_314 | 185 | 0.050082 | 0.012552 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_297-9_0_5_load_315 | 186 | 0.043294 | 0.010851 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_297-9_0_5_load_317 | 187 | 7.8305e-05 | 1.9625e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_297-9_0_5_load_318 | 188 | 0.0001332 | 3.3383e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 160 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_297-9_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_297-9_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.063975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_297-9_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.047457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_297-9_0_5_line_3 | NAYY 4x150 SE | 1 | 4 | 0.017512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_297-9_0_5_line_4 | NAYY 4x150 SE | 1 | 5 | 0.039238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_297-9_0_5_line_5 | NAYY 4x150 SE | 2 | 6 | 0.37641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_297-9_0_5_line_6 | NAYY 4x150 SE | 3 | 7 | 0.022853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_297-9_0_5_line_7 | NAYY 4x150 SE | 4 | 8 | 0.040905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_297-9_0_5_line_8 | NAYY 4x150 SE | 6 | 9 | 0.053225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_297-9_0_5_line_9 | NAYY 4x150 SE | 7 | 10 | 0.02167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_297-9_0_5_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_297-9_0_5_line_11 | NAYY 4x150 SE | 10 | 32 | 0.14351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_297-9_0_5_line_12 | NAYY 4x150 SE | 11 | 17 | 0.046599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_297-9_0_5_line_13 | NAYY 4x150 SE | 12 | 13 | 0.018729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_297-9_0_5_line_14 | NAYY 4x150 SE | 12 | 14 | 0.09383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_297-9_0_5_line_15 | NAYY 4x150 SE | 13 | 15 | 0.018218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_297-9_0_5_line_16 | NAYY 4x150 SE | 14 | 16 | 0.1769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_297-9_0_5_line_17 | NAYY 4x150 SE | 14 | 17 | 0.13983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_297-9_0_5_line_18 | NAYY 4x150 SE | 15 | 18 | 0.011442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_297-9_0_5_line_19 | NAYY 4x150 SE | 16 | 20 | 0.030025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_297-9_0_5_line_20 | NAYY 4x150 SE | 16 | 21 | 0.25945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_297-9_0_5_line_21 | NAYY 4x150 SE | 17 | 19 | 0.26127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_297-9_0_5_line_22 | NAYY 4x150 SE | 18 | 24 | 0.0075308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_297-9_0_5_line_23 | NAYY 4x150 SE | 19 | 25 | 0.0050793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_297-9_0_5_line_24 | NAYY 4x150 SE | 21 | 22 | 0.11387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_297-9_0_5_line_25 | NAYY 4x150 SE | 21 | 23 | 0.028183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_297-9_0_5_line_26 | NAYY 4x150 SE | 22 | 26 | 0.02722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_297-9_0_5_line_27 | NAYY 4x150 SE | 22 | 27 | 0.077594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_297-9_0_5_line_28 | NAYY 4x150 SE | 22 | 28 | 0.089596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_297-9_0_5_line_29 | NAYY 4x150 SE | 23 | 31 | 0.055955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_297-9_0_5_line_30 | NAYY 4x150 SE | 24 | 67 | 0.011718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_297-9_0_5_line_31 | NAYY 4x150 SE | 27 | 29 | 0.02095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_297-9_0_5_line_32 | NAYY 4x150 SE | 27 | 30 | 0.050197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_297-9_0_5_line_33 | NAYY 4x150 SE | 28 | 74 | 0.14915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_297-9_0_5_line_34 | NAYY 4x150 SE | 29 | 76 | 0.025728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_297-9_0_5_line_35 | NAYY 4x150 SE | 30 | 77 | 0.19806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_297-9_0_5_line_36 | NAYY 4x150 SE | 33 | 34 | 0.0014223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_297-9_0_5_line_37 | NAYY 4x150 SE | 33 | 35 | 0.012123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_297-9_0_5_line_38 | NAYY 4x150 SE | 34 | 36 | 0.007288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_297-9_0_5_line_39 | NAYY 4x150 SE | 35 | 37 | 0.070664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_297-9_0_5_line_40 | NAYY 4x150 SE | 37 | 38 | 0.063876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_297-9_0_5_line_41 | NAYY 4x150 SE | 38 | 39 | 0.089728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_297-9_0_5_line_42 | NAYY 4x150 SE | 38 | 40 | 0.02062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_297-9_0_5_line_43 | NAYY 4x150 SE | 39 | 95 | 0.007412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_297-9_0_5_line_44 | NAYY 4x150 SE | 39 | 96 | 0.050853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_297-9_0_5_line_45 | NAYY 4x150 SE | 40 | 94 | 0.01166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_297-9_0_5_line_46 | NAYY 4x150 SE | 41 | 42 | 0.062573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_297-9_0_5_line_47 | NAYY 4x150 SE | 41 | 43 | 0.023689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_297-9_0_5_line_48 | NAYY 4x150 SE | 42 | 44 | 0.024863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_297-9_0_5_line_49 | NAYY 4x150 SE | 43 | 45 | 0.025962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_297-9_0_5_line_50 | NAYY 4x150 SE | 44 | 46 | 0.055466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_297-9_0_5_line_51 | NAYY 4x150 SE | 44 | 47 | 0.0036519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_297-9_0_5_line_52 | NAYY 4x150 SE | 45 | 50 | 0.088319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_297-9_0_5_line_53 | NAYY 4x150 SE | 46 | 48 | 0.10898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_297-9_0_5_line_54 | NAYY 4x150 SE | 47 | 51 | 0.030676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_297-9_0_5_line_55 | NAYY 4x150 SE | 48 | 49 | 0.051378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_297-9_0_5_line_56 | NAYY 4x150 SE | 49 | 52 | 0.03387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_297-9_0_5_line_57 | NAYY 4x150 SE | 50 | 53 | 0.012243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_297-9_0_5_line_58 | NAYY 4x150 SE | 50 | 54 | 0.039877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_297-9_0_5_line_59 | NAYY 4x150 SE | 51 | 55 | 0.026325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_297-9_0_5_line_60 | NAYY 4x150 SE | 52 | 105 | 0.065364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_297-9_0_5_line_61 | NAYY 4x150 SE | 53 | 65 | 0.11052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_297-9_0_5_line_62 | NAYY 4x150 SE | 54 | 64 | 0.0010477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_297-9_0_5_line_63 | NAYY 4x150 SE | 55 | 56 | 0.28822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_297-9_0_5_line_64 | NAYY 4x150 SE | 55 | 57 | 0.037061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_297-9_0_5_line_65 | NAYY 4x150 SE | 56 | 61 | 0.13581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_297-9_0_5_line_66 | NAYY 4x150 SE | 56 | 62 | 0.073661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_297-9_0_5_line_67 | NAYY 4x150 SE | 57 | 63 | 0.011697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_297-9_0_5_line_68 | NAYY 4x150 SE | 58 | 59 | 0.32211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_297-9_0_5_line_69 | NAYY 4x150 SE | 58 | 60 | 0.27391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_297-9_0_5_line_70 | NAYY 4x150 SE | 59 | 129 | 0.3069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_297-9_0_5_line_71 | NAYY 4x150 SE | 60 | 130 | 0.1059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_297-9_0_5_line_72 | NAYY 4x150 SE | 62 | 173 | 0.027238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_297-9_0_5_line_73 | NAYY 4x150 SE | 62 | 182 | 0.0045209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_297-9_0_5_line_74 | NAYY 4x150 SE | 63 | 96 | 0.025876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_297-9_0_5_line_75 | NAYY 4x150 SE | 65 | 66 | 0.0088203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_297-9_0_5_line_76 | NAYY 4x150 SE | 66 | 98 | 0.15025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_297-9_0_5_line_77 | NAYY 4x150 SE | 66 | 71 | 0.1985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_297-9_0_5_line_78 | NAYY 4x150 SE | 67 | 68 | 0.006514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_297-9_0_5_line_79 | NAYY 4x150 SE | 68 | 69 | 0.0092149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_297-9_0_5_line_80 | NAYY 4x150 SE | 69 | 70 | 0.014909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_297-9_0_5_line_81 | NAYY 4x150 SE | 71 | 72 | 0.028386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_297-9_0_5_line_82 | NAYY 4x150 SE | 72 | 101 | 0.012467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_297-9_0_5_line_83 | NAYY 4x150 SE | 73 | 74 | 0.14577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_297-9_0_5_line_84 | NAYY 4x150 SE | 73 | 75 | 0.010546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_297-9_0_5_line_85 | NAYY 4x150 SE | 75 | 88 | 0.1154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_297-9_0_5_line_86 | NAYY 4x150 SE | 77 | 91 | 0.023227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_297-9_0_5_line_87 | NAYY 4x150 SE | 78 | 79 | 0.049714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_297-9_0_5_line_88 | NAYY 4x150 SE | 78 | 80 | 0.010904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_297-9_0_5_line_89 | NAYY 4x150 SE | 79 | 81 | 0.022763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_297-9_0_5_line_90 | NAYY 4x150 SE | 80 | 82 | 0.035849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_297-9_0_5_line_91 | NAYY 4x150 SE | 80 | 83 | 0.018289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_297-9_0_5_line_92 | NAYY 4x150 SE | 81 | 84 | 0.011374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_297-9_0_5_line_93 | NAYY 4x150 SE | 82 | 85 | 0.041259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_297-9_0_5_line_94 | NAYY 4x150 SE | 83 | 86 | 0.031924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_297-9_0_5_line_95 | NAYY 4x150 SE | 83 | 87 | 0.032563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_297-9_0_5_line_96 | NAYY 4x150 SE | 84 | 88 | 0.20661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_297-9_0_5_line_97 | NAYY 4x150 SE | 85 | 89 | 0.045195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_297-9_0_5_line_98 | NAYY 4x150 SE | 86 | 90 | 0.15903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_297-9_0_5_line_99 | NAYY 4x150 SE | 89 | 102 | 0.018145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_297-9_0_5_line_100 | NAYY 4x150 SE | 91 | 92 | 0.05295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_297-9_0_5_line_101 | NAYY 4x150 SE | 91 | 93 | 0.038695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_297-9_0_5_line_102 | NAYY 4x150 SE | 95 | 97 | 0.011073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_297-9_0_5_line_103 | NAYY 4x150 SE | 97 | 188 | 0.00054672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_297-9_0_5_line_104 | NAYY 4x150 SE | 98 | 99 | 0.0090001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_297-9_0_5_line_105 | NAYY 4x150 SE | 99 | 100 | 0.017545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_297-9_0_5_line_106 | NAYY 4x150 SE | 100 | 153 | 0.044251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_297-9_0_5_line_107 | NAYY 4x150 SE | 102 | 103 | 0.0087254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_297-9_0_5_line_108 | NAYY 4x150 SE | 103 | 104 | 0.015817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_297-9_0_5_line_109 | NAYY 4x150 SE | 104 | 172 | 0.0030745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_297-9_0_5_line_110 | NAYY 4x150 SE | 104 | 176 | 0.016366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_297-9_0_5_line_111 | NAYY 4x150 SE | 105 | 140 | 0.026568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_297-9_0_5_line_112 | NAYY 4x150 SE | 105 | 141 | 0.062177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_297-9_0_5_line_113 | NAYY 4x150 SE | 106 | 107 | 0.016013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_297-9_0_5_line_114 | NAYY 4x150 SE | 107 | 108 | 0.024119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_297-9_0_5_line_115 | NAYY 4x150 SE | 107 | 109 | 0.26537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_297-9_0_5_line_116 | NAYY 4x150 SE | 109 | 110 | 0.10913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_297-9_0_5_line_117 | NAYY 4x150 SE | 110 | 114 | 0.091526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_297-9_0_5_line_118 | NAYY 4x150 SE | 110 | 118 | 0.12991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_297-9_0_5_line_119 | NAYY 4x150 SE | 111 | 112 | 0.0044627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_297-9_0_5_line_120 | NAYY 4x150 SE | 111 | 113 | 0.032349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_297-9_0_5_line_121 | NAYY 4x150 SE | 113 | 114 | 0.33664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_297-9_0_5_line_122 | NAYY 4x150 SE | 113 | 115 | 0.008626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_297-9_0_5_line_123 | NAYY 4x150 SE | 115 | 117 | 0.019402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_297-9_0_5_line_124 | NAYY 4x150 SE | 116 | 117 | 0.014045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_297-9_0_5_line_125 | NAYY 4x150 SE | 118 | 134 | 0.0068202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_297-9_0_5_line_126 | NAYY 4x150 SE | 119 | 120 | 0.14779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
127 | LV_297-9_0_5_line_127 | NAYY 4x150 SE | 119 | 121 | 0.022154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_297-9_0_5_line_128 | NAYY 4x150 SE | 120 | 122 | 0.36347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_297-9_0_5_line_129 | NAYY 4x150 SE | 121 | 123 | 0.015778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_297-9_0_5_line_130 | NAYY 4x150 SE | 122 | 124 | 0.12038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_297-9_0_5_line_131 | NAYY 4x150 SE | 122 | 125 | 0.04417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_297-9_0_5_line_132 | NAYY 4x150 SE | 123 | 126 | 0.36151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_297-9_0_5_line_133 | NAYY 4x150 SE | 124 | 127 | 0.025632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
134 | LV_297-9_0_5_line_134 | NAYY 4x150 SE | 126 | 128 | 0.067747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_297-9_0_5_line_135 | NAYY 4x150 SE | 127 | 137 | 0.036625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
136 | LV_297-9_0_5_line_136 | NAYY 4x150 SE | 128 | 145 | 0.092385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_297-9_0_5_line_137 | NAYY 4x150 SE | 129 | 131 | 0.27959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
138 | LV_297-9_0_5_line_138 | NAYY 4x150 SE | 129 | 132 | 0.098812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
139 | LV_297-9_0_5_line_139 | NAYY 4x150 SE | 130 | 133 | 0.01647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
140 | LV_297-9_0_5_line_140 | NAYY 4x150 SE | 131 | 135 | 0.0070487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
141 | LV_297-9_0_5_line_141 | NAYY 4x150 SE | 132 | 137 | 0.038379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
142 | LV_297-9_0_5_line_142 | NAYY 4x150 SE | 132 | 136 | 0.038646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_297-9_0_5_line_143 | NAYY 4x150 SE | 133 | 163 | 0.027239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
144 | LV_297-9_0_5_line_144 | NAYY 4x150 SE | 134 | 135 | 0.0039273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_297-9_0_5_line_145 | NAYY 4x150 SE | 138 | 139 | 0.29278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_297-9_0_5_line_146 | NAYY 4x150 SE | 139 | 142 | 0.018821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_297-9_0_5_line_147 | NAYY 4x150 SE | 141 | 144 | 0.001203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_297-9_0_5_line_148 | NAYY 4x150 SE | 142 | 143 | 0.2217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_297-9_0_5_line_149 | NAYY 4x150 SE | 143 | 149 | 0.034048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_297-9_0_5_line_150 | NAYY 4x150 SE | 144 | 148 | 0.0064913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_297-9_0_5_line_151 | NAYY 4x150 SE | 145 | 146 | 0.23056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_297-9_0_5_line_152 | NAYY 4x150 SE | 146 | 147 | 0.019482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_297-9_0_5_line_153 | NAYY 4x150 SE | 147 | 156 | 0.013037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_297-9_0_5_line_154 | NAYY 4x150 SE | 149 | 155 | 0.0086027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_297-9_0_5_line_155 | NAYY 4x150 SE | 150 | 151 | 0.0048784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_297-9_0_5_line_156 | NAYY 4x150 SE | 150 | 152 | 0.015121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_297-9_0_5_line_157 | NAYY 4x150 SE | 151 | 153 | 0.021952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_297-9_0_5_line_158 | NAYY 4x150 SE | 152 | 154 | 0.018335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_297-9_0_5_line_159 | NAYY 4x150 SE | 154 | 155 | 0.13225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_297-9_0_5_line_160 | NAYY 4x150 SE | 157 | 158 | 0.031673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_297-9_0_5_line_161 | NAYY 4x150 SE | 158 | 159 | 0.073646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_297-9_0_5_line_162 | NAYY 4x150 SE | 159 | 160 | 0.28444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_297-9_0_5_line_163 | NAYY 4x150 SE | 160 | 161 | 0.011132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_297-9_0_5_line_164 | NAYY 4x150 SE | 160 | 162 | 0.0083879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
165 | LV_297-9_0_5_line_165 | NAYY 4x150 SE | 161 | 180 | 0.0081486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_297-9_0_5_line_166 | NAYY 4x150 SE | 162 | 178 | 0.030457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
167 | LV_297-9_0_5_line_167 | NAYY 4x150 SE | 163 | 164 | 0.045048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
168 | LV_297-9_0_5_line_168 | NAYY 4x150 SE | 164 | 165 | 0.025055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_297-9_0_5_line_169 | NAYY 4x150 SE | 164 | 166 | 0.015571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
170 | LV_297-9_0_5_line_170 | NAYY 4x150 SE | 165 | 173 | 0.055508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
171 | LV_297-9_0_5_line_171 | NAYY 4x150 SE | 166 | 171 | 0.0058401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
172 | LV_297-9_0_5_line_172 | NAYY 4x150 SE | 167 | 168 | 0.055365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
173 | LV_297-9_0_5_line_173 | NAYY 4x150 SE | 167 | 169 | 0.021773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
174 | LV_297-9_0_5_line_174 | NAYY 4x150 SE | 167 | 170 | 0.12423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
175 | LV_297-9_0_5_line_175 | NAYY 4x150 SE | 168 | 177 | 0.010338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
176 | LV_297-9_0_5_line_176 | NAYY 4x150 SE | 168 | 175 | 0.006949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
177 | LV_297-9_0_5_line_177 | NAYY 4x150 SE | 169 | 178 | 0.014982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
178 | LV_297-9_0_5_line_178 | NAYY 4x150 SE | 170 | 179 | 0.035524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
179 | LV_297-9_0_5_line_179 | NAYY 4x150 SE | 171 | 172 | 0.025596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
180 | LV_297-9_0_5_line_180 | NAYY 4x150 SE | 174 | 175 | 0.007151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
181 | LV_297-9_0_5_line_181 | NAYY 4x150 SE | 174 | 176 | 0.036066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
182 | LV_297-9_0_5_line_182 | NAYY 4x150 SE | 175 | 181 | 0.012683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
183 | LV_297-9_0_5_line_183 | NAYY 4x150 SE | 179 | 184 | 0.014516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
184 | LV_297-9_0_5_line_184 | NAYY 4x150 SE | 182 | 183 | 0.041881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
185 | LV_297-9_0_5_line_185 | NAYY 4x150 SE | 184 | 185 | 0.042986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
186 | LV_297-9_0_5_line_186 | NAYY 4x150 SE | 185 | 186 | 0.031845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
187 | LV_297-9_0_5_line_187 | NAYY 4x150 SE | 187 | 188 | 0.019227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_297-9_0_5_trafo_288 | 0.25 MVA 20/0.4 kV | 189 | 160 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61 | x62 | y62 | x63 | y63 | x64 | y64 | x65 | y65 | x66 | y66 | x67 | y67 | x68 | y68 | x69 | y69 | x70 | y70 | x71 | y71 | x72 | y72 | x73 | y73 | x74 | y74 | x75 | y75 | x76 | y76 | x77 | y77 | x78 | y78 | x79 | y79 | x80 | y80 | x81 | y81 | x82 | y82 | x83 | y83 | x84 | y84 | x85 | y85 | x86 | y86 | x87 | y87 | x88 | y88 | x89 | y89 | x90 | y90 | x91 | y91 | x92 | y92 | x93 | y93 | x94 | y94 | x95 | y95 | x96 | y96 | x97 | y97 | x98 | y98
0 | 2711080.1052 | 1248644.1749 | 2711073.3605 | 1248645.7721 | 2711067.7632 | 1248645.9127
1 | 2711008.0764 | 1248627.7235 | 2711014.8353 | 1248630.608 | 2711027.3632 | 1248637.615 | 2711047.2518 | 1248646.428 | 2711067.7632 | 1248645.9127
2 | 2711080.1052 | 1248644.1749 | 2711067.9449 | 1248640.9334 | 2711043.8244 | 1248635.0545 | 2711039.2304 | 1248630.7094 | 2711039.2267 | 1248626.8729
3 | 2711080.1052 | 1248644.1749 | 2711078.3962 | 1248661.6016
4 | 2711080.1052 | 1248644.1749 | 2711091.6057 | 1248642.3223 | 2711096.9015 | 1248643.478 | 2711110.2435 | 1248648.9547 | 2711117.3311 | 1248652.08
5 | 2710668.3409 | 1248757.0442 | 2710674.0447 | 1248748.4881 | 2710692.2957 | 1248740.2555 | 2710706.8283 | 1248730.9304 | 2710717.7649 | 1248726.0973 | 2710731.4921 | 1248724.3078 | 2710739.9566 | 1248720.8075 | 2710777.4756 | 1248700.8699 | 2710815.3054 | 1248692.1921 | 2710832.9251 | 1248685.8273 | 2710858.6277 | 1248668.9163 | 2710866.9278 | 1248664.5235 | 2710879.2285 | 1248661.073 | 2710913.4472 | 1248656.4871 | 2710928.1809 | 1248652.5929 | 2710934.3887 | 1248649.8179 | 2710943.799 | 1248642.6103 | 2710965.0204 | 1248625.4379 | 2710971.6279 | 1248621.4917 | 2710980.2879 | 1248620.4752 | 2710992.4215 | 1248622.7264 | 2711008.0764 | 1248627.7235
6 | 2711039.2267 | 1248626.8729 | 2711042.4584 | 1248623.7086 | 2711049.8618 | 1248619.2102 | 2711058.9826 | 1248616.0048
7 | 2711078.3962 | 1248661.6016 | 2711075.8385 | 1248661.4535 | 2711063.6291 | 1248661.6361 | 2711037.5108 | 1248662.4803
8 | 2710668.3409 | 1248757.0442 | 2710633.9226 | 1248764.6747 | 2710623.8603 | 1248766.7886 | 2710616.1731 | 1248766.9756
9 | 2711058.9826 | 1248616.0048 | 2711071.1892 | 1248611.7148 | 2711079.8113 | 1248610.335
10 | 2710603.2943 | 1248766.8652 | 2710606.5333 | 1248767.2101 | 2710616.1731 | 1248766.9756
11 | 2711187.7893 | 1248570.979 | 2711185.8569 | 1248578.626 | 2711186.1413 | 1248594.8668 | 2711178.9931 | 1248607.0872 | 2711170.9046 | 1248613.8743 | 2711159.0714 | 1248618.156 | 2711144.7446 | 1248620.4782 | 2711131.3098 | 1248622.3612 | 2711101.153 | 1248618.5595 | 2711084.1896 | 1248609.6344 | 2711079.8113 | 1248610.335
12 | 2710557.3841 | 1248766.8931 | 2710562.716 | 1248764.4906 | 2710577.0543 | 1248763.9465 | 2710591.5929 | 1248765.619 | 2710603.2943 | 1248766.8652
13 | 2710383.1245 | 1248789.7869 | 2710397.9717 | 1248801.2035
14 | 2710460.2963 | 1248860.5152 | 2710437.4361 | 1248845.7996 | 2710413.3102 | 1248829.6926 | 2710410.5047 | 1248820.1437 | 2710413.9818 | 1248813.5142 | 2710397.9717 | 1248801.2035
15 | 2710383.1245 | 1248789.7869 | 2710378.127 | 1248790.8614 | 2710365.291 | 1248793.5092
16 | 2710464.6381 | 1248929.4301 | 2710476.5034 | 1248924.5805 | 2710486.7116 | 1248918.2767 | 2710492.9018 | 1248909.1291 | 2710501.3379 | 1248890.5267 | 2710507.1238 | 1248872.2864 | 2710509.5223 | 1248859.5096 | 2710483.5572 | 1248886.5477 | 2710475.232 | 1248893.1312 | 2710470.4413 | 1248892.8417 | 2710465.9069 | 1248888.9318 | 2710461.54 | 1248879.287 | 2710459.5713 | 1248869.8315 | 2710460.2963 | 1248860.5152
17 | 2710557.3841 | 1248766.8931 | 2710550.0869 | 1248770.182 | 2710521.8175 | 1248800.4573 | 2710507.2688 | 1248809.8605 | 2710491.6129 | 1248815.451 | 2710489.8155 | 1248826.3708 | 2710483.1833 | 1248837.3451 | 2710460.2963 | 1248860.5152
18 | 2710365.291 | 1248793.5092 | 2710359.2399 | 1248794.7574 | 2710354.0061 | 1248795.3188
19 | 2710464.6381 | 1248929.4301 | 2710462.9574 | 1248933.2908 | 2710455.2547 | 1248957.934
20 | 2710464.6381 | 1248929.4301 | 2710476.5034 | 1248924.5805 | 2710486.7116 | 1248918.2767 | 2710492.9018 | 1248909.1291 | 2710501.3379 | 1248890.5267 | 2710507.1238 | 1248872.2864 | 2710509.5223 | 1248859.5096 | 2710529.1997 | 1248844.0193 | 2710535.8771 | 1248842.3647 | 2710572.3609 | 1248850.6963 | 2710587.3987 | 1248854.7467 | 2710600.3339 | 1248867.0425 | 2710616.2317 | 1248882.8742 | 2710636.6516 | 1248891.1287 | 2710650.263 | 1248893.4957 | 2710660.2288 | 1248894.1156
21 | 2710557.3841 | 1248766.8931 | 2710562.2066 | 1248759.4103 | 2710597.9919 | 1248748.947 | 2710613.4854 | 1248741.9526 | 2710621.9803 | 1248736.4177 | 2710631.4017 | 1248720.9031 | 2710636.063 | 1248706.6896 | 2710645.8477 | 1248675.3689 | 2710653.7746 | 1248663.8519 | 2710661.2192 | 1248657.9416 | 2710679.3465 | 1248645.4254 | 2710698.28 | 1248635.8488 | 2710705.0782 | 1248629.7708 | 2710707.7897 | 1248622.5044 | 2710707.5893 | 1248610.591 | 2710704.1744 | 1248596.8938 | 2710697.3353 | 1248586.5688
22 | 2710346.485 | 1248795.6273 | 2710346.9876 | 1248795.6412 | 2710351.5226 | 1248795.4699 | 2710353.0568 | 1248795.4207 | 2710354.0061 | 1248795.3188
23 | 2710697.3353 | 1248586.5688 | 2710694.1272 | 1248582.6309
24 | 2710660.2288 | 1248894.1156 | 2710670.5188 | 1248894.7638 | 2710695.7699 | 1248890.2204 | 2710714.0357 | 1248891.2734 | 2710730.6292 | 1248894.5193 | 2710737.2368 | 1248897.8121 | 2710737.361 | 1248900.461 | 2710737.4349 | 1248902.1638 | 2710746.5824 | 1248905.7487 | 2710758.0021 | 1248923.5321
25 | 2710660.2288 | 1248894.1156 | 2710662.8821 | 1248909.3553 | 2710660.7954 | 1248913.1083 | 2710652.5496 | 1248914.8107
26 | 2710758.0021 | 1248923.5321 | 2710757.5454 | 1248926.1479 | 2710753.8722 | 1248927.4915 | 2710733.245 | 1248925.4934
27 | 2710705.4111 | 1248934.0695 | 2710716.6432 | 1248918.2552 | 2710727.7924 | 1248911.7248 | 2710737.5265 | 1248904.1338 | 2710737.4349 | 1248902.1638 | 2710746.5824 | 1248905.7487 | 2710758.0021 | 1248923.5321
28 | 2710758.0021 | 1248923.5321 | 2710770.6637 | 1248939.5261 | 2710791.2569 | 1248954.2452 | 2710809.2942 | 1248964.6797 | 2710829.4022 | 1248972.6176 | 2710830.6322 | 1248973.3436
29 | 2710652.5496 | 1248914.8107 | 2710640.1494 | 1248917.3709 | 2710634.1345 | 1248912.6659 | 2710630.3943 | 1248906.2798 | 2710628.1309 | 1248900.8887 | 2710607.1796 | 1248892.9399
30 | 2710334.8228 | 1248794.6696 | 2710334.8228 | 1248794.6696 | 2710340.82 | 1248795.4707 | 2710346.485 | 1248795.6273
31 | 2710700.5835 | 1248954.3514 | 2710704.8856 | 1248940.3648 | 2710705.4111 | 1248934.0695
32 | 2710705.4111 | 1248934.0695 | 2710689.8585 | 1248943.8426 | 2710659.7264 | 1248948.9064 | 2710658.4551 | 1248948.9922
33 | 2710863.8985 | 1249054.7963 | 2710864.5628 | 1249051.1836 | 2710872.068 | 1249037.5795 | 2710882.4399 | 1249018.9138 | 2710880.5174 | 1249017.9215 | 2710873.2167 | 1249019.3862 | 2710865.5368 | 1249023.7572 | 2710856.8213 | 1249031.8119 | 2710851.6571 | 1249031.7153 | 2710847.8246 | 1249029.0637 | 2710847.4408 | 1249023.741 | 2710850.5223 | 1249014.4577 | 2710855.6499 | 1248999.5637 | 2710854.1457 | 1248993.5751 | 2710842.4379 | 1248980.312 | 2710830.6322 | 1248973.3436
34 | 2710700.5835 | 1248954.3514 | 2710692.8398 | 1248961.3348 | 2710685.5869 | 1248964.2795 | 2710678.1755 | 1248965.6089
35 | 2710499.275 | 1249034.3166 | 2710514.3016 | 1249020.3186 | 2710538.5824 | 1249005.0032 | 2710568.573 | 1248957.3237 | 2710582.1706 | 1248948.6925 | 2710599.0416 | 1248950.0082 | 2710639.0736 | 1248950.2999 | 2710658.4551 | 1248948.9922
36 | 2710527.303 | 1249699.0101 | 2710526.2115 | 1249699.922
37 | 2710536.606 | 1249691.2376 | 2710536.606 | 1249691.2376 | 2710527.303 | 1249699.0101
38 | 2710520.6187 | 1249704.5948 | 2710526.2115 | 1249699.922
39 | 2710576.2772 | 1249749.4139 | 2710574.2335 | 1249746.0286 | 2710567.1209 | 1249734.2307 | 2710562.6233 | 1249726.7741 | 2710552.0529 | 1249709.2626 | 2710550.9688 | 1249707.4631 | 2710548.1018 | 1249704.0847 | 2710536.606 | 1249691.2376
40 | 2710576.2772 | 1249749.4139 | 2710580.8832 | 1249752.6803 | 2710603.9171 | 1249760.7166 | 2710622.0661 | 1249767.8834 | 2710634.9465 | 1249774.5069
41 | 2710717.8059 | 1249807.5477 | 2710702.6067 | 1249804.5948 | 2710680.1847 | 1249798.5823 | 2710658.3907 | 1249787.6553 | 2710646.127 | 1249780.7652 | 2710634.9465 | 1249774.5069
42 | 2710634.9465 | 1249774.5069 | 2710641.4829 | 1249754.9503
43 | 2710717.8059 | 1249807.5477 | 2710716.1636 | 1249800.32
44 | 2710717.8059 | 1249807.5477 | 2710722.9134 | 1249807.8211 | 2710727.9832 | 1249806.8706 | 2710732.4051 | 1249804.6292 | 2710737.4487 | 1249799.4302 | 2710741.6679 | 1249795.1055 | 2710747.3248 | 1249789.4177 | 2710760.9195 | 1249784.9328
45 | 2710647.8128 | 1249745.9867 | 2710646.4292 | 1249750.0346 | 2710642.2894 | 1249752.5371 | 2710641.4829 | 1249754.9503
46 | 2710771.3266 | 1249944.3374 | 2710782.9468 | 1249941.1964 | 2710789.2654 | 1249936.0548 | 2710793.7574 | 1249927.6429 | 2710795.7328 | 1249918.9283 | 2710793.1983 | 1249895.1455
47 | 2710747.6808 | 1249943.228 | 2710755.5505 | 1249943.175 | 2710771.3266 | 1249944.3374
48 | 2710796.6471 | 1249870.8616 | 2710792.7432 | 1249884.1662 | 2710792.8805 | 1249892.1642 | 2710793.1983 | 1249895.1455
49 | 2710747.6808 | 1249943.228 | 2710730.2045 | 1249943.3349 | 2710721.7637 | 1249944.199
50 | 2710796.6471 | 1249870.8616 | 2710803.6536 | 1249872.1492 | 2710812.5772 | 1249879.5443 | 2710817.0049 | 1249891.1143 | 2710817.7387 | 1249899.9241 | 2710819.0356 | 1249915.3935
51 | 2710796.6471 | 1249870.8616 | 2710797.1484 | 1249867.2443
52 | 2710647.3496 | 1249987.7685 | 2710651.4869 | 1249984.1761 | 2710681.5841 | 1249958.0722 | 2710698.7378 | 1249948.9629 | 2710713.7636 | 1249945.018 | 2710721.7637 | 1249944.199
53 | 2710818.5883 | 1250023.6191 | 2710814.7246 | 1250008.5456 | 2710815.4528 | 1249951.468 | 2710819.3933 | 1249919.6601 | 2710819.0356 | 1249915.3935
54 | 2710800.8326 | 1249837.2568 | 2710797.1889 | 1249847.953 | 2710798.009 | 1249861.0346 | 2710797.1484 | 1249867.2443
55 | 2710818.5883 | 1250023.6191 | 2710835.2093 | 1250058.7141 | 2710838.1978 | 1250070.8995
56 | 2710833.6335 | 1250104.1775 | 2710838.0272 | 1250086.4896 | 2710838.5629 | 1250072.388 | 2710838.1978 | 1250070.8995
57 | 2710638.0849 | 1249995.8021 | 2710647.3496 | 1249987.7685
58 | 2710647.3496 | 1249987.7685 | 2710622.9803 | 1249956.2044
59 | 2710800.8326 | 1249837.2568 | 2710806.3472 | 1249828.2747 | 2710816.5787 | 1249816.2228
60 | 2710806.3562 | 1250163.605 | 2710833.6335 | 1250104.1775
61 | 2710638.0849 | 1249995.8021 | 2710623.7289 | 1250008.3667 | 2710601.6017 | 1250027.4471 | 2710580.3236 | 1250041.5061 | 2710559.1093 | 1250050.9403 | 2710546.7691 | 1250056.4278
62 | 2710622.34 | 1249955.3752 | 2710622.9803 | 1249956.2044
63 | 2710816.5787 | 1249816.2228 | 2710821.3713 | 1249808.2948 | 2710824.4149 | 1249797.3872 | 2710824.1868 | 1249785.362 | 2710820.3311 | 1249755.3209 | 2710817.4165 | 1249732.292 | 2710856.6271 | 1249712.4423 | 2710891.7417 | 1249693.5614 | 2710897.8372 | 1249689.8724 | 2710907.8775 | 1249681.5979 | 2710976.6804 | 1249611.595
64 | 2710816.5787 | 1249816.2228 | 2710812.3403 | 1249802.5991 | 2710806.5435 | 1249793.1608 | 2710800.5378 | 1249788.0221 | 2710797.1851 | 1249786.2065
65 | 2710976.4731 | 1249483.5976 | 2710972.5368 | 1249507.0653 | 2710960.4956 | 1249588.2619 | 2710960.6589 | 1249594.0585 | 2710962.792 | 1249599.1137 | 2710976.6804 | 1249611.595
66 | 2711038.2425 | 1249574.2173 | 2711023.874 | 1249583.3223 | 2711009.8119 | 1249590.1868 | 2711001.5068 | 1249593.7008 | 2710993.9957 | 1249594.3384 | 2710976.6804 | 1249611.595
67 | 2710786.4672 | 1249781.6539 | 2710792.0301 | 1249783.4148 | 2710797.1851 | 1249786.2065
68 | 2711232.5655 | 1250067.8967 | 2711231.353 | 1250065.3181 | 2711221.8738 | 1250054.1755 | 2711218.2989 | 1250035.0372 | 2711219.388 | 1250018.8666 | 2711225.2381 | 1249992.0432 | 2711226.5131 | 1249980.0462 | 2711223.4943 | 1249966.6786 | 2711219.3847 | 1249955.1031 | 2711220.4967 | 1249944.949 | 2711221.5696 | 1249936.4733 | 2711217.1957 | 1249925.2931 | 2711212.0631 | 1249911.4855 | 2711204.3503 | 1249890.7127 | 2711199.5801 | 1249886.9645 | 2711191.6675 | 1249889.6961 | 2711187.42 | 1249899.5356 | 2711172.286 | 1249917.2663 | 2711157.4055 | 1249928.7411 | 2711147.1511 | 1249937.556 | 2711136.7352 | 1249955.3864 | 2711127.342 | 1249956.9449 | 2711115.4114 | 1249945.6342 | 2711116.0092 | 1249937.2477
69 | 2711150.4796 | 1249670.0548 | 2711151.6883 | 1249682.9102 | 2711152.3247 | 1249703.3278 | 2711149.0551 | 1249725.8405 | 2711151.1523 | 1249742.4601 | 2711149.6282 | 1249764.5162 | 2711126.0084 | 1249835.6427 | 2711117.8393 | 1249866.5371 | 2711122.1638 | 1249918.1939 | 2711116.3748 | 1249932.119 | 2711116.0092 | 1249937.2477
70 | 2711539.1463 | 1250081.8935 | 2711232.5655 | 1250067.8967
71 | 2711211.4185 | 1249583.4491 | 2711150.4796 | 1249670.0548
72 | 2711038.2425 | 1249574.2173 | 2711041.9151 | 1249570.8723 | 2711049.6906 | 1249562.9781 | 2711059.8988 | 1249558.394
73 | 2711038.2425 | 1249574.2173 | 2711042.7513 | 1249574.5486
74 | 2710786.4672 | 1249781.6539 | 2710773.9094 | 1249782.0195 | 2710761.0099 | 1249784.903 | 2710760.9195 | 1249784.9328
75 | 2710538.7098 | 1250060.0117 | 2710546.7691 | 1250056.4278
76 | 2710538.7098 | 1250060.0117 | 2710522.8319 | 1250089.4063 | 2710517.9253 | 1250099.8345 | 2710511.8727 | 1250116.235 | 2710508.7609 | 1250155.1199 | 2710504.98 | 1250169.1609 | 2710493.6846 | 1250189.7339 | 2710489.3156 | 1250199.6251
77 | 2710349.1748 | 1250089.3485 | 2710372.9257 | 1250092.4822 | 2710399.4813 | 1250097.0694 | 2710421.24 | 1250100.9445 | 2710446.9981 | 1250098.8894 | 2710472.2737 | 1250089.5083 | 2710505.6234 | 1250074.7846 | 2710528.3993 | 1250064.6121 | 2710531.5976 | 1250063.1816 | 2710538.7098 | 1250060.0117
78 | 2710334.8228 | 1248794.6696 | 2710328.4311 | 1248793.4128
79 | 2710319.4698 | 1248791.3033 | 2710323.2035 | 1248792.3848 | 2710328.4311 | 1248793.4128
80 | 2710319.4698 | 1248791.3033 | 2710307.3837 | 1248800.0325
81 | 2710349.1748 | 1250089.3485 | 2710350.1818 | 1250085.553 | 2710353.8412 | 1250081.6624 | 2710372.8038 | 1250084.0987
82 | 2710385.1696 | 1250085.6874 | 2710372.8038 | 1250084.0987
83 | 2710863.8985 | 1249054.7963 | 2710867.1241 | 1249055.1681 | 2710873.0486 | 1249056.6134 | 2710878.9202 | 1249061.2826 | 2710896.3435 | 1249072.2174 | 2710896.1769 | 1249077.8856 | 2710886.0062 | 1249078.9518 | 2710870.651 | 1249077.7747 | 2710862.0681 | 1249079.9604 | 2710852.9522 | 1249084.7939 | 2710835.0079 | 1249093.6323 | 2710831.5447 | 1249098.2936 | 2710833.8609 | 1249101.2504 | 2710842.4284 | 1249101.4997 | 2710853.4495 | 1249101.4057 | 2710855.404 | 1249103.9109 | 2710855.6464 | 1249106.2952 | 2710853.4145 | 1249108.5219
84 | 2710853.4145 | 1249108.5219 | 2710859.2494 | 1249109.0982 | 2710863.931 | 1249108.9921
85 | 2710961.3116 | 1249165.3425 | 2710947.4098 | 1249156.3416 | 2710920.1984 | 1249135.7489 | 2710891.1972 | 1249113.5215 | 2710878.5998 | 1249108.6597 | 2710863.931 | 1249108.9921
86 | 2710499.275 | 1249034.3166 | 2710484.8098 | 1249036.8379 | 2710476.7406 | 1249039.8344
87 | 2711020.3332 | 1249360.4514 | 2711020.3037 | 1249368.0682 | 2711022.8934 | 1249381.4054 | 2711027.6916 | 1249393.3606 | 2711032.5633 | 1249401.3918 | 2711036.9561 | 1249405.817
88 | 2711043.8399 | 1249414.2246 | 2711040.2794 | 1249409.1649 | 2711036.9561 | 1249405.817
89 | 2711020.3332 | 1249360.4514 | 2711016.0976 | 1249345.8824 | 2711015.6054 | 1249339.101 | 2711015.6349 | 1249338.3102
90 | 2711043.8399 | 1249414.2246 | 2711052.5829 | 1249415.9676 | 2711076.6316 | 1249428.095
91 | 2711043.8399 | 1249414.2246 | 2711036.3532 | 1249412.7387 | 2711026.0702 | 1249409.7548
92 | 2711016.0598 | 1249326.944 | 2711015.6349 | 1249338.3102
93 | 2711111.5185 | 1249450.0417 | 2711100.1882 | 1249441.9475 | 2711079.1047 | 1249429.3421 | 2711076.6316 | 1249428.095
94 | 2710995.643 | 1249418.5811 | 2711013.6332 | 1249415.7156 | 2711026.0702 | 1249409.7548
95 | 2711026.0702 | 1249409.7548 | 2711011.1181 | 1249396.386 | 2711004.1492 | 1249386.0015
96 | 2711016.0598 | 1249326.944 | 2711021.3266 | 1249324.3739 | 2711026.099 | 1249320.3822 | 2711031.7275 | 1249315.4392 | 2711043.2095 | 1249300.4086 | 2711046.5948 | 1249287.0166 | 2711046.6074 | 1249273.4502 | 2711044.0121 | 1249264.0383 | 2711023.7141 | 1249228.8294 | 2711011.1912 | 1249215.9844 | 2711003.5418 | 1249206.2443 | 2711000.2781 | 1249200.6564 | 2710997.8945 | 1249199.2884 | 2710993.9405 | 1249197.891 | 2710991.8253 | 1249195.0936 | 2710988.7116 | 1249187.9517 | 2710983.0161 | 1249183.1633 | 2710972.4625 | 1249174.4364 | 2710961.3116 | 1249165.3425
97 | 2711144.2429 | 1249481.0885 | 2711125.2568 | 1249461.9226 | 2711117.5968 | 1249454.384 | 2711111.5185 | 1249450.0417
98 | 2710995.643 | 1249418.5811 | 2710983.0967 | 1249427.5535 | 2710976.0566 | 1249430.8577 | 2710969.3153 | 1249431.1095 | 2710960.2276 | 1249429.6271 | 2710951.0092 | 1249429.877 | 2710941.1182 | 1249434.1843 | 2710931.6457 | 1249441.146 | 2710920.8675 | 1249446.8601 | 2710901.4063 | 1249449.6427 | 2710863.8903 | 1249451.4869 | 2710853.2319 | 1249450.7981 | 2710845.5564 | 1249448.5039
99 | 2711156.9078 | 1249494.0816 | 2711152.4876 | 1249489.4112 | 2711144.2429 | 1249481.0885
100 | 2710432.721 | 1249068.3264 | 2710451.9091 | 1249060.3996 | 2710465.2101 | 1249048.2042 | 2710476.7406 | 1249039.8344
101 | 2710454.9256 | 1249071.1757 | 2710458.7085 | 1249069.2001 | 2710470.4657 | 1249049.8812 | 2710476.7406 | 1249039.8344
102 | 2710716.1636 | 1249800.32 | 2710713.7101 | 1249789.5224
103 | 2710713.7101 | 1249789.5224 | 2710713.589 | 1249788.9893
104 | 2710486.7117 | 1250208.2284 | 2710488.7885 | 1250200.8183 | 2710489.3156 | 1250199.6251
105 | 2710481.977 | 1250225.1224 | 2710486.7117 | 1250208.2284
106 | 2710481.977 | 1250225.1224 | 2710481.3328 | 1250233.7508 | 2710476.8413 | 1250258.365 | 2710474.6397 | 1250268.7102
107 | 2711156.9078 | 1249494.0816 | 2711162.9055 | 1249500.4188
108 | 2711173.7778 | 1249511.9067 | 2711162.9055 | 1249500.4188
109 | 2711173.7778 | 1249511.9067 | 2711171.4586 | 1249513.9249
110 | 2711173.7778 | 1249511.9067 | 2711178.5857 | 1249509.6394 | 2711184.8681 | 1249508.89 | 2711189.5183 | 1249509.7169
111 | 2710806.3562 | 1250163.605 | 2710811.2126 | 1250171.2243 | 2710816.3431 | 1250188.0006
112 | 2710806.3562 | 1250163.605 | 2710796.2616 | 1250159.0904 | 2710787.9378 | 1250152.3515 | 2710777.2669 | 1250137.4621 | 2710768.4185 | 1250124.8531 | 2710762.2742 | 1250122.2149
113 | 2711982.4551 | 1250599.2783 | 2711967.8292 | 1250604.4729 | 2711967.3554 | 1250604.604
114 | 2711982.4551 | 1250599.2783 | 2711989.4561 | 1250609.1854 | 2711995.2778 | 1250611.9755 | 2712000.7667 | 1250612.6651
115 | 2711982.4551 | 1250599.2783 | 2711973.4542 | 1250586.5199 | 2711966.2997 | 1250576.3431 | 2711958.1658 | 1250566.4479 | 2711927.9271 | 1250531.9706 | 2711898.8495 | 1250499.9618 | 2711863.0836 | 1250463.0452 | 2711847.0129 | 1250449.5752 | 2711836.2479 | 1250437.4399 | 2711822.626 | 1250417.4442 | 2711815.8993 | 1250410.178 | 2711809.1087 | 1250403.9002 | 2711806.078 | 1250402.2256
116 | 2711702.3195 | 1250380.0337 | 2711707.9453 | 1250378.4162 | 2711712.0522 | 1250377.2593 | 2711714.7004 | 1250376.5753 | 2711716.7301 | 1250376.2578 | 2711718.6673 | 1250376.0385 | 2711720.5034 | 1250375.9731 | 2711722.1481 | 1250376.0486 | 2711724.0027 | 1250376.2059 | 2711726.0349 | 1250376.5556 | 2711728.1619 | 1250377.085 | 2711733.9137 | 1250378.7949 | 2711746.5358 | 1250381.7686 | 2711766.5848 | 1250384.9159 | 2711772.7608 | 1250386.1556 | 2711777.6433 | 1250387.5155 | 2711782.8734 | 1250389.6603 | 2711793.4601 | 1250395.2535 | 2711806.078 | 1250402.2256
117 | 2711702.3195 | 1250380.0337 | 2711699.6809 | 1250381.4073 | 2711697.247 | 1250382.7403 | 2711694.7663 | 1250384.1503 | 2711691.6188 | 1250386.0815 | 2711685.0229 | 1250390.6943 | 2711682.9347 | 1250392.1117 | 2711680.8962 | 1250393.2965 | 2711678.8005 | 1250394.3134 | 2711676.6648 | 1250395.0515 | 2711674.3491 | 1250395.7195 | 2711672.0765 | 1250396.1104 | 2711670.0187 | 1250396.3162 | 2711667.3676 | 1250396.3552 | 2711662.2976 | 1250396.1261 | 2711656.4667 | 1250395.8049 | 2711652.3816 | 1250395.4054 | 2711648.6225 | 1250394.9342 | 2711644.6423 | 1250394.1808 | 2711640.9954 | 1250393.367 | 2711636.2527 | 1250392.199 | 2711618.0817 | 1250387.9644 | 2711615.9456 | 1250387.9031
118 | 2711702.3195 | 1250380.0337 | 2711704.0063 | 1250377.8748 | 2711705.7294 | 1250375.7945 | 2711707.4865 | 1250373.9149 | 2711709.5655 | 1250371.7857 | 2711724.6429 | 1250357.4803 | 2711726.3128 | 1250355.8216 | 2711727.625 | 1250354.3117 | 2711728.7166 | 1250352.8867 | 2711729.5205 | 1250351.5007 | 2711730.031 | 1250350.4539 | 2711730.5458 | 1250349.1848 | 2711731.0369 | 1250347.5705 | 2711731.2833 | 1250346.1184 | 2711731.238 | 1250344.9166 | 2711730.7165 | 1250343.7391 | 2711729.7648 | 1250342.5535 | 2711728.7554 | 1250341.6226 | 2711727.7049 | 1250340.8688 | 2711726.6754 | 1250340.2044 | 2711725.5759 | 1250339.6499 | 2711724.128 | 1250339.1444 | 2711722.5424 | 1250338.7364 | 2711721.1431 | 1250338.4654 | 2711719.8338 | 1250338.2183 | 2711716.8524 | 1250337.7506 | 2711714.504 | 1250337.3505 | 2711712.1062 | 1250336.7714 | 2711709.8607 | 1250336.1175 | 2711707.6782 | 1250335.3313 | 2711705.4244 | 1250334.3213 | 2711701.7286 | 1250332.4946 | 2711699.2214 | 1250331.3019 | 2711696.7732 | 1250330.1882 | 2711693.903 | 1250329.0331 | 2711690.8561 | 1250328.0304 | 2711688.1221 | 1250327.2561 | 2711669.8136 | 1250323.0966 | 2711666.9729 | 1250322.3758 | 2711664.7954 | 1250321.7231 | 2711662.8961 | 1250321.1313 | 2711661.2977 | 1250320.6007 | 2711659.8352 | 1250320.0727 | 2711658.2226 | 1250319.4974 | 2711656.243 | 1250318.7596 | 2711654.3624 | 1250317.979 | 2711653.592 | 1250317.6577
119 | 2711489.9608 | 1250679.6929 | 2711487.1063 | 1250676.2626
120 | 2711489.9608 | 1250679.6929 | 2711522.1698 | 1250675.7957
121 | 2711522.1698 | 1250675.7957 | 2711514.1985 | 1250662.4458 | 2711510.5699 | 1250652.6473 | 2711509.0305 | 1250644.178 | 2711510.1467 | 1250634.6245 | 2711522.2314 | 1250602.759 | 2711531.5937 | 1250577.9369 | 2711534.0868 | 1250567.4419 | 2711542.6698 | 1250553.5253 | 2711556.7783 | 1250536.0987 | 2711563.5306 | 1250518.7671 | 2711565.575 | 1250504.0379 | 2711564.2289 | 1250467.6715 | 2711563.6547 | 1250445.6426 | 2711566.6047 | 1250428.94 | 2711571.7423 | 1250408.7423 | 2711574.5866 | 1250402.8577 | 2711577.9489 | 1250397.9391 | 2711584.9849 | 1250393.6125 | 2711593.5042 | 1250390.7149 | 2711606.7764 | 1250387.6401 | 2711615.9456 | 1250387.9031
122 | 2711522.1698 | 1250675.7957 | 2711528.6274 | 1250674.8942 | 2711530.7131 | 1250674.6047
123 | 2711549.9307 | 1250671.9372 | 2711530.7131 | 1250674.6047
124 | 2711549.9307 | 1250671.9372 | 2711555.1482 | 1250684.9775
125 | 2711647.2973 | 1250315.0324 | 2711653.592 | 1250317.6577
126 | 2711972.0907 | 1250204.157 | 2711978.8515 | 1250210.0229 | 2711998.1925 | 1250227.8697 | 2712015.7709 | 1250249.8756 | 2712025.752 | 1250264.732 | 2712039.1645 | 1250282.6113 | 2712054.1222 | 1250297.0393 | 2712065.6906 | 1250303.8192 | 2712071.2321 | 1250307.0711 | 2712074.359 | 1250308.6155
127 | 2712094.4112 | 1250317.9962 | 2712089.4937 | 1250316.0905 | 2712074.359 | 1250308.6155
128 | 2711707.3426 | 1249963.1857 | 2711737.1139 | 1249973.8333 | 2711763.0307 | 1249986.2432 | 2711776.0868 | 1249993.8735 | 2711786.4182 | 1250001.8304 | 2711794.3871 | 1250010.9215 | 2711815.432 | 1250031.3797 | 2711851.082 | 1250070.5957 | 2711866.4862 | 1250087.0222 | 2711904.8398 | 1250126.1895 | 2711919.0144 | 1250142.9375 | 2711931.0937 | 1250161.8701 | 2711939.2273 | 1250174.2116 | 2711944.8442 | 1250181.0678 | 2711955.4559 | 1250190.5427 | 2711972.0907 | 1250204.157
129 | 2712094.4112 | 1250317.9962 | 2712106.9362 | 1250325.695 | 2712107.7424 | 1250326.4081
130 | 2711707.3426 | 1249963.1857 | 2711681.5638 | 1249956.6612 | 2711655.3984 | 1249950.6077 | 2711630.2202 | 1249938.2567 | 2711620.0578 | 1249931.7377 | 2711610.6516 | 1249920.7516 | 2711602.5658 | 1249916.2401 | 2711599.5678 | 1249915.4888
131 | 2711707.3426 | 1249963.1857 | 2711735.0982 | 1249960.1952 | 2711741.0859 | 1249953.4248 | 2711747.0253 | 1249949.3279
132 | 2712107.7424 | 1250326.4081 | 2712379.4669 | 1250087.9712
133 | 2711576.9402 | 1249921.2062 | 2711583.8832 | 1249914.6315 | 2711590.9534 | 1249913.3302 | 2711599.5678 | 1249915.4888
134 | 2712379.4669 | 1250087.9712 | 2712373.937 | 1250084.1076 | 2712352.3143 | 1250067.9399 | 2712338.5051 | 1250056.6689 | 2712326.7573 | 1250045.5474
135 | 2711576.9402 | 1249921.2062 | 2711560.9313 | 1249938.0186 | 2711552.9577 | 1249948.8009
136 | 2712275.5488 | 1249971.0055 | 2712277.7737 | 1249983.102 | 2712280.1127 | 1249991.1752 | 2712311.3478 | 1250028.5088 | 2712321.6878 | 1250040.7482 | 2712326.7573 | 1250045.5474
137 | 2711539.1463 | 1250081.8935 | 2711541.6774 | 1250087.0342 | 2711542.9368 | 1250090.3273 | 2711543.8568 | 1250093.2025 | 2711544.6799 | 1250096.8099 | 2711545.3942 | 1250100.582 | 2711545.8854 | 1250104.1719 | 2711546.1373 | 1250107.2348 | 2711546.2137 | 1250109.994 | 2711546.0562 | 1250114.3502 | 2711545.6462 | 1250119.2798 | 2711544.9452 | 1250125.2271 | 2711544.3641 | 1250130.8208 | 2711543.9795 | 1250136.407 | 2711543.814 | 1250141.5859 | 2711543.6372 | 1250150.5677 | 2711543.7159 | 1250158.8205 | 2711543.8876 | 1250164.5395 | 2711543.8924 | 1250170.7002 | 2711543.6432 | 1250175.5106 | 2711543.2942 | 1250180.8084 | 2711542.6834 | 1250186.3792 | 2711541.5821 | 1250194.3317 | 2711540.67 | 1250200.6642 | 2711540.1327 | 1250206.3365 | 2711539.7146 | 1250211.6997 | 2711539.6084 | 1250216.1347 | 2711539.6697 | 1250220.495 | 2711539.9917 | 1250224.2486 | 2711540.7678 | 1250227.944 | 2711541.9187 | 1250231.3907 | 2711543.4331 | 1250234.7775 | 2711545.1567 | 1250237.8792 | 2711547.0492 | 1250240.4391 | 2711549.3469 | 1250243.129 | 2711560.3991 | 1250254.502 | 2711567.3391 | 1250262.0944 | 2711574.1155 | 1250270.3509 | 2711581.799 | 1250280.5595 | 2711585.5067 | 1250285.3666 | 2711588.8813 | 1250289.4113 | 2711591.9847 | 1250292.2276 | 2711595.5354 | 1250294.9411 | 2711598.9759 | 1250297.0965 | 2711602.8632 | 1250299.1825 | 2711607.1769 | 1250301.0764 | 2711612.2438 | 1250303.0735 | 2711617.5928 | 1250304.9313 | 2711623.5162 | 1250306.7555 | 2711628.7505 | 1250308.2886 | 2711631.8288 | 1250309.2252 | 2711634.3879 | 1250310.0629 | 2711636.7743 | 1250310.853 | 2711637.1006 | 1250310.9725
138 | 2711539.1463 | 1250081.8935 | 2711541.4456 | 1250078.8898 | 2711542.5653 | 1250077.1762 | 2711543.1975 | 1250075.6868 | 2711543.6315 | 1250073.8935 | 2711543.8403 | 1250072.0293 | 2711543.8446 | 1250070.1945 | 2711543.663 | 1250068.2117 | 2711543.146 | 1250063.1867 | 2711542.846 | 1250060.6679 | 2711542.4108 | 1250058.1132 | 2711540.9281 | 1250050.6347 | 2711538.8611 | 1250037.6963 | 2711538.3476 | 1250032.4823 | 2711538.0063 | 1250027.3495 | 2711537.9239 | 1250022.0992 | 2711538.1978 | 1250015.9771 | 2711538.8172 | 1250009.1498 | 2711541.688 | 1249985.0284
139 | 2711211.4185 | 1249583.4491 | 2711199.4902 | 1249575.5966 | 2711197.6413 | 1249574.4255
140 | 2711637.1006 | 1250310.9725 | 2711638.9191 | 1250311.6385 | 2711643.6572 | 1250313.5579
141 | 2711541.688 | 1249985.0284 | 2711545.4377 | 1249965.5608 | 2711549.6333 | 1249953.2963 | 2711552.9577 | 1249948.8009
142 | 2711541.688 | 1249985.0284 | 2711554.4063 | 1249977.7285 | 2711562.2427 | 1249979.0437 | 2711566.8942 | 1249985.4698 | 2711567.7685 | 1249993.5247
143 | 2711179.3184 | 1249555.9021 | 2711180.109 | 1249560.454 | 2711186.1384 | 1249567.1393 | 2711197.6413 | 1249574.4255
144 | 2711647.2973 | 1250315.0324 | 2711643.6572 | 1250313.5579
145 | 2710954.0559 | 1250385.8503 | 2710737.3167 | 1250582.6805
146 | 2710737.3167 | 1250582.6805 | 2710726.557 | 1250596.8133 | 2710725.7912 | 1250597.544
147 | 2710762.2742 | 1250122.2149 | 2710761.1688 | 1250121.7403
148 | 2710537.8582 | 1250479.9422 | 2710725.7912 | 1250597.544
149 | 2710537.8582 | 1250479.9422 | 2710538.107 | 1250473.8059 | 2710535.606 | 1250461.7605 | 2710540.1722 | 1250446.8389
150 | 2710761.1688 | 1250121.7403 | 2710755.2041 | 1250119.1793
151 | 2712185.2707 | 1249758.8549 | 2712275.5488 | 1249971.0055
152 | 2712185.2707 | 1249758.8549 | 2712183.113 | 1249757.5463 | 2712167.982 | 1249749.8894
153 | 2712156.2825 | 1249744.1422 | 2712160.2835 | 1249745.9937 | 2712167.982 | 1249749.8894
154 | 2710540.1722 | 1250446.8389 | 2710541.9265 | 1250441.1059 | 2710541.8979 | 1250438.4988
155 | 2710472.171 | 1250295.4265 | 2710472.6198 | 1250290.5688
156 | 2710472.171 | 1250295.4265 | 2710470.7796 | 1250310.4835
157 | 2710474.6397 | 1250268.7102 | 2710472.6198 | 1250290.5688
158 | 2710487.5323 | 1250317.9352 | 2710470.7796 | 1250310.4835
159 | 2710487.5323 | 1250317.9352 | 2710541.8979 | 1250438.4988
160 | 2711477.4485 | 1249765.3609 | 2711477.7672 | 1249763.811 | 2711478.3909 | 1249761.5654 | 2711479.1114 | 1249759.7997 | 2711479.9073 | 1249758.0354 | 2711480.7454 | 1249756.4388 | 2711481.6823 | 1249754.8106 | 2711482.668 | 1249753.3947 | 2711483.9186 | 1249751.9503 | 2711485.274 | 1249750.5525 | 2711487.0317 | 1249749.051 | 2711489.0839 | 1249747.1435 | 2711490.7008 | 1249745.4948 | 2711492.3742 | 1249743.6581 | 2711493.6356 | 1249742.0361 | 2711495.2344 | 1249739.8721
161 | 2711533.6585 | 1249678.3701 | 2711530.7527 | 1249683.0971 | 2711529.4249 | 1249685.4296 | 2711528.4044 | 1249687.4899 | 2711527.525 | 1249689.6751 | 2711524.3602 | 1249698.1225 | 2711523.5211 | 1249700.1751 | 2711522.7587 | 1249701.762 | 2711521.6911 | 1249703.51 | 2711520.6198 | 1249705.0578 | 2711519.4152 | 1249706.4696 | 2711517.8773 | 1249707.9308 | 2711513.6077 | 1249711.2866 | 2711511.0522 | 1249713.4514 | 2711509.0771 | 1249715.2713 | 2711507.9441 | 1249716.4843 | 2711506.925 | 1249717.6661 | 2711506.2186 | 1249718.687 | 2711505.4532 | 1249720.0292 | 2711504.6623 | 1249721.5267 | 2711503.5197 | 1249724.0517 | 2711501.7546 | 1249728.3554 | 2711500.6817 | 1249730.7927 | 2711499.2716 | 1249733.4906 | 2711498.1546 | 1249735.4601 | 2711496.995 | 1249737.2843 | 2711495.4102 | 1249739.6342 | 2711495.2344 | 1249739.8721
162 | 2711533.6585 | 1249678.3701 | 2711534.0246 | 1249676.5755 | 2711534.5331 | 1249674.0386 | 2711534.7593 | 1249672.4526 | 2711534.9311 | 1249670.1429 | 2711534.9336 | 1249668.0078 | 2711534.796 | 1249666.0926 | 2711534.5436 | 1249663.4523 | 2711534.1711 | 1249660.7764 | 2711533.6837 | 1249658.1874 | 2711533.0117 | 1249655.3724 | 2711532.3502 | 1249653.2026 | 2711531.4765 | 1249650.673 | 2711530.5055 | 1249648.0971 | 2711529.5158 | 1249645.7098 | 2711528.4981 | 1249643.6112 | 2711527.4742 | 1249641.8349 | 2711526.092 | 1249639.8406 | 2711524.6746 | 1249638.1125 | 2711522.9363 | 1249636.1782 | 2711520.6379 | 1249633.9109 | 2711513.7107 | 1249627.1973 | 2711511.2659 | 1249624.6826 | 2711509.9357 | 1249623.1341 | 2711508.3186 | 1249621.1798 | 2711507.0809 | 1249619.533 | 2711506.0881 | 1249618.1131 | 2711505.1337 | 1249616.6607 | 2711504.022 | 1249614.7382 | 2711502.4275 | 1249611.9837 | 2711501.3252 | 1249609.9613 | 2711500.2716 | 1249607.7619 | 2711499.5552 | 1249606.1026 | 2711499.0797 | 1249604.8816 | 2711498.5279 | 1249603.3032 | 2711495.1467 | 1249593.1646 | 2711494.193 | 1249590.0664 | 2711493.2677 | 1249587.0687 | 2711492.348 | 1249583.771 | 2711491.5518 | 1249580.7313 | 2711491.0105 | 1249578.5971 | 2711490.5065 | 1249576.4859 | 2711490.0807 | 1249574.6319 | 2711489.7346 | 1249572.5571 | 2711489.5085 | 1249570.5289 | 2711489.3211 | 1249568.4459 | 2711489.1833 | 1249566.1414 | 2711489.0961 | 1249563.9491 | 2711489.0537 | 1249560.9903 | 2711489.0556 | 1249557.6765 | 2711489.1794 | 1249552.7081 | 2711489.1659 | 1249551.0176 | 2711488.9863 | 1249549.3239 | 2711488.6077 | 1249547.7711 | 2711488.0848 | 1249546.26 | 2711487.3569 | 1249544.8118 | 2711486.3188 | 1249543.3911 | 2711485.0123 | 1249542.1878 | 2711483.2046 | 1249541.1307 | 2711481.0521 | 1249540.334 | 2711478.8101 | 1249539.8804 | 2711475.939 | 1249539.5483 | 2711472.2367 | 1249539.2451 | 2711467.7114 | 1249538.9264 | 2711462.9855 | 1249538.8375 | 2711458.3038 | 1249538.805 | 2711455.4329 | 1249538.8622 | 2711452.3641 | 1249539.0046 | 2711446.4802 | 1249539.4499 | 2711443.2677 | 1249539.6007 | 2711440.0967 | 1249539.5522 | 2711436.591 | 1249539.2305 | 2711433.466 | 1249538.7491 | 2711430.1193 | 1249538.0078 | 2711427.1215 | 1249537.1841 | 2711423.8567 | 1249536.0996 | 2711420.3711 | 1249534.7108 | 2711416.8597 | 1249533.0879 | 2711414.2052 | 1249531.6813 | 2711411.3004 | 1249529.9252 | 2711408.1505 | 1249527.9533 | 2711405.6306 | 1249526.2156 | 2711403.4869 | 1249524.5518 | 2711401.4667 | 1249522.7457 | 2711397.292 | 1249518.6416 | 2711393.7218 | 1249514.927 | 2711392.0195 | 1249513.4828 | 2711390.3953 | 1249512.3068 | 2711388.663 | 1249511.2512 | 2711386.7391 | 1249510.3476 | 2711384.7225 | 1249509.5535 | 2711382.5822 | 1249508.9128 | 2711380.5147 | 1249508.418 | 2711378.5063 | 1249507.991 | 2711376.5189 | 1249507.6534 | 2711374.418 | 1249507.3248 | 2711371.9911 | 1249507.0678 | 2711369.3659 | 1249506.9073 | 2711360.3074 | 1249506.6925
163 | 2711360.3074 | 1249506.6925 | 2711365.2256 | 1249496.7057
164 | 2711360.3074 | 1249506.6925 | 2711354.0858 | 1249506.62 | 2711351.9216 | 1249506.5364
165 | 2711368.8257 | 1249489.3955 | 2711365.2256 | 1249496.7057
166 | 2711321.5219 | 1249505.4754 | 2711323.0481 | 1249505.336 | 2711325.3605 | 1249505.2571 | 2711328.0265 | 1249505.2516 | 2711334.981 | 1249505.3045 | 2711337.5694 | 1249505.4088 | 2711340.2023 | 1249505.5583 | 2711343.3991 | 1249505.8408 | 2711346.331 | 1249506.1517 | 2711348.9249 | 1249506.3673 | 2711351.2785 | 1249506.5116 | 2711351.9216 | 1249506.5364
167 | 2711179.3184 | 1249555.9021 | 2711173.0063 | 1249554.2157 | 2711135.6424 | 1249544.3626
168 | 2711111.2733 | 1249538.2452 | 2711135.6424 | 1249544.3626
169 | 2711135.6424 | 1249544.3626 | 2711147.6475 | 1249534.4467
170 | 2711111.2733 | 1249538.2452 | 2711106.3557 | 1249541.9338 | 2711086.2395 | 1249547.8394 | 2711071.4881 | 1249553.1896 | 2711059.8988 | 1249558.394
171 | 2711152.1503 | 1249530.7276 | 2711147.6475 | 1249534.4467
172 | 2711232.2228 | 1249524.013 | 2711241.8591 | 1249522.4147 | 2711247.0827 | 1249520.1331 | 2711253.4989 | 1249520.6984 | 2711260.685 | 1249520.889 | 2711271.6372 | 1249519.1932 | 2711286.5462 | 1249516.3151
173 | 2711286.5462 | 1249516.3151 | 2711292.7673 | 1249514.8085 | 2711296.0244 | 1249513.8911 | 2711299.0034 | 1249512.9018 | 2711301.9998 | 1249511.7905 | 2711304.4374 | 1249510.6798 | 2711307.1316 | 1249509.4197
174 | 2711286.5462 | 1249516.3151 | 2711292.1065 | 1249506.5671 | 2711301.7899 | 1249488.4007 | 2711307.3251 | 1249479.9866 | 2711317.0037 | 1249470.1158 | 2711327.6292 | 1249463.7101 | 2711341.6883 | 1249459.0482 | 2711369.199 | 1249456.7408 | 2711382.7187 | 1249454.5144
175 | 2711232.2228 | 1249524.013 | 2711233.6668 | 1249534.2492
176 | 2711232.2228 | 1249524.013 | 2711225.297 | 1249523.2379
177 | 2711321.5219 | 1249505.4754 | 2711320.7256 | 1249505.5481 | 2711318.3396 | 1249505.9258 | 2711315.8143 | 1249506.4788 | 2711313.4537 | 1249507.1128 | 2711311.3875 | 1249507.7523 | 2711309.4721 | 1249508.4058 | 2711307.386 | 1249509.3007 | 2711307.1316 | 1249509.4197
178 | 2711382.7187 | 1249454.5144 | 2711384.0473 | 1249454.2956 | 2711416.3318 | 1249443.078
179 | 2711152.1503 | 1249530.7276 | 2711171.4586 | 1249513.9249
180 | 2711225.0158 | 1249516.0935 | 2711225.297 | 1249523.2379
181 | 2711225.0158 | 1249516.0935 | 2711207.3813 | 1249512.8933 | 2711189.5183 | 1249509.7169
182 | 2711225.297 | 1249523.2379 | 2711221.5822 | 1249524.4025 | 2711221.1082 | 1249526.7177 | 2711217.5017 | 1249527.3395 | 2711217.8408 | 1249530.0859
183 | 2711429.7102 | 1249437.5207 | 2711423.638 | 1249440.5395 | 2711416.3318 | 1249443.078
184 | 2711081.2064 | 1249572.9879 | 2711071.9947 | 1249573.2933 | 2711058.3366 | 1249579.954 | 2711053.397 | 1249579.5834 | 2711048.6047 | 1249574.9787 | 2711042.7513 | 1249574.5486
185 | 2711456.8408 | 1249405.3226 | 2711448.8918 | 1249419.3079 | 2711443.3839 | 1249427.0551 | 2711435.2333 | 1249434.7749 | 2711429.7102 | 1249437.5207
186 | 2711456.8408 | 1249405.3226 | 2711464.5447 | 1249391.7685 | 2711474.5198 | 1249378.9347
187 | 2710718.4865 | 1249775.8846 | 2710711.0306 | 1249777.7301 | 2710713.589 | 1249788.9893

## bus_geodata
| x | y | coords
0 | 2711067.7632 | 1248645.9127
1 | 2711080.1052 | 1248644.1749
2 | 2711008.0764 | 1248627.7235
3 | 2711039.2267 | 1248626.8729
4 | 2711078.3962 | 1248661.6016
5 | 2711117.3311 | 1248652.08
6 | 2710668.3409 | 1248757.0442
7 | 2711058.9826 | 1248616.0048
8 | 2711037.5108 | 1248662.4803
9 | 2710616.1731 | 1248766.9756
10 | 2711079.8113 | 1248610.335
11 | 2710603.2943 | 1248766.8652
12 | 2710397.9717 | 1248801.2035
13 | 2710383.1245 | 1248789.7869
14 | 2710460.2963 | 1248860.5152
15 | 2710365.291 | 1248793.5092
16 | 2710464.6381 | 1248929.4301
17 | 2710557.3841 | 1248766.8931
18 | 2710354.0061 | 1248795.3188
19 | 2710697.3353 | 1248586.5688
20 | 2710455.2547 | 1248957.934
21 | 2710660.2288 | 1248894.1156
22 | 2710758.0021 | 1248923.5321
23 | 2710652.5496 | 1248914.8107
24 | 2710346.485 | 1248795.6273
25 | 2710694.1272 | 1248582.6308
26 | 2710733.245 | 1248925.4934
27 | 2710705.4111 | 1248934.0695
28 | 2710830.6322 | 1248973.3436
29 | 2710700.5835 | 1248954.3514
30 | 2710658.4551 | 1248948.9922
31 | 2710607.1796 | 1248892.9399
32 | 2711187.7893 | 1248570.979
33 | 2710527.303 | 1249699.0101
34 | 2710526.2115 | 1249699.922
35 | 2710536.606 | 1249691.2376
36 | 2710520.6187 | 1249704.5948
37 | 2710576.2772 | 1249749.4139
38 | 2710634.9465 | 1249774.5069
39 | 2710717.8059 | 1249807.5477
40 | 2710641.4829 | 1249754.9503
41 | 2710771.3266 | 1249944.3374
42 | 2710793.1983 | 1249895.1455
43 | 2710747.6808 | 1249943.228
44 | 2710796.6471 | 1249870.8616
45 | 2710721.7637 | 1249944.199
46 | 2710819.0356 | 1249915.3935
47 | 2710797.1484 | 1249867.2443
48 | 2710818.5883 | 1250023.6191
49 | 2710838.1978 | 1250070.8995
50 | 2710647.3496 | 1249987.7685
51 | 2710800.8326 | 1249837.2568
52 | 2710833.6335 | 1250104.1775
53 | 2710638.0849 | 1249995.8021
54 | 2710622.9803 | 1249956.2044
55 | 2710816.5787 | 1249816.2228
56 | 2710976.6804 | 1249611.595
57 | 2710797.1851 | 1249786.2065
58 | 2711116.0092 | 1249937.2477
59 | 2711232.5655 | 1250067.8967
60 | 2711150.4796 | 1249670.0548
61 | 2710976.4731 | 1249483.5976
62 | 2711038.2425 | 1249574.2173
63 | 2710786.4672 | 1249781.6539
64 | 2710622.34 | 1249955.3752
65 | 2710546.7691 | 1250056.4278
66 | 2710538.7098 | 1250060.0117
67 | 2710334.8228 | 1248794.6696
68 | 2710328.4311 | 1248793.4128
69 | 2710319.4698 | 1248791.3033
70 | 2710307.3837 | 1248800.0325
71 | 2710349.1748 | 1250089.3485
72 | 2710372.8038 | 1250084.0987
73 | 2710853.4145 | 1249108.5219
74 | 2710863.8985 | 1249054.7964
75 | 2710863.931 | 1249108.9921
76 | 2710678.1755 | 1248965.6089
77 | 2710499.275 | 1249034.3166
78 | 2711036.9561 | 1249405.817
79 | 2711020.3332 | 1249360.4514
80 | 2711043.8399 | 1249414.2246
81 | 2711015.6349 | 1249338.3102
82 | 2711076.6316 | 1249428.095
83 | 2711026.0702 | 1249409.7548
84 | 2711016.0598 | 1249326.944
85 | 2711111.5185 | 1249450.0417
86 | 2710995.643 | 1249418.5811
87 | 2711004.1492 | 1249386.0015
88 | 2710961.3116 | 1249165.3425
89 | 2711144.2429 | 1249481.0885
90 | 2710845.5564 | 1249448.5039
91 | 2710476.7406 | 1249039.8344
92 | 2710432.721 | 1249068.3264
93 | 2710454.9256 | 1249071.1757
94 | 2710647.8128 | 1249745.9867
95 | 2710716.1636 | 1249800.32
96 | 2710760.9195 | 1249784.9328
97 | 2710713.7101 | 1249789.5224
98 | 2710489.3156 | 1250199.6251
99 | 2710486.7117 | 1250208.2284
100 | 2710481.977 | 1250225.1224
101 | 2710385.1696 | 1250085.6874
102 | 2711156.9078 | 1249494.0816
103 | 2711162.9055 | 1249500.4188
104 | 2711173.7778 | 1249511.9067
105 | 2710806.3562 | 1250163.605
106 | 2711967.3554 | 1250604.604
107 | 2711982.4551 | 1250599.2783
108 | 2712000.7667 | 1250612.6651
109 | 2711806.078 | 1250402.2256
110 | 2711702.3195 | 1250380.0337
111 | 2711489.9608 | 1250679.6929
112 | 2711487.1063 | 1250676.2626
113 | 2711522.1698 | 1250675.7957
114 | 2711615.9456 | 1250387.9031
115 | 2711530.7131 | 1250674.6047
116 | 2711555.1482 | 1250684.9775
117 | 2711549.9307 | 1250671.9372
118 | 2711653.592 | 1250317.6577
119 | 2712074.359 | 1250308.6155
120 | 2711972.0907 | 1250204.157
121 | 2712094.4112 | 1250317.9962
122 | 2711707.3426 | 1249963.1857
123 | 2712107.7424 | 1250326.4081
124 | 2711599.5678 | 1249915.4888
125 | 2711747.0253 | 1249949.3279
126 | 2712379.4669 | 1250087.9712
127 | 2711576.9402 | 1249921.2062
128 | 2712326.7573 | 1250045.5474
129 | 2711539.1463 | 1250081.8935
130 | 2711211.4185 | 1249583.4491
131 | 2711637.1006 | 1250310.9725
132 | 2711541.688 | 1249985.0284
133 | 2711197.6413 | 1249574.4255
134 | 2711647.2973 | 1250315.0324
135 | 2711643.6572 | 1250313.5579
136 | 2711567.7685 | 1249993.5247
137 | 2711552.9577 | 1249948.8009
138 | 2710954.0559 | 1250385.8503
139 | 2710737.3167 | 1250582.6805
140 | 2710816.3431 | 1250188.0006
141 | 2710762.2742 | 1250122.2149
142 | 2710725.7912 | 1250597.544
143 | 2710537.8582 | 1250479.9422
144 | 2710761.1688 | 1250121.7403
145 | 2712275.5488 | 1249971.0055
146 | 2712185.2707 | 1249758.8549
147 | 2712167.982 | 1249749.8894
148 | 2710755.2041 | 1250119.1793
149 | 2710540.1722 | 1250446.8389
150 | 2710472.171 | 1250295.4265
151 | 2710472.6198 | 1250290.5688
152 | 2710470.7796 | 1250310.4835
153 | 2710474.6397 | 1250268.7102
154 | 2710487.5323 | 1250317.9352
155 | 2710541.8979 | 1250438.4988
156 | 2712156.2825 | 1249744.1422
157 | 2711477.4485 | 1249765.3609
158 | 2711495.2344 | 1249739.8721
159 | 2711533.6585 | 1249678.3701
160 | 2711360.3074 | 1249506.6925
161 | 2711365.2256 | 1249496.7057
162 | 2711351.9216 | 1249506.5364
163 | 2711179.3184 | 1249555.9021
164 | 2711135.6424 | 1249544.3626
165 | 2711111.2733 | 1249538.2452
166 | 2711147.6475 | 1249534.4467
167 | 2711286.5462 | 1249516.3151
168 | 2711232.2228 | 1249524.013
169 | 2711307.1316 | 1249509.4197
170 | 2711382.7187 | 1249454.5144
171 | 2711152.1503 | 1249530.7276
172 | 2711171.4586 | 1249513.9249
173 | 2711059.8988 | 1249558.394
174 | 2711225.0158 | 1249516.0935
175 | 2711225.297 | 1249523.2379
176 | 2711189.5183 | 1249509.7169
177 | 2711233.6668 | 1249534.2492
178 | 2711321.5219 | 1249505.4754
179 | 2711416.3318 | 1249443.078
180 | 2711368.8257 | 1249489.3955
181 | 2711217.8408 | 1249530.0859
182 | 2711042.7513 | 1249574.5486
183 | 2711081.2064 | 1249572.9879
184 | 2711429.7102 | 1249437.5207
185 | 2711456.8408 | 1249405.3226
186 | 2711474.5198 | 1249378.9347
187 | 2710718.4865 | 1249775.8846
188 | 2710713.589 | 1249788.9893
189 | 2711369.6512 | 1249487.7191

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1