## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3102-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3102-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3102-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3102-1_0_3_node_40 | 0.4 | n |  | TRUE
4 | bus_LV_3102-1_0_3_node_37 | 0.4 | n |  | TRUE
5 | bus_LV_3102-1_0_3_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_3102-1_0_3_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_3102-1_0_3_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_3102-1_0_3_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_3102-1_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_3102-1_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_3102-1_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_3102-1_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_3102-1_0_3_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_3102-1_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_3102-1_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_3102-1_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_3102-1_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_3102-1_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_3102-1_0_3_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_3102-1_0_3_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_3102-1_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_3102-1_0_3_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_3102-1_0_3_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_3102-1_0_3_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_3102-1_0_3_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_3102-1_0_3_node_63 | 0.4 | n |  | TRUE
27 | bus_LV_3102-1_0_3_node_66 | 0.4 | n |  | TRUE
28 | bus_LV_3102-1_0_3_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_3102-1_0_3_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_3102-1_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_3102-1_0_3_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_3102-1_0_3_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_3102-1_0_3_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_3102-1_0_3_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_3102-1_0_3_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_3102-1_0_3_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_3102-1_0_3_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_3102-1_0_3_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_3102-1_0_3_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_3102-1_0_3_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_3102-1_0_3_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_3102-1_0_3_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_3102-1_0_3_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_3102-1_0_3_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_3102-1_0_3_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_3102-1_0_3_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_3102-1_0_3_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_3102-1_0_3_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_3102-1_0_3_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_3102-1_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_3102-1_0_3_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_3102-1_0_3_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_3102-1_0_3_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_3102-1_0_3_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_3102-1_0_3_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_3102-1_0_3_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_3102-1_0_3_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_3102-1_0_3_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_3102-1_0_3_node_69 | 0.4 | n |  | TRUE
60 | bus_LV_3102-1_0_3_node_70 | 0.4 | n |  | TRUE
61 | bus_LV_3102-1_0_3_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_3102-1_0_3_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_3102-1_0_3_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_3102-1_0_3_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_3102-1_0_3_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_3102-1_0_3_node_72 | 0.4 | n |  | TRUE
67 | bus_LV_3102-1_0_3_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_3102-1_0_3_node_73 | 0.4 | n |  | TRUE
69 | bus_LV_3102-1_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_MV_39_0_node_65 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3102-1_0_3_load_0 | 0 | 0.00085116 | 0.00021332 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3102-1_0_3_load_1 | 1 | 0.0034776 | 0.00087158 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3102-1_0_3_load_40 | 3 | 0.0033832 | 0.00084792 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3102-1_0_3_load_37 | 4 | 0.0011367 | 0.0002849 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3102-1_0_3_load_39 | 5 | 0.0046093 | 0.0011552 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3102-1_0_3_load_35 | 7 | 0.0024809 | 0.00062177 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3102-1_0_3_load_4 | 8 | 0.0058507 | 0.0014663 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3102-1_0_3_load_5 | 9 | 0.0020968 | 0.00052551 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3102-1_0_3_load_60 | 13 | 0.0053709 | 0.0013461 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3102-1_0_3_load_9 | 14 | 0.0026638 | 0.00066762 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3102-1_0_3_load_13 | 17 | 0.0061912 | 0.0015516 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3102-1_0_3_load_14 | 18 | 0.0055392 | 0.0013882 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3102-1_0_3_load_58 | 19 | 0.0054537 | 0.0013668 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3102-1_0_3_load_43 | 20 | 0.0024005 | 0.00060162 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3102-1_0_3_load_19 | 21 | 0.0057841 | 0.0014496 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3102-1_0_3_load_59 | 22 | 0.0087235 | 0.0021863 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3102-1_0_3_load_49 | 25 | 0.0024102 | 0.00060405 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3102-1_0_3_load_63 | 26 | 0.0017831 | 0.00044689 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3102-1_0_3_load_66 | 27 | 0.0035369 | 0.00088643 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3102-1_0_3_load_71 | 28 | 0.0061692 | 0.0015461 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3102-1_0_3_load_25 | 29 | 0.0012743 | 0.00031936 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3102-1_0_3_load_20 | 30 | 0.0059828 | 0.0014994 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3102-1_0_3_load_15 | 31 | 0.0053734 | 0.0013467 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3102-1_0_3_load_17 | 33 | 0.0030782 | 0.00077146 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3102-1_0_3_load_18 | 34 | 0.0076339 | 0.0019132 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3102-1_0_3_load_48 | 35 | 0.0023093 | 0.00057876 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3102-1_0_3_load_54 | 37 | 0.0036486 | 0.00091443 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3102-1_0_3_load_21 | 39 | 0.0020126 | 0.00050441 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3102-1_0_3_load_22 | 40 | 0.0021086 | 0.00052846 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3102-1_0_3_load_23 | 41 | 0.0030013 | 0.00075219 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3102-1_0_3_load_26 | 42 | 0.002317 | 0.0005807 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3102-1_0_3_load_27 | 43 | 0.0030921 | 0.00077495 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3102-1_0_3_load_30 | 45 | 0.0023698 | 0.00059392 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3102-1_0_3_load_31 | 46 | 0.0034466 | 0.00086381 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3102-1_0_3_load_32 | 47 | 0.0022403 | 0.00056148 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3102-1_0_3_load_45 | 48 | 0.0024857 | 0.00062297 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3102-1_0_3_load_33 | 49 | 0.016469 | 0.0041276 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3102-1_0_3_load_44 | 50 | 0.0087992 | 0.0022053 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3102-1_0_3_load_56 | 53 | 0.0024521 | 0.00061456 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3102-1_0_3_load_62 | 54 | 0.0042683 | 0.0010697 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3102-1_0_3_load_36 | 55 | 0.0022106 | 0.00055403 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3102-1_0_3_load_38 | 56 | 0.0050661 | 0.0012697 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3102-1_0_3_load_69 | 59 | 0.0041172 | 0.0010319 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3102-1_0_3_load_70 | 60 | 0.00038967 | 9.7661e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3102-1_0_3_load_46 | 62 | 0.0028638 | 0.00071775 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3102-1_0_3_load_53 | 63 | 0.0051051 | 0.0012795 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3102-1_0_3_load_61 | 64 | 0.002625 | 0.0006579 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3102-1_0_3_load_55 | 65 | 0.0033799 | 0.00084709 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3102-1_0_3_load_72 | 66 | 0.0083397 | 0.0020901 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3102-1_0_3_load_65 | 67 | 0.00091257 | 0.00022871 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3102-1_0_3_load_73 | 68 | 0.00058911 | 0.00014765 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3102-1_0_3_load_67 | 69 | 0.0027961 | 0.00070078 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3102-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0082857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3102-1_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.036734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3102-1_0_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.12661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3102-1_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.11364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3102-1_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.011392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3102-1_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.013961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3102-1_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.020024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3102-1_0_3_line_7 | NAYY 4x150 SE | 5 | 57 | 0.044125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3102-1_0_3_line_8 | NAYY 4x150 SE | 6 | 43 | 0.035183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_3102-1_0_3_line_9 | NAYY 4x150 SE | 7 | 55 | 0.0023854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3102-1_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.042496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3102-1_0_3_line_11 | NAYY 4x150 SE | 8 | 10 | 0.028398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3102-1_0_3_line_12 | NAYY 4x150 SE | 9 | 11 | 0.0059873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3102-1_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.019116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3102-1_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.02997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3102-1_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.032787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3102-1_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.011941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3102-1_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.02827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3102-1_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.022301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3102-1_0_3_line_19 | NAYY 4x150 SE | 15 | 18 | 0.028256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3102-1_0_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.012902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3102-1_0_3_line_21 | NAYY 4x150 SE | 16 | 20 | 0.015435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3102-1_0_3_line_22 | NAYY 4x150 SE | 17 | 21 | 0.014553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3102-1_0_3_line_23 | NAYY 4x150 SE | 18 | 22 | 0.036014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3102-1_0_3_line_24 | NAYY 4x150 SE | 19 | 28 | 0.010272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3102-1_0_3_line_25 | NAYY 4x150 SE | 20 | 29 | 4.5409e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3102-1_0_3_line_26 | NAYY 4x150 SE | 21 | 30 | 0.018064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3102-1_0_3_line_27 | NAYY 4x150 SE | 23 | 24 | 0.012396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_3102-1_0_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.016247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_3102-1_0_3_line_29 | NAYY 4x150 SE | 24 | 64 | 0.070402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_3102-1_0_3_line_30 | NAYY 4x150 SE | 24 | 26 | 0.00925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3102-1_0_3_line_31 | NAYY 4x150 SE | 25 | 38 | 0.010728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_3102-1_0_3_line_32 | NAYY 4x150 SE | 26 | 27 | 0.14255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3102-1_0_3_line_33 | NAYY 4x150 SE | 27 | 69 | 0.0070789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3102-1_0_3_line_34 | NAYY 4x150 SE | 27 | 67 | 0.021817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3102-1_0_3_line_35 | NAYY 4x150 SE | 28 | 66 | 0.010662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3102-1_0_3_line_36 | NAYY 4x150 SE | 29 | 41 | 0.024208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3102-1_0_3_line_37 | NAYY 4x150 SE | 30 | 37 | 0.020922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_3102-1_0_3_line_38 | NAYY 4x150 SE | 31 | 32 | 0.011245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3102-1_0_3_line_39 | NAYY 4x150 SE | 32 | 33 | 0.017496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3102-1_0_3_line_40 | NAYY 4x150 SE | 32 | 34 | 0.013677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3102-1_0_3_line_41 | NAYY 4x150 SE | 34 | 35 | 0.025074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3102-1_0_3_line_42 | NAYY 4x150 SE | 35 | 36 | 0.018289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3102-1_0_3_line_43 | NAYY 4x150 SE | 36 | 40 | 0.038952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3102-1_0_3_line_44 | NAYY 4x150 SE | 37 | 38 | 0.011545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_3102-1_0_3_line_45 | NAYY 4x150 SE | 38 | 63 | 0.034272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3102-1_0_3_line_46 | NAYY 4x150 SE | 39 | 40 | 0.018518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3102-1_0_3_line_47 | NAYY 4x150 SE | 39 | 41 | 0.027342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3102-1_0_3_line_48 | NAYY 4x150 SE | 42 | 43 | 0.014031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_3102-1_0_3_line_49 | NAYY 4x150 SE | 42 | 44 | 0.025763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_3102-1_0_3_line_50 | NAYY 4x150 SE | 44 | 45 | 0.011844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_3102-1_0_3_line_51 | NAYY 4x150 SE | 44 | 46 | 0.01303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3102-1_0_3_line_52 | NAYY 4x150 SE | 45 | 47 | 0.01927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_3102-1_0_3_line_53 | NAYY 4x150 SE | 46 | 48 | 0.023344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3102-1_0_3_line_54 | NAYY 4x150 SE | 47 | 49 | 0.00010615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_3102-1_0_3_line_55 | NAYY 4x150 SE | 48 | 50 | 0.026471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3102-1_0_3_line_56 | NAYY 4x150 SE | 49 | 51 | 0.012396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_3102-1_0_3_line_57 | NAYY 4x150 SE | 51 | 52 | 0.074368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_3102-1_0_3_line_58 | NAYY 4x150 SE | 51 | 53 | 0.02418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3102-1_0_3_line_59 | NAYY 4x150 SE | 52 | 54 | 0.031149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_3102-1_0_3_line_60 | NAYY 4x150 SE | 54 | 64 | 0.024637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_3102-1_0_3_line_61 | NAYY 4x150 SE | 55 | 56 | 0.018636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3102-1_0_3_line_62 | NAYY 4x150 SE | 57 | 58 | 0.043914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3102-1_0_3_line_63 | NAYY 4x150 SE | 58 | 59 | 0.041661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3102-1_0_3_line_64 | NAYY 4x150 SE | 58 | 60 | 0.23031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3102-1_0_3_line_65 | NAYY 4x150 SE | 59 | 61 | 0.038241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3102-1_0_3_line_66 | NAYY 4x150 SE | 61 | 62 | 0.018186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3102-1_0_3_line_67 | NAYY 4x150 SE | 63 | 65 | 0.0081782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3102-1_0_3_line_68 | NAYY 4x150 SE | 67 | 68 | 0.080818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3102-1_0_3_trafo_20 | 0.25 MVA 20/0.4 kV | 70 | 30 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2743875.5832 | 1243699.3589 | 2743872.5346 | 1243700.9754 | 2743869.8178 | 1243704.9749
1 | 2743911.4935 | 1243693.3798 | 2743905.733 | 1243695.8201 | 2743893.5697 | 1243697.8826 | 2743879.9743 | 1243698.1976 | 2743875.5832 | 1243699.3589
2 | 2743819.9458 | 1243585.6266 | 2743875.5832 | 1243699.3589
3 | 2743963.9111 | 1243592.5553 | 2743911.4935 | 1243693.3798
4 | 2743809.2366 | 1243582.104 | 2743813.102 | 1243582.5591 | 2743819.9458 | 1243585.6266
5 | 2743976.7106 | 1243591.2346 | 2743968.5846 | 1243594.5516 | 2743966.1839 | 1243594.0818 | 2743963.9111 | 1243592.5553
6 | 2743963.9111 | 1243592.5553 | 2743961.2363 | 1243590.7587 | 2743946.1741 | 1243583.3135
7 | 2743765.2333 | 1243579.0069 | 2743783.3537 | 1243579.8134 | 2743803.8203 | 1243581.4664 | 2743809.2366 | 1243582.104
8 | 2743976.7106 | 1243591.2346 | 2743968.5698 | 1243583.0184 | 2743961.4088 | 1243570.2663 | 2743959.237 | 1243561.5408
9 | 2743944.0357 | 1243582.2565 | 2743946.1741 | 1243583.3135
10 | 2743906.6548 | 1243320.659 | 2743897.0481 | 1243308.7759 | 2743877.118 | 1243290.2427
11 | 2743924.4584 | 1243342.783 | 2743922.5153 | 1243340.278 | 2743906.6548 | 1243320.659
12 | 2743872.7335 | 1243286.1655 | 2743877.118 | 1243290.2427
13 | 2743936.1747 | 1243357.9144 | 2743924.4584 | 1243342.783
14 | 2743872.7335 | 1243286.1655 | 2743889.6022 | 1243268.7919 | 2743894.2342 | 1243265.3772
15 | 2743936.1747 | 1243357.9144 | 2743926.6928 | 1243360.0753 | 2743905.2969 | 1243358.9776 | 2743903.6846 | 1243359.2639
16 | 2743892.4506 | 1243362.9809 | 2743898.1885 | 1243360.2397 | 2743903.6846 | 1243359.2639
17 | 2743892.4506 | 1243362.9809 | 2743872.5658 | 1243383.1283
18 | 2743892.4506 | 1243362.9809 | 2743906.0231 | 1243380.6766
19 | 2743892.4506 | 1243362.9809 | 2743886.3267 | 1243355.7702 | 2743872.9956 | 1243342.5208
20 | 2743872.5658 | 1243383.1283 | 2743863.6094 | 1243373.8417
21 | 2743872.5658 | 1243383.1283 | 2743864.6496 | 1243396.3785
22 | 2743915.5691 | 1243391.657 | 2743906.905 | 1243381.8265 | 2743906.0231 | 1243380.6766
23 | 2743872.9956 | 1243342.5208 | 2743863.5702 | 1243333.1532 | 2743845.1528 | 1243319.8407
24 | 2743856.479 | 1243366.4484 | 2743863.6094 | 1243373.8417
25 | 2743864.6263 | 1243396.4175 | 2743864.6496 | 1243396.3785
26 | 2743927.8447 | 1243404.8905 | 2743923.8822 | 1243401.0893 | 2743915.5691 | 1243391.657
27 | 2743977.6926 | 1243407.8898 | 2743985.2573 | 1243417.7268
28 | 2743977.6926 | 1243407.8898 | 2743964.3059 | 1243417.0961
29 | 2743985.2573 | 1243417.7268 | 2743998.3971 | 1243433.7048 | 2744012.2172 | 1243450.9338 | 2744020.2096 | 1243460.9036 | 2744029.5015 | 1243472.488
30 | 2743985.2573 | 1243417.7268 | 2743988.0559 | 1243415.5149 | 2743992.5196 | 1243411.9978
31 | 2743954.8473 | 1243421.6482 | 2743958.6211 | 1243421.0058 | 2743964.3059 | 1243417.0961
32 | 2743992.5196 | 1243411.9978 | 2744079.9076 | 1243299.3746
33 | 2744079.9076 | 1243299.3746 | 2744074.4852 | 1243294.824
34 | 2744096.6196 | 1243313.3994 | 2744079.9076 | 1243299.3746
35 | 2743848.0064 | 1243360.0228 | 2743855.136 | 1243365.0558 | 2743856.479 | 1243366.4484
36 | 2743864.6263 | 1243396.4175 | 2743859.742 | 1243404.5927 | 2743853.1838 | 1243417.7316
37 | 2743944.1215 | 1243417.6997 | 2743938.0481 | 1243414.6787 | 2743927.8447 | 1243404.8905
38 | 2743802.7294 | 1243385.471 | 2743795.1671 | 1243377.1484
39 | 2743802.7294 | 1243385.471 | 2743790.9404 | 1243379.8691 | 2743786.5971 | 1243378.9276
40 | 2743802.7294 | 1243385.471 | 2743808.5542 | 1243397.8458
41 | 2743798.737 | 1243419.2427 | 2743806.7573 | 1243411.1366 | 2743808.8359 | 1243405.5597 | 2743808.5542 | 1243397.8458 | 2743808.5542 | 1243397.8458
42 | 2743789.7598 | 1243434.157 | 2743789.5198 | 1243431.2707 | 2743791.5949 | 1243426.4611 | 2743798.737 | 1243419.2427
43 | 2743789.7598 | 1243434.157 | 2743790.0544 | 1243437.6006 | 2743793.7759 | 1243443.1626 | 2743800.1538 | 1243447.3877 | 2743816.7656 | 1243448.6804 | 2743821.1203 | 1243447.5806
44 | 2743954.8473 | 1243421.6482 | 2743950.6001 | 1243420.9223 | 2743944.1215 | 1243417.6997
45 | 2743954.8473 | 1243421.6482 | 2743953.2638 | 1243435.478 | 2743954.1842 | 1243440.8609 | 2743957.217 | 1243444.2598 | 2743966.9698 | 1243447.6817
46 | 2743821.1203 | 1243447.5806 | 2743824.9216 | 1243446.6206 | 2743833.2118 | 1243442.7736 | 2743837.644 | 1243439.5885
47 | 2743853.1838 | 1243417.7316 | 2743846.1509 | 1243431.8216 | 2743842.239 | 1243436.2864 | 2743837.644 | 1243439.5885
48 | 2743959.237 | 1243561.5408 | 2743957.8607 | 1243556.0115 | 2743958.0301 | 1243547.6804
49 | 2743960.4013 | 1243522.0753 | 2743958.2491 | 1243536.9034 | 2743958.0301 | 1243547.6804
50 | 2743960.4013 | 1243522.0753 | 2743972.1852 | 1243523.2675
51 | 2743960.4013 | 1243522.0753 | 2743952.4971 | 1243521.2383 | 2743947.4487 | 1243520.6558
52 | 2743972.1852 | 1243523.2675 | 2743991.3572 | 1243525.2071
53 | 2743924.2582 | 1243517.9799 | 2743947.4487 | 1243520.6558
54 | 2743991.4628 | 1243525.2178 | 2743991.3572 | 1243525.2071
55 | 2743897.8196 | 1243516.75 | 2743922.7124 | 1243517.8015 | 2743924.2582 | 1243517.9799
56 | 2744003.7963 | 1243526.4656 | 2743991.4628 | 1243525.2178
57 | 2744003.7963 | 1243526.4656 | 2744040.416 | 1243530.2357 | 2744048.6147 | 1243529.8454 | 2744052.5158 | 1243528.3165 | 2744069.0055 | 1243521.8665 | 2744064.4068 | 1243516.005
58 | 2744003.7963 | 1243526.4656 | 2744001.9714 | 1243544.0041 | 2744002.7575 | 1243547.4375 | 2744004.7283 | 1243549.7319
59 | 2744064.4068 | 1243516.005 | 2744044.9169 | 1243491.7066
60 | 2744029.5015 | 1243472.488 | 2744044.9169 | 1243491.7066
61 | 2743927.3292 | 1243573.9985 | 2743944.0357 | 1243582.2565
62 | 2743765.2333 | 1243579.0069 | 2743728.0181 | 1243555.5171
63 | 2743728.0181 | 1243555.5171 | 2743733.4646 | 1243548.5649 | 2743738.8588 | 1243535.3501 | 2743739.5784 | 1243530.6187 | 2743738.8237 | 1243528.3762 | 2743736.2623 | 1243525.1778 | 2743733.261 | 1243523.5926 | 2743729.5684 | 1243522.3002
64 | 2743728.0181 | 1243555.5171 | 2743598.9087 | 1243746.2394
65 | 2743705.3112 | 1243495.3007 | 2743711.7011 | 1243509.3239 | 2743715.428 | 1243514.6635 | 2743718.4955 | 1243517.5738 | 2743722.0966 | 1243519.6852 | 2743729.5684 | 1243522.3002
66 | 2743705.3112 | 1243495.3007 | 2743714.4618 | 1243488.7052 | 2743718.4563 | 1243487.3785 | 2743721.1532 | 1243487.3334
67 | 2743974.6868 | 1243450.3893 | 2743966.9698 | 1243447.6817
68 | 2744096.6196 | 1243313.3994 | 2744140.9876 | 1243245.8495

## bus_geodata
| x | y | coords
0 | 2743875.5832 | 1243699.3589
1 | 2743869.8178 | 1243704.9749
2 | 2743911.4935 | 1243693.3798
3 | 2743819.9458 | 1243585.6266
4 | 2743963.9111 | 1243592.5553
5 | 2743809.2366 | 1243582.104
6 | 2743976.7106 | 1243591.2346
7 | 2743946.1741 | 1243583.3135
8 | 2743906.6548 | 1243320.659
9 | 2743877.118 | 1243290.2427
10 | 2743924.4584 | 1243342.783
11 | 2743872.7335 | 1243286.1655
12 | 2743936.1747 | 1243357.9144
13 | 2743894.2342 | 1243265.3772
14 | 2743903.6846 | 1243359.2639
15 | 2743892.4506 | 1243362.9809
16 | 2743872.5658 | 1243383.1283
17 | 2743906.0231 | 1243380.6766
18 | 2743872.9956 | 1243342.5208
19 | 2743863.6094 | 1243373.8417
20 | 2743864.6496 | 1243396.3785
21 | 2743915.5691 | 1243391.657
22 | 2743845.1528 | 1243319.8407
23 | 2743977.6926 | 1243407.8898
24 | 2743985.2573 | 1243417.7268
25 | 2743964.3059 | 1243417.0961
26 | 2743992.5196 | 1243411.9978
27 | 2744079.9076 | 1243299.3746
28 | 2743856.479 | 1243366.4484
29 | 2743864.6263 | 1243396.4175
30 | 2743927.8447 | 1243404.8905
31 | 2743795.1671 | 1243377.1484
32 | 2743802.7294 | 1243385.471
33 | 2743786.5971 | 1243378.9276
34 | 2743808.5542 | 1243397.8458
35 | 2743798.737 | 1243419.2427
36 | 2743789.7598 | 1243434.157
37 | 2743944.1215 | 1243417.6997
38 | 2743954.8473 | 1243421.6482
39 | 2743837.644 | 1243439.5885
40 | 2743821.1203 | 1243447.5806
41 | 2743853.1838 | 1243417.7316
42 | 2743958.0301 | 1243547.6804
43 | 2743959.237 | 1243561.5408
44 | 2743960.4013 | 1243522.0753
45 | 2743972.1852 | 1243523.2675
46 | 2743947.4487 | 1243520.6558
47 | 2743991.3572 | 1243525.2071
48 | 2743924.2582 | 1243517.9799
49 | 2743991.4628 | 1243525.2178
50 | 2743897.8196 | 1243516.75
51 | 2744003.7963 | 1243526.4656
52 | 2744064.4068 | 1243516.005
53 | 2744004.7283 | 1243549.7319
54 | 2744044.9169 | 1243491.7066
55 | 2743944.0357 | 1243582.2565
56 | 2743927.3292 | 1243573.9985
57 | 2743765.2333 | 1243579.0069
58 | 2743728.0181 | 1243555.5171
59 | 2743729.5684 | 1243522.3002
60 | 2743598.9087 | 1243746.2394
61 | 2743705.3112 | 1243495.3007
62 | 2743721.1532 | 1243487.3334
63 | 2743966.9698 | 1243447.6817
64 | 2744029.5015 | 1243472.488
65 | 2743974.6868 | 1243450.3893
66 | 2743848.0064 | 1243360.0228
67 | 2744096.6196 | 1243313.3994
68 | 2744140.9876 | 1243245.8495
69 | 2744074.4852 | 1243294.824
70 | 2743954.8473 | 1243421.6482

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1