## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3104-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3104-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3104-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3104-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3104-1_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3104-1_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3104-1_0_2_node_47 | 0.4 | n |  | TRUE
7 | bus_LV_3104-1_0_2_node_46 | 0.4 | n |  | TRUE
8 | bus_LV_3104-1_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_3104-1_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_3104-1_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_3104-1_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_3104-1_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_3104-1_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_3104-1_0_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_3104-1_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_3104-1_0_2_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_3104-1_0_2_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_3104-1_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_3104-1_0_2_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_3104-1_0_2_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_3104-1_0_2_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_3104-1_0_2_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_3104-1_0_2_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_3104-1_0_2_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_3104-1_0_2_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_3104-1_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_3104-1_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_3104-1_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_3104-1_0_2_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_3104-1_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_3104-1_0_2_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_3104-1_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_3104-1_0_2_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_3104-1_0_2_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_3104-1_0_2_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_3104-1_0_2_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_3104-1_0_2_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_3104-1_0_2_node_106 | 0.4 | n |  | TRUE
39 | bus_LV_3104-1_0_2_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_3104-1_0_2_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_3104-1_0_2_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_3104-1_0_2_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_3104-1_0_2_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_3104-1_0_2_node_48 | 0.4 | n |  | TRUE
45 | bus_LV_3104-1_0_2_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_3104-1_0_2_node_50 | 0.4 | n |  | TRUE
47 | bus_LV_3104-1_0_2_node_58 | 0.4 | n |  | TRUE
48 | bus_LV_3104-1_0_2_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_3104-1_0_2_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_3104-1_0_2_node_56 | 0.4 | n |  | TRUE
51 | bus_LV_3104-1_0_2_node_103 | 0.4 | n |  | TRUE
52 | bus_LV_3104-1_0_2_node_104 | 0.4 | n |  | TRUE
53 | bus_MV_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3104-1_0_2_load_0 | 0 | 0.00038645 | 9.6852e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3104-1_0_2_load_3 | 3 | 0.00035239 | 8.8317e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3104-1_0_2_load_5 | 5 | 0.00014743 | 3.6949e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3104-1_0_2_load_46 | 7 | 5.983e-05 | 1.4995e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3104-1_0_2_load_6 | 8 | 0.0010907 | 0.00027336 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3104-1_0_2_load_7 | 9 | 0.0027601 | 0.00069175 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3104-1_0_2_load_9 | 11 | 0.0027925 | 0.00069987 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3104-1_0_2_load_10 | 12 | 0.00085817 | 0.00021508 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3104-1_0_2_load_11 | 13 | 0.0022669 | 0.00056815 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3104-1_0_2_load_15 | 17 | 0.00018313 | 4.5896e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3104-1_0_2_load_17 | 20 | 0.0037289 | 0.00093456 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3104-1_0_2_load_18 | 21 | 0.00026859 | 6.7316e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3104-1_0_2_load_43 | 22 | 0.00015685 | 3.9309e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3104-1_0_2_load_27 | 24 | 0.0072189 | 0.0018092 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3104-1_0_2_load_21 | 27 | 0.0055201 | 0.0013835 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3104-1_0_2_load_23 | 29 | 0.0070681 | 0.0017714 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3104-1_0_2_load_24 | 30 | 0.002169 | 0.0005436 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3104-1_0_2_load_28 | 33 | 0.0097319 | 0.0024391 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3104-1_0_2_load_30 | 35 | 0.00085883 | 0.00021524 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3104-1_0_2_load_31 | 36 | 0.0012556 | 0.00031468 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3104-1_0_2_load_45 | 37 | 0.0051769 | 0.0012975 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3104-1_0_2_load_106 | 38 | 0.0016365 | 0.00041014 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3104-1_0_2_load_33 | 39 | 7.7261e-05 | 1.9363e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3104-1_0_2_load_34 | 40 | 0.00010452 | 2.6194e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3104-1_0_2_load_36 | 42 | 4.0197e-05 | 1.0074e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3104-1_0_2_load_37 | 43 | 0.00015973 | 4.0033e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3104-1_0_2_load_48 | 44 | 0.0091295 | 0.0022881 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3104-1_0_2_load_49 | 45 | 0.00030795 | 7.718e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3104-1_0_2_load_58 | 47 | 0.00071513 | 0.00017923 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3104-1_0_2_load_54 | 48 | 0.00015412 | 3.8627e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3104-1_0_2_load_56 | 50 | 0.00010231 | 2.5641e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3104-1_0_2_load_103 | 51 | 0.0033364 | 0.00083618 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3104-1_0_2_load_104 | 52 | 0.0025217 | 0.00063199 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3104-1_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3104-1_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.069084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3104-1_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.028547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3104-1_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.080525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3104-1_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.039417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3104-1_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.005382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3104-1_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.11586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3104-1_0_2_line_7 | NAYY 4x150 SE | 6 | 45 | 0.19262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3104-1_0_2_line_8 | NAYY 4x150 SE | 6 | 46 | 0.098225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3104-1_0_2_line_9 | NAYY 4x150 SE | 7 | 23 | 0.14422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3104-1_0_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.03766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3104-1_0_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.17738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3104-1_0_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.011905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3104-1_0_2_line_13 | NAYY 4x150 SE | 10 | 12 | 0.025823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3104-1_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.026786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3104-1_0_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.011225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3104-1_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.11602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3104-1_0_2_line_17 | NAYY 4x150 SE | 14 | 16 | 0.14854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3104-1_0_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.23717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3104-1_0_2_line_19 | NAYY 4x150 SE | 16 | 26 | 0.082061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3104-1_0_2_line_20 | NAYY 4x150 SE | 16 | 27 | 0.013664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3104-1_0_2_line_21 | NAYY 4x150 SE | 17 | 21 | 0.16809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3104-1_0_2_line_22 | NAYY 4x150 SE | 18 | 19 | 0.10386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3104-1_0_2_line_23 | NAYY 4x150 SE | 18 | 20 | 0.032419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3104-1_0_2_line_24 | NAYY 4x150 SE | 19 | 22 | 0.047931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3104-1_0_2_line_25 | NAYY 4x150 SE | 19 | 23 | 0.139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3104-1_0_2_line_26 | NAYY 4x150 SE | 20 | 24 | 0.04413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3104-1_0_2_line_27 | NAYY 4x150 SE | 21 | 25 | 0.14963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3104-1_0_2_line_28 | NAYY 4x150 SE | 23 | 44 | 0.14582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3104-1_0_2_line_29 | NAYY 4x150 SE | 24 | 32 | 0.026253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3104-1_0_2_line_30 | NAYY 4x150 SE | 25 | 39 | 0.10892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3104-1_0_2_line_31 | NAYY 4x150 SE | 26 | 28 | 0.026513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3104-1_0_2_line_32 | NAYY 4x150 SE | 26 | 29 | 0.010411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3104-1_0_2_line_33 | NAYY 4x150 SE | 28 | 30 | 0.012553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3104-1_0_2_line_34 | NAYY 4x150 SE | 29 | 31 | 0.054466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3104-1_0_2_line_35 | NAYY 4x150 SE | 30 | 32 | 0.21224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3104-1_0_2_line_36 | NAYY 4x150 SE | 31 | 34 | 0.29754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3104-1_0_2_line_37 | NAYY 4x150 SE | 32 | 33 | 0.016008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3104-1_0_2_line_38 | NAYY 4x150 SE | 33 | 35 | 0.29993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3104-1_0_2_line_39 | NAYY 4x150 SE | 34 | 36 | 0.035919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3104-1_0_2_line_40 | NAYY 4x150 SE | 35 | 37 | 0.34894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3104-1_0_2_line_41 | NAYY 4x150 SE | 35 | 38 | 0.39875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3104-1_0_2_line_42 | NAYY 4x150 SE | 38 | 52 | 0.12498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3104-1_0_2_line_43 | NAYY 4x150 SE | 39 | 40 | 0.0093953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3104-1_0_2_line_44 | NAYY 4x150 SE | 40 | 41 | 0.32937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3104-1_0_2_line_45 | NAYY 4x150 SE | 41 | 42 | 0.096904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3104-1_0_2_line_46 | NAYY 4x150 SE | 42 | 43 | 0.011364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3104-1_0_2_line_47 | NAYY 4x150 SE | 46 | 47 | 0.042987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3104-1_0_2_line_48 | NAYY 4x150 SE | 46 | 48 | 0.047957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3104-1_0_2_line_49 | NAYY 4x150 SE | 48 | 49 | 0.12257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3104-1_0_2_line_50 | NAYY 4x150 SE | 49 | 50 | 0.089749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3104-1_0_2_line_51 | NAYY 4x150 SE | 51 | 52 | 0.013987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3104-1_0_2_trafo_28 | 0.25 MVA 20/0.4 kV | 53 | 33 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2747643.6776 | 1248299.3425 | 2747635.5235 | 1248293.9455 | 2747626.0518 | 1248286.971
1 | 2747706.4382 | 1248313.1632 | 2747702.1872 | 1248317.5949 | 2747695.8549 | 1248319.4389 | 2747686.7744 | 1248319.079 | 2747676.7078 | 1248315.2357 | 2747643.6776 | 1248299.3425
2 | 2747706.4382 | 1248313.1632 | 2747714.0269 | 1248314.5647 | 2747723.2001 | 1248316.6619 | 2747731.9762 | 1248324.0765
3 | 2747706.4382 | 1248313.1632 | 2747707.0948 | 1248279.5588 | 2747711.8526 | 1248256.6223 | 2747712.219 | 1248233.1425
4 | 2747706.4382 | 1248313.1632 | 2747708.0012 | 1248337.7477 | 2747706.3928 | 1248352.4433
5 | 2747706.8822 | 1248232.331 | 2747712.219 | 1248233.1425
6 | 2747712.219 | 1248233.1425 | 2747755.4241 | 1248231.5842 | 2747774.3054 | 1248225.2487 | 2747785.7927 | 1248216.6713 | 2747812.6415 | 1248189.2477
7 | 2747706.8822 | 1248232.331 | 2747702.8389 | 1248220.8527 | 2747699.1765 | 1248207.7379 | 2747700.5701 | 1248195.4832 | 2747705.6517 | 1248180.7737 | 2747712.8987 | 1248166.4962 | 2747720.8696 | 1248152.5816 | 2747731.3518 | 1248139.4637 | 2747738.0834 | 1248131.3125 | 2747739.3601 | 1248123.7483 | 2747735.5621 | 1248116.0686 | 2747729.1911 | 1248109.7594 | 2747708.2311 | 1248091.8759 | 2747688.7387 | 1248073.306
8 | 2747706.8822 | 1248232.331 | 2747688.0751 | 1248229.938 | 2747617.8673 | 1248192.6209
9 | 2747952.8323 | 1248162.3968 | 2747901.689 | 1248164.4116 | 2747835.7609 | 1248179.9711 | 2747815.341 | 1248186.4904 | 2747812.6415 | 1248189.2477
10 | 2748234.3231 | 1247659.2916 | 2748245.0455 | 1247664.3337 | 2748268.775 | 1247674.4891
11 | 2748404.5589 | 1247768.0111 | 2748399.4469 | 1247745.2393 | 2748369.0615 | 1247710.5793 | 2748355.1575 | 1247700.0214 | 2748336.3975 | 1247692.9676 | 2748290.8088 | 1247683.9188 | 2748268.775 | 1247674.4891
12 | 2748404.5589 | 1247768.0111 | 2748398.7615 | 1247778.4089
13 | 2748404.5589 | 1247768.0111 | 2748424.8311 | 1247784.0076
14 | 2748398.7615 | 1247778.4089 | 2748385.7171 | 1247801.804
15 | 2748433.6428 | 1247790.9608 | 2748424.8311 | 1247784.0076
16 | 2748297.439 | 1247867.926 | 2748307.1597 | 1247852.0985 | 2748319.1607 | 1247842.6786 | 2748333.7992 | 1247836.8726 | 2748360.1182 | 1247830.525 | 2748376.4086 | 1247818.499 | 2748385.7171 | 1247801.804
17 | 2748433.6428 | 1247790.9608 | 2748437.7077 | 1247799.7265 | 2748435.9142 | 1247809.4797 | 2748412.1362 | 1247864.9039 | 2748409.5863 | 1247880.7218 | 2748410.7278 | 1247903.9279 | 2748417.1792 | 1247921.4839 | 2748424.9116 | 1247928.9289
18 | 2748297.439 | 1247867.926 | 2748267.2051 | 1247877.6347 | 2748223.0764 | 1247886.3953 | 2748169.1611 | 1247893.3989 | 2748135.8551 | 1247904.1992 | 2748092.9237 | 1247918.5849 | 2748071.3049 | 1247928.5767 | 2748069.6615 | 1247929.6216
19 | 2748424.9116 | 1247928.9289 | 2748426.7553 | 1247939.4851 | 2748425.4004 | 1247951.6405 | 2748414.8552 | 1247968.4036 | 2748406.0118 | 1247984.7979 | 2748402.2526 | 1248005.1565
20 | 2748424.9116 | 1247928.9289 | 2748437.9561 | 1247932.9979
21 | 2748069.6615 | 1247929.6216 | 2748048.7003 | 1247942.9481 | 2748003.1737 | 1247984.4064 | 2747978.8268 | 1248000.1804 | 2747961.1688 | 1248005.6004 | 2747947.6512 | 1248006.197 | 2747927.7275 | 1248000.7017
22 | 2748070.2192 | 1248110.7669 | 2748078.0524 | 1248104.8125 | 2748121.1203 | 1248083.1009 | 2748139.5786 | 1248071.9626 | 2748157.0816 | 1248054.9171
23 | 2748157.0816 | 1248054.9171 | 2748173.042 | 1248083.135
24 | 2748070.2192 | 1248110.7669 | 2748066.2218 | 1248107.4529 | 2748062.0828 | 1248107.0825 | 2748054.6654 | 1248109.6998 | 2748027.046 | 1248123.4009
25 | 2747952.8323 | 1248162.3968 | 2748015.5673 | 1248160.0381 | 2748029.7005 | 1248156.2651 | 2748044.815 | 1248145.5767 | 2748063.5941 | 1248116.4513 | 2748070.2192 | 1248110.7669
26 | 2748173.042 | 1248083.135 | 2748175.2223 | 1248086.9897 | 2748178.1297 | 1248110.6181 | 2748185.6522 | 1248121.016 | 2748188.2692 | 1248122.6041
27 | 2747789.2295 | 1248031.9707 | 2747833.2353 | 1248036.5387 | 2747847.8817 | 1248033.7012 | 2747864.7815 | 1248026.26 | 2747899.0129 | 1248001.3457 | 2747908.6802 | 1247997.8947 | 2747918.2564 | 1247998.0893 | 2747927.7275 | 1248000.7017
28 | 2747952.8323 | 1248162.3968 | 2747954.3322 | 1248168.5956 | 2747959.9463 | 1248173.1289 | 2747976.8799 | 1248182.7718 | 2747996.6116 | 1248195.3428 | 2748015.9087 | 1248207.4583 | 2748031.4624 | 1248219.7026 | 2748046.7512 | 1248233.4752 | 2748064.323 | 1248253.2439
29 | 2748210.7126 | 1248136.2235 | 2748188.2692 | 1248122.6041
30 | 2747789.2295 | 1248031.9707 | 2747761.9919 | 1248027.9548 | 2747753.9774 | 1248022.7056 | 2747750.7877 | 1248012.4498 | 2747756.3808 | 1247959.6724 | 2747756.3158 | 1247951.6744
31 | 2748402.2526 | 1248005.1565 | 2748395.0596 | 1248000.9169 | 2748386.0088 | 1248005.3835 | 2748381.6214 | 1248012.2135
32 | 2748402.2526 | 1248005.1565 | 2748410.484 | 1248011.5303
33 | 2748381.6214 | 1248012.2135 | 2748369.5009 | 1248015.4796
34 | 2748447.6919 | 1248050.8151 | 2748425.9127 | 1248023.4772 | 2748410.484 | 1248011.5303
35 | 2748210.7126 | 1248136.2235 | 2748290.6702 | 1248059.839 | 2748313.3458 | 1248021.5142 | 2748342.8386 | 1248022.6642 | 2748369.5009 | 1248015.4796
36 | 2748730.3273 | 1248045.0813 | 2748681.733 | 1248055.3613 | 2748659.4729 | 1248069.5055 | 2748602.6716 | 1248080.7479 | 2748585.9774 | 1248087.7918 | 2748574.2667 | 1248089.2553 | 2748545.9893 | 1248083.9417 | 2748512.9084 | 1248078.8415 | 2748477.2929 | 1248069.9522 | 2748464.472 | 1248064.159 | 2748447.6919 | 1248050.8151
37 | 2748210.7126 | 1248136.2235 | 2748224.483 | 1248144.3866
38 | 2748224.483 | 1248144.3866 | 2748244.2471 | 1248156.1029 | 2748268.8954 | 1248165.7284 | 2748296.6364 | 1248166.2004 | 2748337.3917 | 1248156.8999 | 2748349.8634 | 1248154.3095 | 2748373.2077 | 1248154.4493 | 2748385.9856 | 1248154.1132 | 2748410.4643 | 1248161.7553 | 2748427.3267 | 1248165.4698 | 2748447.9894 | 1248167.0887 | 2748480.5651 | 1248167.9051 | 2748516.4071 | 1248166.8986
39 | 2748764.97 | 1248035.2299 | 2748730.3273 | 1248045.0813
40 | 2748516.4071 | 1248166.8986 | 2748517.8118 | 1248166.8592 | 2748542.7943 | 1248171.8787 | 2748583.519 | 1248164.1139 | 2748600.136 | 1248160.1377 | 2748615.4162 | 1248148.0091 | 2748629.4025 | 1248134.7471 | 2748665.9392 | 1248109.3166 | 2748676.8214 | 1248105.6415 | 2748685.7978 | 1248108.0578 | 2748693.7837 | 1248114.4085 | 2748739.2768 | 1248162.3174 | 2748778.4416 | 1248207.6543 | 2748800.1284 | 1248216.0176
41 | 2748516.4071 | 1248166.8986 | 2748368.0301 | 1248537.017
42 | 2748368.0301 | 1248537.017 | 2748375.8677 | 1248567.0751 | 2748376.8867 | 1248579.1788 | 2748374.557 | 1248592.5555 | 2748378.4065 | 1248598.4352 | 2748388.8535 | 1248601.2326 | 2748393.4113 | 1248607.486 | 2748389.4714 | 1248616.3736 | 2748381.6226 | 1248625.3746 | 2748379.6716 | 1248639.3169 | 2748385.0002 | 1248643.6579
43 | 2747756.3158 | 1247951.6744 | 2747756.3158 | 1247951.6744 | 2747753.5899 | 1247948.2699 | 2747749.4873 | 1247945.3528
44 | 2747481.1697 | 1247869.9025 | 2747495.6248 | 1247855.3372 | 2747509.7375 | 1247846.0239 | 2747529.5176 | 1247838.8314 | 2747566.6617 | 1247833.1725 | 2747599.9239 | 1247824.7035 | 2747612.6937 | 1247825.0217 | 2747629.0865 | 1247830.0457 | 2747653.4635 | 1247842.7647 | 2747670.9243 | 1247856.7794 | 2747685.4703 | 1247874.047 | 2747705.8411 | 1247905.2951 | 2747715.8953 | 1247915.7221 | 2747744.6582 | 1247941.9191 | 2747749.4873 | 1247945.3528
45 | 2747481.1697 | 1247869.9025 | 2747469.563 | 1247875.9863 | 2747454.4647 | 1247880.8821 | 2747441.7082 | 1247880.3422 | 2747430.8236 | 1247875.022 | 2747404.9816 | 1247851.3238 | 2747399.1445 | 1247845.8801
46 | 2747390.8339 | 1247838.1295 | 2747399.1445 | 1247845.8801
47 | 2747632.3488 | 1248152.7214 | 2747631.4436 | 1248162.3636 | 2747622.7295 | 1248185.1905 | 2747617.8673 | 1248192.6209
48 | 2747617.8673 | 1248192.6209 | 2747604.5397 | 1248188.3406 | 2747590.8947 | 1248188.0006 | 2747570.9242 | 1248191.698
49 | 2747449.7271 | 1248192.9375 | 2747484.3745 | 1248198.8492 | 2747522.433 | 1248200.6755 | 2747570.9242 | 1248191.698
50 | 2747449.7271 | 1248192.9375 | 2747442.5056 | 1248196.5057 | 2747436.0902 | 1248197.436 | 2747424.2922 | 1248193.6279 | 2747405.9378 | 1248187.9106 | 2747394.326 | 1248185.4196 | 2747385.5432 | 1248184.3224 | 2747377.7481 | 1248187.8653 | 2747369.2341 | 1248193.5814 | 2747366.01 | 1248196.0249
51 | 2748394.5699 | 1248653.2188 | 2748392.7323 | 1248649.0641 | 2748387.024 | 1248645.3066 | 2748385.0002 | 1248643.6579

## bus_geodata
| x | y | coords
0 | 2747626.0518 | 1248286.971
1 | 2747643.6776 | 1248299.3425
2 | 2747706.4382 | 1248313.1632
3 | 2747731.9762 | 1248324.0765
4 | 2747712.219 | 1248233.1425
5 | 2747706.3928 | 1248352.4433
6 | 2747706.8822 | 1248232.331
7 | 2747812.6415 | 1248189.2477
8 | 2748234.3231 | 1247659.2916
9 | 2748268.775 | 1247674.4891
10 | 2748404.5589 | 1247768.0111
11 | 2748398.7615 | 1247778.4089
12 | 2748424.8311 | 1247784.0076
13 | 2748385.7171 | 1247801.804
14 | 2748433.6428 | 1247790.9608
15 | 2748297.439 | 1247867.926
16 | 2748424.9116 | 1247928.9289
17 | 2748069.6615 | 1247929.6216
18 | 2748157.0816 | 1248054.9171
19 | 2748070.2192 | 1248110.7669
20 | 2748173.042 | 1248083.135
21 | 2747927.7275 | 1248000.7017
22 | 2748027.046 | 1248123.4009
23 | 2747952.8323 | 1248162.3968
24 | 2748188.2692 | 1248122.6041
25 | 2747789.2295 | 1248031.9707
26 | 2748402.2526 | 1248005.1565
27 | 2748437.9561 | 1247932.9979
28 | 2748381.6214 | 1248012.2135
29 | 2748410.484 | 1248011.5303
30 | 2748369.5009 | 1248015.4796
31 | 2748447.6919 | 1248050.8151
32 | 2748210.7126 | 1248136.2235
33 | 2748224.483 | 1248144.3866
34 | 2748730.3273 | 1248045.0813
35 | 2748516.4071 | 1248166.8986
36 | 2748764.97 | 1248035.2299
37 | 2748800.1284 | 1248216.0176
38 | 2748368.0301 | 1248537.017
39 | 2747756.3158 | 1247951.6744
40 | 2747749.4873 | 1247945.3528
41 | 2747481.1697 | 1247869.9025
42 | 2747399.1445 | 1247845.8801
43 | 2747390.8339 | 1247838.1295
44 | 2748064.323 | 1248253.2439
45 | 2747688.7387 | 1248073.306
46 | 2747617.8673 | 1248192.6209
47 | 2747632.3488 | 1248152.7214
48 | 2747570.9242 | 1248191.698
49 | 2747449.7271 | 1248192.9375
50 | 2747366.01 | 1248196.0249
51 | 2748394.5699 | 1248653.2188
52 | 2748385.0002 | 1248643.6579
53 | 2748224.483 | 1248144.3866

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1