## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3274-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3274-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3274-7_0_6_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_3274-7_0_6_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_3274-7_0_6_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_3274-7_0_6_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_3274-7_0_6_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_3274-7_0_6_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_3274-7_0_6_node_50 | 0.4 | n |  | TRUE
9 | bus_LV_3274-7_0_6_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_3274-7_0_6_node_46 | 0.4 | n |  | TRUE
11 | bus_LV_3274-7_0_6_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_3274-7_0_6_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_3274-7_0_6_node_37 | 0.4 | n |  | TRUE
14 | bus_LV_3274-7_0_6_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_3274-7_0_6_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_3274-7_0_6_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_3274-7_0_6_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_3274-7_0_6_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_3274-7_0_6_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_3274-7_0_6_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_3274-7_0_6_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_3274-7_0_6_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_3274-7_0_6_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_3274-7_0_6_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_3274-7_0_6_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_3274-7_0_6_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_3274-7_0_6_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_3274-7_0_6_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_3274-7_0_6_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_3274-7_0_6_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_3274-7_0_6_node_166 | 0.4 | n |  | TRUE
32 | bus_LV_3274-7_0_6_node_173 | 0.4 | n |  | TRUE
33 | bus_LV_3274-7_0_6_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_3274-7_0_6_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_3274-7_0_6_node_60 | 0.4 | n |  | TRUE
36 | bus_LV_3274-7_0_6_node_61 | 0.4 | n |  | TRUE
37 | bus_LV_3274-7_0_6_node_172 | 0.4 | n |  | TRUE
38 | bus_LV_3274-7_0_6_node_63 | 0.4 | n |  | TRUE
39 | bus_LV_3274-7_0_6_node_164 | 0.4 | n |  | TRUE
40 | bus_LV_3274-7_0_6_node_167 | 0.4 | n |  | TRUE
41 | bus_LV_3274-7_0_6_node_163 | 0.4 | n |  | TRUE
42 | bus_LV_3274-7_0_6_node_165 | 0.4 | n |  | TRUE
43 | bus_LV_3274-7_0_6_node_160 | 0.4 | n |  | TRUE
44 | bus_LV_3274-7_0_6_node_168 | 0.4 | n |  | TRUE
45 | bus_LV_3274-7_0_6_node_169 | 0.4 | n |  | TRUE
46 | bus_LV_3274-7_0_6_node_170 | 0.4 | n |  | TRUE
47 | bus_LV_3274-7_0_6_node_171 | 0.4 | n |  | TRUE
48 | bus_LV_3274-7_0_6_node_161 | 0.4 | n |  | TRUE
49 | bus_LV_3274-7_0_6_node_17 | 0.4 | n |  | TRUE
50 | bus_LV_3274-7_0_6_node_8 | 0.4 | n |  | TRUE
51 | bus_LV_3274-7_0_6_node_2 | 0.4 | n |  | TRUE
52 | bus_LV_3274-7_0_6_node_3 | 0.4 | n |  | TRUE
53 | bus_LV_3274-7_0_6_node_140 | 0.4 | n |  | TRUE
54 | bus_LV_3274-7_0_6_node_85 | 0.4 | n |  | TRUE
55 | bus_LV_3274-7_0_6_node_138 | 0.4 | n |  | TRUE
56 | bus_LV_3274-7_0_6_node_86 | 0.4 | n |  | TRUE
57 | bus_LV_3274-7_0_6_node_131 | 0.4 | n |  | TRUE
58 | bus_LV_3274-7_0_6_node_5 | 0.4 | n |  | TRUE
59 | bus_LV_3274-7_0_6_node_123 | 0.4 | n |  | TRUE
60 | bus_LV_3274-7_0_6_node_6 | 0.4 | n |  | TRUE
61 | bus_LV_3274-7_0_6_node_7 | 0.4 | n |  | TRUE
62 | bus_LV_3274-7_0_6_node_130 | 0.4 | n |  | TRUE
63 | bus_LV_3274-7_0_6_node_21 | 0.4 | n |  | TRUE
64 | bus_LV_3274-7_0_6_node_105 | 0.4 | n |  | TRUE
65 | bus_LV_3274-7_0_6_node_104 | 0.4 | n |  | TRUE
66 | bus_LV_3274-7_0_6_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_3274-7_0_6_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_3274-7_0_6_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_3274-7_0_6_node_143 | 0.4 | n |  | TRUE
70 | bus_LV_3274-7_0_6_node_144 | 0.4 | n |  | TRUE
71 | bus_LV_3274-7_0_6_node_146 | 0.4 | n |  | TRUE
72 | bus_LV_3274-7_0_6_node_147 | 0.4 | n |  | TRUE
73 | bus_LV_3274-7_0_6_node_148 | 0.4 | n |  | TRUE
74 | bus_LV_3274-7_0_6_node_153 | 0.4 | n |  | TRUE
75 | bus_LV_3274-7_0_6_node_149 | 0.4 | n |  | TRUE
76 | bus_LV_3274-7_0_6_node_150 | 0.4 | n |  | TRUE
77 | bus_LV_3274-7_0_6_node_151 | 0.4 | n |  | TRUE
78 | bus_LV_3274-7_0_6_node_152 | 0.4 | n |  | TRUE
79 | bus_LV_3274-7_0_6_node_154 | 0.4 | n |  | TRUE
80 | bus_LV_3274-7_0_6_node_156 | 0.4 | n |  | TRUE
81 | bus_LV_3274-7_0_6_node_157 | 0.4 | n |  | TRUE
82 | bus_LV_3274-7_0_6_node_158 | 0.4 | n |  | TRUE
83 | bus_LV_3274-7_0_6_node_159 | 0.4 | n |  | TRUE
84 | bus_LV_3274-7_0_6_node_162 | 0.4 | n |  | TRUE
85 | bus_LV_3274-7_0_6_node_175 | 0.4 | n |  | TRUE
86 | bus_LV_3274-7_0_6_node_174 | 0.4 | n |  | TRUE
87 | bus_LV_3274-7_0_6_node_107 | 0.4 | n |  | TRUE
88 | bus_LV_3274-7_0_6_node_10 | 0.4 | n |  | TRUE
89 | bus_LV_3274-7_0_6_node_11 | 0.4 | n |  | TRUE
90 | bus_LV_3274-7_0_6_node_12 | 0.4 | n |  | TRUE
91 | bus_LV_3274-7_0_6_node_13 | 0.4 | n |  | TRUE
92 | bus_LV_3274-7_0_6_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_3274-7_0_6_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_3274-7_0_6_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_3274-7_0_6_node_14 | 0.4 | n |  | TRUE
96 | bus_LV_3274-7_0_6_node_15 | 0.4 | n |  | TRUE
97 | bus_LV_3274-7_0_6_node_16 | 0.4 | n |  | TRUE
98 | bus_LV_3274-7_0_6_node_122 | 0.4 | n |  | TRUE
99 | bus_LV_3274-7_0_6_node_118 | 0.4 | n |  | TRUE
100 | bus_LV_3274-7_0_6_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_3274-7_0_6_node_139 | 0.4 | n |  | TRUE
102 | bus_LV_3274-7_0_6_node_18 | 0.4 | n |  | TRUE
103 | bus_LV_3274-7_0_6_node_19 | 0.4 | n |  | TRUE
104 | bus_LV_3274-7_0_6_node_20 | 0.4 | n |  | TRUE
105 | bus_LV_3274-7_0_6_node_22 | 0.4 | n |  | TRUE
106 | bus_LV_3274-7_0_6_node_23 | 0.4 | n |  | TRUE
107 | bus_LV_3274-7_0_6_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_3274-7_0_6_node_119 | 0.4 | n |  | TRUE
109 | bus_LV_3274-7_0_6_node_125 | 0.4 | n |  | TRUE
110 | bus_LV_3274-7_0_6_node_117 | 0.4 | n |  | TRUE
111 | bus_LV_3274-7_0_6_node_128 | 0.4 | n |  | TRUE
112 | bus_LV_3274-7_0_6_node_28 | 0.4 | n |  | TRUE
113 | bus_LV_3274-7_0_6_node_124 | 0.4 | n |  | TRUE
114 | bus_LV_3274-7_0_6_node_24 | 0.4 | n |  | TRUE
115 | bus_LV_3274-7_0_6_node_25 | 0.4 | n |  | TRUE
116 | bus_LV_3274-7_0_6_node_26 | 0.4 | n |  | TRUE
117 | bus_LV_3274-7_0_6_node_27 | 0.4 | n |  | TRUE
118 | bus_LV_3274-7_0_6_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_3274-7_0_6_node_65 | 0.4 | n |  | TRUE
120 | bus_LV_3274-7_0_6_node_66 | 0.4 | n |  | TRUE
121 | bus_LV_3274-7_0_6_node_67 | 0.4 | n |  | TRUE
122 | bus_LV_3274-7_0_6_node_70 | 0.4 | n |  | TRUE
123 | bus_LV_3274-7_0_6_node_72 | 0.4 | n |  | TRUE
124 | bus_LV_3274-7_0_6_node_68 | 0.4 | n |  | TRUE
125 | bus_LV_3274-7_0_6_node_69 | 0.4 | n |  | TRUE
126 | bus_LV_3274-7_0_6_node_73 | 0.4 | n |  | TRUE
127 | bus_LV_3274-7_0_6_node_74 | 0.4 | n |  | TRUE
128 | bus_LV_3274-7_0_6_node_76 | 0.4 | n |  | TRUE
129 | bus_LV_3274-7_0_6_node_75 | 0.4 | n |  | TRUE
130 | bus_LV_3274-7_0_6_node_78 | 0.4 | n |  | TRUE
131 | bus_LV_3274-7_0_6_node_81 | 0.4 | n |  | TRUE
132 | bus_LV_3274-7_0_6_node_77 | 0.4 | n |  | TRUE
133 | bus_LV_3274-7_0_6_node_82 | 0.4 | n |  | TRUE
134 | bus_LV_3274-7_0_6_node_84 | 0.4 | n |  | TRUE
135 | bus_LV_3274-7_0_6_node_87 | 0.4 | n |  | TRUE
136 | bus_LV_3274-7_0_6_node_91 | 0.4 | n |  | TRUE
137 | bus_LV_3274-7_0_6_node_89 | 0.4 | n |  | TRUE
138 | bus_LV_3274-7_0_6_node_90 | 0.4 | n |  | TRUE
139 | bus_LV_3274-7_0_6_node_92 | 0.4 | n |  | TRUE
140 | bus_LV_3274-7_0_6_node_93 | 0.4 | n |  | TRUE
141 | bus_LV_3274-7_0_6_node_106 | 0.4 | n |  | TRUE
142 | bus_LV_3274-7_0_6_node_101 | 0.4 | n |  | TRUE
143 | bus_LV_3274-7_0_6_node_94 | 0.4 | n |  | TRUE
144 | bus_LV_3274-7_0_6_node_95 | 0.4 | n |  | TRUE
145 | bus_LV_3274-7_0_6_node_96 | 0.4 | n |  | TRUE
146 | bus_LV_3274-7_0_6_node_97 | 0.4 | n |  | TRUE
147 | bus_LV_3274-7_0_6_node_98 | 0.4 | n |  | TRUE
148 | bus_LV_3274-7_0_6_node_99 | 0.4 | n |  | TRUE
149 | bus_LV_3274-7_0_6_node_115 | 0.4 | n |  | TRUE
150 | bus_LV_3274-7_0_6_node_100 | 0.4 | n |  | TRUE
151 | bus_LV_3274-7_0_6_node_114 | 0.4 | n |  | TRUE
152 | bus_LV_3274-7_0_6_node_108 | 0.4 | n |  | TRUE
153 | bus_LV_3274-7_0_6_node_109 | 0.4 | n |  | TRUE
154 | bus_LV_3274-7_0_6_node_110 | 0.4 | n |  | TRUE
155 | bus_LV_3274-7_0_6_node_111 | 0.4 | n |  | TRUE
156 | bus_LV_3274-7_0_6_node_113 | 0.4 | n |  | TRUE
157 | bus_LV_3274-7_0_6_node_116 | 0.4 | n |  | TRUE
158 | bus_LV_3274-7_0_6_node_121 | 0.4 | n |  | TRUE
159 | bus_LV_3274-7_0_6_node_120 | 0.4 | n |  | TRUE
160 | bus_LV_3274-7_0_6_node_127 | 0.4 | n |  | TRUE
161 | bus_LV_3274-7_0_6_node_134 | 0.4 | n |  | TRUE
162 | bus_LV_3274-7_0_6_node_126 | 0.4 | n |  | TRUE
163 | bus_LV_3274-7_0_6_node_129 | 0.4 | n |  | TRUE
164 | bus_LV_3274-7_0_6_node_135 | 0.4 | n |  | TRUE
165 | bus_LV_3274-7_0_6_node_132 | 0.4 | n |  | TRUE
166 | bus_LV_3274-7_0_6_node_133 | 0.4 | n |  | TRUE
167 | bus_LV_3274-7_0_6_node_136 | 0.4 | n |  | TRUE
168 | bus_LV_3274-7_0_6_node_137 | 0.4 | n |  | TRUE
169 | bus_LV_3274-7_0_6_node_141 | 0.4 | n |  | TRUE
170 | bus_LV_3274-7_0_6_node_142 | 0.4 | n |  | TRUE
171 | bus_MV_49_1_node_220 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3274-7_0_6_load_0 | 0 | 0.01363 | 0.0034161 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3274-7_0_6_load_1 | 1 | 0.0049361 | 0.0012371 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3274-7_0_6_load_29 | 3 | 0.00098232 | 0.00024619 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3274-7_0_6_load_30 | 4 | 0.0023726 | 0.00059463 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3274-7_0_6_load_31 | 5 | 0.0017542 | 0.00043964 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3274-7_0_6_load_32 | 6 | 0.0021885 | 0.00054849 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3274-7_0_6_load_50 | 8 | 0.0042226 | 0.0010583 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3274-7_0_6_load_58 | 9 | 0.0010389 | 0.00026037 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3274-7_0_6_load_46 | 10 | 0.001526 | 0.00038245 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3274-7_0_6_load_34 | 11 | 0.0011698 | 0.00029317 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3274-7_0_6_load_35 | 12 | 0.00074124 | 0.00018577 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3274-7_0_6_load_36 | 14 | 0.0016623 | 0.0004166 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3274-7_0_6_load_39 | 17 | 0.0032731 | 0.00082031 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3274-7_0_6_load_40 | 18 | 0.0038629 | 0.00096812 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3274-7_0_6_load_41 | 19 | 0.0031299 | 0.00078443 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3274-7_0_6_load_42 | 20 | 0.0030031 | 0.00075264 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3274-7_0_6_load_48 | 21 | 0.0019057 | 0.00047763 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3274-7_0_6_load_43 | 22 | 0.0014198 | 0.00035585 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3274-7_0_6_load_44 | 23 | 0.0004683 | 0.00011737 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3274-7_0_6_load_45 | 24 | 0.0014917 | 0.00037386 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3274-7_0_6_load_57 | 26 | 0.0017402 | 0.00043614 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3274-7_0_6_load_54 | 27 | 0.0037532 | 0.00094063 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3274-7_0_6_load_49 | 28 | 0.0012677 | 0.00031771 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3274-7_0_6_load_55 | 29 | 0.0014777 | 0.00037034 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3274-7_0_6_load_166 | 31 | 0.0020046 | 0.0005024 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3274-7_0_6_load_173 | 32 | 0.0012206 | 0.00030592 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3274-7_0_6_load_59 | 34 | 0.0019458 | 0.00048766 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3274-7_0_6_load_60 | 35 | 0.0022325 | 0.00055951 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3274-7_0_6_load_61 | 36 | 0.0021298 | 0.00053377 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3274-7_0_6_load_172 | 37 | 0.0010508 | 0.00026335 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3274-7_0_6_load_63 | 38 | 0.00046778 | 0.00011724 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3274-7_0_6_load_164 | 39 | 0.0016178 | 0.00040547 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3274-7_0_6_load_167 | 40 | 0.00093632 | 0.00023467 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3274-7_0_6_load_163 | 41 | 0.00098128 | 0.00024593 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3274-7_0_6_load_165 | 42 | 0.0014754 | 0.00036978 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3274-7_0_6_load_160 | 43 | 0.0012756 | 0.0003197 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3274-7_0_6_load_168 | 44 | 0.0014543 | 0.00036449 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3274-7_0_6_load_169 | 45 | 0.0015332 | 0.00038426 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3274-7_0_6_load_170 | 46 | 0.0017956 | 0.00045001 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3274-7_0_6_load_171 | 47 | 0.001138 | 0.00028521 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3274-7_0_6_load_161 | 48 | 0.001307 | 0.00032756 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3274-7_0_6_load_2 | 51 | 0.0018338 | 0.00045959 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3274-7_0_6_load_3 | 52 | 0.0013711 | 0.00034363 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3274-7_0_6_load_140 | 53 | 0.0055808 | 0.0013987 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3274-7_0_6_load_85 | 54 | 0.003282 | 0.00082255 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3274-7_0_6_load_131 | 57 | 0.0010983 | 0.00027525 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3274-7_0_6_load_5 | 58 | 0.0015197 | 0.00038088 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3274-7_0_6_load_6 | 60 | 0.00089311 | 0.00022383 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3274-7_0_6_load_7 | 61 | 0.0017629 | 0.00044181 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3274-7_0_6_load_130 | 62 | 0.0010226 | 0.00025628 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3274-7_0_6_load_21 | 63 | 0.00099173 | 0.00024855 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3274-7_0_6_load_105 | 64 | 0.0025813 | 0.00064694 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3274-7_0_6_load_104 | 65 | 0.0028502 | 0.00071433 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3274-7_0_6_load_51 | 66 | 0.0015717 | 0.0003939 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3274-7_0_6_load_53 | 68 | 0.0015178 | 0.00038039 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3274-7_0_6_load_143 | 69 | 0.0020734 | 0.00051964 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3274-7_0_6_load_144 | 70 | 0.0023515 | 0.00058934 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3274-7_0_6_load_146 | 71 | 0.0027969 | 0.00070098 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3274-7_0_6_load_147 | 72 | 0.0021416 | 0.00053674 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3274-7_0_6_load_153 | 74 | 0.0015393 | 0.00038579 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3274-7_0_6_load_149 | 75 | 0.0016818 | 0.00042151 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3274-7_0_6_load_151 | 77 | 0.0025961 | 0.00065065 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3274-7_0_6_load_152 | 78 | 0.001716 | 0.00043006 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3274-7_0_6_load_154 | 79 | 0.0013059 | 0.00032729 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3274-7_0_6_load_156 | 80 | 0.00078653 | 0.00019712 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3274-7_0_6_load_157 | 81 | 0.0015292 | 0.00038326 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3274-7_0_6_load_159 | 83 | 0.00090713 | 0.00022735 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3274-7_0_6_load_162 | 84 | 0.0013515 | 0.00033871 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3274-7_0_6_load_175 | 85 | 0.00080581 | 0.00020195 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3274-7_0_6_load_107 | 87 | 0.0028713 | 0.00071962 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3274-7_0_6_load_10 | 88 | 0.0023958 | 0.00060044 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3274-7_0_6_load_12 | 90 | 0.0007328 | 0.00018366 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3274-7_0_6_load_80 | 92 | 0.0011383 | 0.00028528 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3274-7_0_6_load_83 | 93 | 0.001037 | 0.00025991 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3274-7_0_6_load_79 | 94 | 0.00053801 | 0.00013484 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3274-7_0_6_load_15 | 96 | 0.0014826 | 0.00037157 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3274-7_0_6_load_16 | 97 | 0.00050674 | 0.000127 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3274-7_0_6_load_118 | 99 | 0.0017577 | 0.00044052 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3274-7_0_6_load_71 | 100 | 0.00072308 | 0.00018122 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3274-7_0_6_load_139 | 101 | 0.0018112 | 0.00045393 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3274-7_0_6_load_18 | 102 | 0.0013143 | 0.0003294 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3274-7_0_6_load_19 | 103 | 0.0010706 | 0.00026833 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3274-7_0_6_load_22 | 105 | 0.0021273 | 0.00053316 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3274-7_0_6_load_125 | 109 | 0.0034388 | 0.00086184 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3274-7_0_6_load_128 | 111 | 0.0033955 | 0.000851 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3274-7_0_6_load_124 | 113 | 0.00061297 | 0.00015362 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3274-7_0_6_load_24 | 114 | 0.0023498 | 0.00058891 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3274-7_0_6_load_25 | 115 | 0.0040926 | 0.0010257 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3274-7_0_6_load_26 | 116 | 0.0029996 | 0.00075176 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3274-7_0_6_load_27 | 117 | 0.0017541 | 0.00043961 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3274-7_0_6_load_65 | 119 | 0.00097707 | 0.00024488 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3274-7_0_6_load_66 | 120 | 0.0018454 | 0.0004625 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3274-7_0_6_load_72 | 123 | 0.00029203 | 7.319e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3274-7_0_6_load_68 | 124 | 0.0010816 | 0.00027109 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3274-7_0_6_load_69 | 125 | 0.00026228 | 6.5733e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3274-7_0_6_load_73 | 126 | 0.00064496 | 0.00016164 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3274-7_0_6_load_76 | 128 | 0.0010086 | 0.00025278 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3274-7_0_6_load_75 | 129 | 0.0002146 | 5.3784e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3274-7_0_6_load_78 | 130 | 0.00074183 | 0.00018592 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3274-7_0_6_load_81 | 131 | 0.00028579 | 7.1626e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3274-7_0_6_load_77 | 132 | 0.00046587 | 0.00011676 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3274-7_0_6_load_84 | 134 | 0.00080195 | 0.00020099 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3274-7_0_6_load_87 | 135 | 0.0011405 | 0.00028584 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3274-7_0_6_load_89 | 137 | 0.0012714 | 0.00031864 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3274-7_0_6_load_90 | 138 | 0.0016876 | 0.00042296 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3274-7_0_6_load_92 | 139 | 0.0011029 | 0.00027642 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3274-7_0_6_load_106 | 141 | 0.001407 | 0.00035263 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3274-7_0_6_load_101 | 142 | 0.00099538 | 0.00024947 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3274-7_0_6_load_94 | 143 | 0.0029428 | 0.00073753 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3274-7_0_6_load_95 | 144 | 0.0014352 | 0.00035969 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3274-7_0_6_load_96 | 145 | 0.0014302 | 0.00035845 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3274-7_0_6_load_98 | 147 | 0.0017184 | 0.00043066 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3274-7_0_6_load_99 | 148 | 0.0019875 | 0.00049812 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3274-7_0_6_load_115 | 149 | 0.0017106 | 0.00042871 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3274-7_0_6_load_100 | 150 | 0.0015772 | 0.00039529 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3274-7_0_6_load_114 | 151 | 0.0014406 | 0.00036104 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3274-7_0_6_load_108 | 152 | 0.0021422 | 0.00053689 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3274-7_0_6_load_109 | 153 | 0.0013547 | 0.00033952 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3274-7_0_6_load_110 | 154 | 0.0010709 | 0.0002684 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3274-7_0_6_load_111 | 155 | 0.0014374 | 0.00036025 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3274-7_0_6_load_116 | 157 | 0.0013057 | 0.00032724 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3274-7_0_6_load_121 | 158 | 0.001744 | 0.00043708 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3274-7_0_6_load_120 | 159 | 0.0023418 | 0.0005869 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_3274-7_0_6_load_127 | 160 | 0.0033424 | 0.00083767 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_3274-7_0_6_load_126 | 162 | 0.00067175 | 0.00016836 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_3274-7_0_6_load_129 | 163 | 0.003456 | 0.00086616 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_3274-7_0_6_load_135 | 164 | 0.0012975 | 0.00032517 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_3274-7_0_6_load_132 | 165 | 0.00066162 | 0.00016582 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_3274-7_0_6_load_133 | 166 | 0.00087473 | 0.00021923 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_3274-7_0_6_load_136 | 167 | 0.00092256 | 0.00023121 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_3274-7_0_6_load_137 | 168 | 0.0010012 | 0.00025094 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_3274-7_0_6_load_141 | 169 | 0.0018225 | 0.00045676 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_3274-7_0_6_load_142 | 170 | 0.00088666 | 0.00022222 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3274-7_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.045023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3274-7_0_6_line_1 | NAYY 4x150 SE | 1 | 2 | 0.013489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3274-7_0_6_line_2 | NAYY 4x150 SE | 2 | 49 | 0.036472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_3274-7_0_6_line_3 | NAYY 4x150 SE | 2 | 50 | 0.035285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_3274-7_0_6_line_4 | NAYY 4x150 SE | 3 | 4 | 0.003867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3274-7_0_6_line_5 | NAYY 4x150 SE | 3 | 5 | 0.0243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3274-7_0_6_line_6 | NAYY 4x150 SE | 4 | 6 | 0.01671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3274-7_0_6_line_7 | NAYY 4x150 SE | 5 | 7 | 0.016266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3274-7_0_6_line_8 | NAYY 4x150 SE | 6 | 8 | 0.01604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3274-7_0_6_line_9 | NAYY 4x150 SE | 7 | 9 | 0.016625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3274-7_0_6_line_10 | NAYY 4x150 SE | 7 | 10 | 0.018438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_3274-7_0_6_line_11 | NAYY 4x150 SE | 8 | 28 | 0.0093887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3274-7_0_6_line_12 | NAYY 4x150 SE | 9 | 33 | 0.022271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3274-7_0_6_line_13 | NAYY 4x150 SE | 10 | 23 | 0.0080858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_3274-7_0_6_line_14 | NAYY 4x150 SE | 11 | 12 | 0.036626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3274-7_0_6_line_15 | NAYY 4x150 SE | 11 | 13 | 0.11713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3274-7_0_6_line_16 | NAYY 4x150 SE | 12 | 14 | 0.0054714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3274-7_0_6_line_17 | NAYY 4x150 SE | 12 | 15 | 0.2783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3274-7_0_6_line_18 | NAYY 4x150 SE | 13 | 16 | 0.062151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3274-7_0_6_line_19 | NAYY 4x150 SE | 15 | 38 | 0.01943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3274-7_0_6_line_20 | NAYY 4x150 SE | 16 | 66 | 0.080003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3274-7_0_6_line_21 | NAYY 4x150 SE | 16 | 18 | 0.1448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3274-7_0_6_line_22 | NAYY 4x150 SE | 17 | 18 | 0.0065923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3274-7_0_6_line_23 | NAYY 4x150 SE | 17 | 19 | 0.024634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3274-7_0_6_line_24 | NAYY 4x150 SE | 19 | 20 | 0.00094406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3274-7_0_6_line_25 | NAYY 4x150 SE | 20 | 21 | 0.023014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3274-7_0_6_line_26 | NAYY 4x150 SE | 21 | 28 | 0.0072816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3274-7_0_6_line_27 | NAYY 4x150 SE | 22 | 23 | 0.01101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_3274-7_0_6_line_28 | NAYY 4x150 SE | 22 | 24 | 0.013352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_3274-7_0_6_line_29 | NAYY 4x150 SE | 24 | 25 | 0.022599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_3274-7_0_6_line_30 | NAYY 4x150 SE | 25 | 26 | 0.017063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3274-7_0_6_line_31 | NAYY 4x150 SE | 25 | 27 | 0.024289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_3274-7_0_6_line_32 | NAYY 4x150 SE | 26 | 32 | 0.022521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3274-7_0_6_line_33 | NAYY 4x150 SE | 27 | 29 | 0.016272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_3274-7_0_6_line_34 | NAYY 4x150 SE | 29 | 30 | 0.031587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_3274-7_0_6_line_35 | NAYY 4x150 SE | 30 | 31 | 0.054007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_3274-7_0_6_line_36 | NAYY 4x150 SE | 31 | 42 | 0.022014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_3274-7_0_6_line_37 | NAYY 4x150 SE | 32 | 46 | 0.0046868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3274-7_0_6_line_38 | NAYY 4x150 SE | 33 | 37 | 0.0037605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3274-7_0_6_line_39 | NAYY 4x150 SE | 33 | 35 | 0.012744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3274-7_0_6_line_40 | NAYY 4x150 SE | 34 | 35 | 0.010034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3274-7_0_6_line_41 | NAYY 4x150 SE | 34 | 36 | 0.0093254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3274-7_0_6_line_42 | NAYY 4x150 SE | 37 | 47 | 0.023523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3274-7_0_6_line_43 | NAYY 4x150 SE | 39 | 40 | 0.0047606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3274-7_0_6_line_44 | NAYY 4x150 SE | 39 | 41 | 0.019826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3274-7_0_6_line_45 | NAYY 4x150 SE | 40 | 44 | 0.020246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3274-7_0_6_line_46 | NAYY 4x150 SE | 41 | 84 | 0.014593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3274-7_0_6_line_47 | NAYY 4x150 SE | 42 | 43 | 0.055509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_3274-7_0_6_line_48 | NAYY 4x150 SE | 43 | 50 | 0.204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_3274-7_0_6_line_49 | NAYY 4x150 SE | 44 | 45 | 0.0056394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3274-7_0_6_line_50 | NAYY 4x150 SE | 45 | 46 | 0.020876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3274-7_0_6_line_51 | NAYY 4x150 SE | 47 | 48 | 0.024987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3274-7_0_6_line_52 | NAYY 4x150 SE | 48 | 73 | 0.015809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3274-7_0_6_line_53 | NAYY 4x150 SE | 49 | 55 | 0.024544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3274-7_0_6_line_54 | NAYY 4x150 SE | 49 | 57 | 0.052885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_3274-7_0_6_line_55 | NAYY 4x150 SE | 51 | 52 | 0.020971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3274-7_0_6_line_56 | NAYY 4x150 SE | 51 | 53 | 0.11267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3274-7_0_6_line_57 | NAYY 4x150 SE | 52 | 54 | 0.024841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3274-7_0_6_line_58 | NAYY 4x150 SE | 53 | 55 | 0.035423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3274-7_0_6_line_59 | NAYY 4x150 SE | 54 | 56 | 0.022473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3274-7_0_6_line_60 | NAYY 4x150 SE | 55 | 101 | 0.0011409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3274-7_0_6_line_61 | NAYY 4x150 SE | 56 | 91 | 0.14165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3274-7_0_6_line_62 | NAYY 4x150 SE | 57 | 59 | 0.043662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_3274-7_0_6_line_63 | NAYY 4x150 SE | 58 | 59 | 0.07225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3274-7_0_6_line_64 | NAYY 4x150 SE | 59 | 62 | 0.0261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3274-7_0_6_line_65 | NAYY 4x150 SE | 59 | 63 | 0.008876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_3274-7_0_6_line_66 | NAYY 4x150 SE | 60 | 61 | 0.052331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3274-7_0_6_line_67 | NAYY 4x150 SE | 61 | 64 | 0.028811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3274-7_0_6_line_68 | NAYY 4x150 SE | 62 | 161 | 0.0086993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3274-7_0_6_line_69 | NAYY 4x150 SE | 63 | 103 | 0.035421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
70 | LV_3274-7_0_6_line_70 | NAYY 4x150 SE | 64 | 65 | 0.024412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3274-7_0_6_line_71 | NAYY 4x150 SE | 65 | 147 | 0.009076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3274-7_0_6_line_72 | NAYY 4x150 SE | 66 | 67 | 0.049012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3274-7_0_6_line_73 | NAYY 4x150 SE | 67 | 68 | 0.022577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3274-7_0_6_line_74 | NAYY 4x150 SE | 69 | 70 | 0.0050171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3274-7_0_6_line_75 | NAYY 4x150 SE | 70 | 71 | 0.026557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3274-7_0_6_line_76 | NAYY 4x150 SE | 71 | 72 | 0.0088392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3274-7_0_6_line_77 | NAYY 4x150 SE | 72 | 73 | 0.016942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3274-7_0_6_line_78 | NAYY 4x150 SE | 73 | 74 | 0.0092581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3274-7_0_6_line_79 | NAYY 4x150 SE | 74 | 76 | 0.021516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3274-7_0_6_line_80 | NAYY 4x150 SE | 75 | 76 | 0.028819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3274-7_0_6_line_81 | NAYY 4x150 SE | 75 | 77 | 0.0058388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3274-7_0_6_line_82 | NAYY 4x150 SE | 76 | 78 | 0.029703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3274-7_0_6_line_83 | NAYY 4x150 SE | 78 | 79 | 0.014235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3274-7_0_6_line_84 | NAYY 4x150 SE | 80 | 81 | 0.019119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3274-7_0_6_line_85 | NAYY 4x150 SE | 81 | 82 | 0.021468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_3274-7_0_6_line_86 | NAYY 4x150 SE | 82 | 83 | 0.026879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3274-7_0_6_line_87 | NAYY 4x150 SE | 83 | 84 | 0.011523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3274-7_0_6_line_88 | NAYY 4x150 SE | 85 | 86 | 0.083829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3274-7_0_6_line_89 | NAYY 4x150 SE | 85 | 87 | 0.079093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3274-7_0_6_line_90 | NAYY 4x150 SE | 86 | 136 | 0.077712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3274-7_0_6_line_91 | NAYY 4x150 SE | 87 | 140 | 0.027422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_3274-7_0_6_line_92 | NAYY 4x150 SE | 88 | 89 | 0.015383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3274-7_0_6_line_93 | NAYY 4x150 SE | 89 | 90 | 0.038487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3274-7_0_6_line_94 | NAYY 4x150 SE | 89 | 91 | 0.036346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_3274-7_0_6_line_95 | NAYY 4x150 SE | 90 | 92 | 0.017396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_3274-7_0_6_line_96 | NAYY 4x150 SE | 91 | 93 | 0.10686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3274-7_0_6_line_97 | NAYY 4x150 SE | 92 | 94 | 0.019657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3274-7_0_6_line_98 | NAYY 4x150 SE | 94 | 132 | 0.017579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3274-7_0_6_line_99 | NAYY 4x150 SE | 95 | 96 | 0.064411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3274-7_0_6_line_100 | NAYY 4x150 SE | 95 | 97 | 0.057299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3274-7_0_6_line_101 | NAYY 4x150 SE | 97 | 98 | 0.027298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3274-7_0_6_line_102 | NAYY 4x150 SE | 98 | 99 | 0.020848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3274-7_0_6_line_103 | NAYY 4x150 SE | 98 | 100 | 0.002345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3274-7_0_6_line_104 | NAYY 4x150 SE | 99 | 112 | 0.059765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3274-7_0_6_line_105 | NAYY 4x150 SE | 100 | 125 | 0.026349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3274-7_0_6_line_106 | NAYY 4x150 SE | 102 | 103 | 0.017988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3274-7_0_6_line_107 | NAYY 4x150 SE | 102 | 104 | 0.011456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3274-7_0_6_line_108 | NAYY 4x150 SE | 104 | 105 | 0.02226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3274-7_0_6_line_109 | NAYY 4x150 SE | 104 | 106 | 0.03624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3274-7_0_6_line_110 | NAYY 4x150 SE | 105 | 107 | 0.037345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_3274-7_0_6_line_111 | NAYY 4x150 SE | 106 | 108 | 0.056997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3274-7_0_6_line_112 | NAYY 4x150 SE | 106 | 109 | 0.0099892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_3274-7_0_6_line_113 | NAYY 4x150 SE | 107 | 110 | 0.016341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3274-7_0_6_line_114 | NAYY 4x150 SE | 108 | 111 | 0.020915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3274-7_0_6_line_115 | NAYY 4x150 SE | 108 | 112 | 0.01427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3274-7_0_6_line_116 | NAYY 4x150 SE | 109 | 113 | 0.022467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3274-7_0_6_line_117 | NAYY 4x150 SE | 110 | 118 | 0.028703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3274-7_0_6_line_118 | NAYY 4x150 SE | 110 | 117 | 0.030858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3274-7_0_6_line_119 | NAYY 4x150 SE | 111 | 160 | 0.012854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3274-7_0_6_line_120 | NAYY 4x150 SE | 113 | 162 | 0.0090689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3274-7_0_6_line_121 | NAYY 4x150 SE | 114 | 115 | 0.01691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3274-7_0_6_line_122 | NAYY 4x150 SE | 114 | 116 | 0.0020942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3274-7_0_6_line_123 | NAYY 4x150 SE | 115 | 117 | 0.010629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3274-7_0_6_line_124 | NAYY 4x150 SE | 118 | 149 | 0.020684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3274-7_0_6_line_125 | NAYY 4x150 SE | 118 | 146 | 0.019102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3274-7_0_6_line_126 | NAYY 4x150 SE | 119 | 120 | 0.001528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3274-7_0_6_line_127 | NAYY 4x150 SE | 120 | 121 | 0.041943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3274-7_0_6_line_128 | NAYY 4x150 SE | 121 | 123 | 0.15858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3274-7_0_6_line_129 | NAYY 4x150 SE | 122 | 123 | 0.033753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3274-7_0_6_line_130 | NAYY 4x150 SE | 122 | 124 | 0.026163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3274-7_0_6_line_131 | NAYY 4x150 SE | 124 | 125 | 0.093229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3274-7_0_6_line_132 | NAYY 4x150 SE | 126 | 127 | 0.054554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3274-7_0_6_line_133 | NAYY 4x150 SE | 127 | 128 | 0.066586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3274-7_0_6_line_134 | NAYY 4x150 SE | 127 | 129 | 0.0184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3274-7_0_6_line_135 | NAYY 4x150 SE | 128 | 130 | 0.050254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3274-7_0_6_line_136 | NAYY 4x150 SE | 130 | 131 | 0.10661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3274-7_0_6_line_137 | NAYY 4x150 SE | 130 | 132 | 0.0018112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3274-7_0_6_line_138 | NAYY 4x150 SE | 131 | 133 | 0.082972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3274-7_0_6_line_139 | NAYY 4x150 SE | 133 | 134 | 0.034376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3274-7_0_6_line_140 | NAYY 4x150 SE | 135 | 136 | 0.12469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3274-7_0_6_line_141 | NAYY 4x150 SE | 137 | 138 | 0.0029723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3274-7_0_6_line_142 | NAYY 4x150 SE | 138 | 139 | 0.03591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3274-7_0_6_line_143 | NAYY 4x150 SE | 139 | 140 | 0.014743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3274-7_0_6_line_144 | NAYY 4x150 SE | 140 | 141 | 0.0047409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3274-7_0_6_line_145 | NAYY 4x150 SE | 141 | 142 | 0.01676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3274-7_0_6_line_146 | NAYY 4x150 SE | 142 | 150 | 0.0087318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3274-7_0_6_line_147 | NAYY 4x150 SE | 143 | 144 | 0.028879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3274-7_0_6_line_148 | NAYY 4x150 SE | 143 | 145 | 0.0020887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3274-7_0_6_line_149 | NAYY 4x150 SE | 144 | 146 | 0.017584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_3274-7_0_6_line_150 | NAYY 4x150 SE | 145 | 147 | 0.00813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_3274-7_0_6_line_151 | NAYY 4x150 SE | 146 | 148 | 0.037955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_3274-7_0_6_line_152 | NAYY 4x150 SE | 148 | 150 | 0.028155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_3274-7_0_6_line_153 | NAYY 4x150 SE | 149 | 151 | 0.024829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_3274-7_0_6_line_154 | NAYY 4x150 SE | 151 | 156 | 0.03262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_3274-7_0_6_line_155 | NAYY 4x150 SE | 152 | 153 | 0.008472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_3274-7_0_6_line_156 | NAYY 4x150 SE | 152 | 154 | 0.019738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_3274-7_0_6_line_157 | NAYY 4x150 SE | 153 | 155 | 0.0018372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_3274-7_0_6_line_158 | NAYY 4x150 SE | 155 | 156 | 0.013224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_3274-7_0_6_line_159 | NAYY 4x150 SE | 156 | 157 | 0.013346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_3274-7_0_6_line_160 | NAYY 4x150 SE | 157 | 159 | 0.01476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_3274-7_0_6_line_161 | NAYY 4x150 SE | 158 | 159 | 0.013463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_3274-7_0_6_line_162 | NAYY 4x150 SE | 160 | 163 | 0.0097781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_3274-7_0_6_line_163 | NAYY 4x150 SE | 161 | 164 | 0.0093357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_3274-7_0_6_line_164 | NAYY 4x150 SE | 161 | 165 | 0.0084196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_3274-7_0_6_line_165 | NAYY 4x150 SE | 164 | 167 | 0.053479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_3274-7_0_6_line_166 | NAYY 4x150 SE | 165 | 166 | 0.018623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_3274-7_0_6_line_167 | NAYY 4x150 SE | 167 | 168 | 0.0047933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_3274-7_0_6_line_168 | NAYY 4x150 SE | 168 | 169 | 0.013808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_3274-7_0_6_line_169 | NAYY 4x150 SE | 169 | 170 | 0.0036729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3274-7_0_6_trafo_8 | 0.25 MVA 20/0.4 kV | 171 | 50 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2756219.0436 | 1234251.581 | 2756198.5712 | 1234211.4822
1 | 2756192.4376 | 1234199.4685 | 2756198.5712 | 1234211.4822
2 | 2756192.4376 | 1234199.4685 | 2756193.3132 | 1234163.0126
3 | 2756192.4376 | 1234199.4685 | 2756192.1114 | 1234215.8977 | 2756191.5893 | 1234227.9732 | 2756186.0329 | 1234224.1124
4 | 2756014.1723 | 1234611.9009 | 2756013.2899 | 1234615.6658
5 | 2756014.1723 | 1234611.9009 | 2756014.564 | 1234610.2297 | 2756015.7304 | 1234596.97 | 2756017.4164 | 1234587.8521
6 | 2756008.3068 | 1234631.591 | 2756008.7713 | 1234630.3634 | 2756011.9965 | 1234621.1838 | 2756013.2899 | 1234615.6658
7 | 2756020.3741 | 1234571.857 | 2756017.4164 | 1234587.8521
8 | 2756008.3068 | 1234631.591 | 2756004.2053 | 1234642.4327 | 2756001.5071 | 1234645.9695
9 | 2756020.3741 | 1234571.857 | 2756013.6542 | 1234556.6506
10 | 2756020.3741 | 1234571.857 | 2756037.805 | 1234565.8458
11 | 2755995.8124 | 1234653.4339 | 2756001.5071 | 1234645.9695
12 | 2756004.5623 | 1234536.3194 | 2756013.4971 | 1234556.2951 | 2756013.6542 | 1234556.6506
13 | 2756045.4491 | 1234563.2097 | 2756037.805 | 1234565.8458
14 | 2755854.2209 | 1234828.1157 | 2755845.2146 | 1234836.2113 | 2755830.3006 | 1234847.2528 | 2755825.7808 | 1234851.1373
15 | 2755854.2209 | 1234828.1157 | 2755824.5523 | 1234714.8101
16 | 2755825.7808 | 1234851.1373 | 2755821.6313 | 1234854.7036
17 | 2755825.7808 | 1234851.1373 | 2756009.1004 | 1235060.5241
18 | 2755824.5523 | 1234714.8101 | 2755818.7977 | 1234705.239 | 2755809.48 | 1234679.9263 | 2755801.7003 | 1234657.1897
19 | 2756009.1004 | 1235060.5241 | 2756020.6315 | 1235067.2554 | 2756025.1127 | 1235071.3614
20 | 2755801.7003 | 1234657.1897 | 2755786.7538 | 1234663.3926 | 2755767.4332 | 1234680.7248 | 2755754.4348 | 1234695.8206 | 2755742.5231 | 1234708.754 | 2755742.2683 | 1234709.01
21 | 2755943.5872 | 1234686.0959 | 2755801.7003 | 1234657.1897
22 | 2755949.7506 | 1234683.7641 | 2755944.4452 | 1234685.8387 | 2755943.5872 | 1234686.0959
23 | 2755949.7506 | 1234683.7641 | 2755961.5555 | 1234679.148 | 2755971.7737 | 1234672.9349
24 | 2755972.5804 | 1234672.4444 | 2755971.7737 | 1234672.9349
25 | 2755990.8296 | 1234658.7437 | 2755985.1377 | 1234664.809 | 2755972.5804 | 1234672.4444
26 | 2755990.8296 | 1234658.7437 | 2755995.8124 | 1234653.4339 | 2755995.8124 | 1234653.4339
27 | 2756055.7165 | 1234559.3196 | 2756054.3855 | 1234560.1278 | 2756045.4491 | 1234563.2097
28 | 2756067.129 | 1234552.3887 | 2756055.7165 | 1234559.3196
29 | 2756084.7466 | 1234538.3156 | 2756071.2719 | 1234549.8727 | 2756067.129 | 1234552.3887
30 | 2756084.7466 | 1234538.3156 | 2756076.1132 | 1234523.5975
31 | 2756084.7466 | 1234538.3156 | 2756105.129 | 1234525.1046
32 | 2756076.1132 | 1234523.5975 | 2756064.7186 | 1234504.172
33 | 2756118.7837 | 1234516.2541 | 2756105.129 | 1234525.1046
34 | 2756145.4967 | 1234499.4079 | 2756137.2339 | 1234504.2955 | 2756118.7837 | 1234516.2541
35 | 2756145.4967 | 1234499.4079 | 2756115.115 | 1234454.7567
36 | 2756102.731 | 1234436.5563 | 2756115.115 | 1234454.7567
37 | 2756062.3473 | 1234500.1294 | 2756064.7186 | 1234504.172
38 | 2756004.5623 | 1234536.3194 | 2756003.0265 | 1234532.8868
39 | 2756004.5623 | 1234536.3194 | 2755993.4543 | 1234542.5661
40 | 2755993.4543 | 1234542.5661 | 2755984.7086 | 1234547.4844
41 | 2755976.5804 | 1234552.0554 | 2755984.7086 | 1234547.4844
42 | 2755993.4196 | 1234511.4149 | 2756003.0265 | 1234532.8868
43 | 2756036.279 | 1234455.6883 | 2756038.6876 | 1234459.7945
44 | 2756026.2477 | 1234438.587 | 2756036.279 | 1234455.6883
45 | 2756048.9314 | 1234477.2581 | 2756038.6876 | 1234459.7945
46 | 2756018.864 | 1234425.9993 | 2756026.2477 | 1234438.587
47 | 2756069.9731 | 1234391.8755 | 2756079.1312 | 1234401.8723 | 2756102.731 | 1234436.5563
48 | 2756186.0329 | 1234224.1124 | 2756069.9731 | 1234391.8755
49 | 2756048.9314 | 1234477.2581 | 2756051.7847 | 1234482.1224
50 | 2756051.7847 | 1234482.1224 | 2756062.3473 | 1234500.1294
51 | 2755993.4196 | 1234511.4149 | 2755986.8283 | 1234496.683 | 2755983.0349 | 1234488.6893
52 | 2755976.2572 | 1234474.4067 | 2755983.0349 | 1234488.6893
53 | 2756193.3132 | 1234163.0126 | 2756217.9246 | 1234163.4932
54 | 2756193.3132 | 1234163.0126 | 2756194.5837 | 1234110.1429
55 | 2756337.9683 | 1234221.548 | 2756356.6855 | 1234212.091
56 | 2756227.8992 | 1234197.4876 | 2756337.9683 | 1234221.548
57 | 2756356.6855 | 1234212.091 | 2756369.39 | 1234205.6719 | 2756378.0328 | 1234199.5233
58 | 2756217.9246 | 1234163.4932 | 2756227.8992 | 1234197.4876
59 | 2756396.3443 | 1234186.4963 | 2756378.0328 | 1234199.5233
60 | 2756217.9246 | 1234163.4932 | 2756219.0652 | 1234163.5163
61 | 2756506.4154 | 1234097.3427 | 2756396.3443 | 1234186.4963
62 | 2756195.6326 | 1234066.4933 | 2756194.5837 | 1234110.1429
63 | 2756195.6326 | 1234066.4933 | 2756125.6133 | 1234084.3099
64 | 2756195.6326 | 1234066.4933 | 2756220.6051 | 1234074.082
65 | 2756195.6326 | 1234066.4933 | 2756195.6724 | 1234057.6173
66 | 2756087.6294 | 1233995.5171 | 2756066.1858 | 1233947.7815
67 | 2756084.1491 | 1233925.2561 | 2756066.1858 | 1233947.7815
68 | 2756228.9285 | 1234076.6113 | 2756220.6051 | 1234074.082
69 | 2756191.6212 | 1234022.5536 | 2756193.222 | 1234030.2845 | 2756195.7228 | 1234046.3655 | 2756195.6724 | 1234057.6173
70 | 2756104.9183 | 1233912.4268 | 2756084.1491 | 1233925.2561
71 | 2756104.9183 | 1233912.4268 | 2756112.64 | 1233907.6571
72 | 2755708.8887 | 1234744.8623 | 2755710.465 | 1234743.38 | 2755728.7083 | 1234722.6384 | 2755742.2683 | 1234709.01
73 | 2755708.8887 | 1234744.8623 | 2755693.4612 | 1234761.3467
74 | 2755926.8258 | 1234503.4791 | 2755931.2173 | 1234501.0529
75 | 2755954.1745 | 1234487.7122 | 2755941.042 | 1234495.6249 | 2755931.2173 | 1234501.0529
76 | 2755954.1745 | 1234487.7122 | 2755961.7456 | 1234483.1504
77 | 2755976.2572 | 1234474.4067 | 2755961.7456 | 1234483.1504
78 | 2755976.2572 | 1234474.4067 | 2755972.0328 | 1234466.1687
79 | 2755962.2151 | 1234447.0234 | 2755972.0328 | 1234466.1687
80 | 2755962.2151 | 1234447.0234 | 2755933.9808 | 1234452.8016
81 | 2755928.2606 | 1234453.9723 | 2755933.9808 | 1234452.8016
82 | 2755962.2151 | 1234447.0234 | 2755947.5072 | 1234421.2177
83 | 2755947.5072 | 1234421.2177 | 2755940.4587 | 1234408.8508
84 | 2755964.3885 | 1234394.5443 | 2755971.6072 | 1234394.2421 | 2755983.4409 | 1234393.0503
85 | 2756004.8009 | 1234390.8991 | 2755983.4409 | 1234393.0503
86 | 2756004.8009 | 1234390.8991 | 2756005.4355 | 1234397.8779 | 2756008.2109 | 1234407.838 | 2756013.0337 | 1234416.0599
87 | 2756018.864 | 1234425.9993 | 2756013.0337 | 1234416.0599
88 | 2756034.091 | 1233806.5932 | 2756035.1864 | 1233786.2361 | 2756033.1707 | 1233766.6647 | 2756030.7206 | 1233751.2302 | 2756029.658 | 1233740.3587 | 2756031.6524 | 1233728.1662 | 2756033.7146 | 1233723.7717
89 | 2756112.5243 | 1233816.7847 | 2756034.091 | 1233806.5932
90 | 2756090.5258 | 1233670.7467 | 2756033.7146 | 1233723.7717
91 | 2756138.8713 | 1233808.9249 | 2756112.5243 | 1233816.7847
92 | 2756487.88 | 1234066.0472 | 2756478.5628 | 1234059.4623 | 2756476.0036 | 1234056.4229
93 | 2756487.88 | 1234066.0472 | 2756514.5006 | 1234038.2522
94 | 2756506.4154 | 1234097.3427 | 2756487.88 | 1234066.0472
95 | 2756527.0293 | 1234026.3694 | 2756524.8768 | 1234027.4182 | 2756514.5006 | 1234038.2522
96 | 2756538.1675 | 1234185.8184 | 2756540.7739 | 1234168.2592 | 2756546.9785 | 1234161.6053 | 2756549.8822 | 1234154.3193 | 2756549.3618 | 1234150.2128 | 2756506.4154 | 1234097.3427
97 | 2756544.7008 | 1234017.7595 | 2756527.0293 | 1234026.3694
98 | 2756560.5043 | 1234010.0597 | 2756544.7008 | 1234017.7595
99 | 2756394.6645 | 1233959.8263 | 2756345.3645 | 1234001.4353
100 | 2756394.6645 | 1233959.8263 | 2756358.6477 | 1233915.2623
101 | 2756341.489 | 1233894.0317 | 2756358.6477 | 1233915.2623
102 | 2756341.489 | 1233894.0317 | 2756325.8389 | 1233907.8055
103 | 2756341.489 | 1233894.0317 | 2756343.246 | 1233892.4787
104 | 2756280.9749 | 1233947.2906 | 2756325.8389 | 1233907.8055
105 | 2756362.988 | 1233875.0285 | 2756343.246 | 1233892.4787
106 | 2756187.6464 | 1234005.0153 | 2756189.4316 | 1234011.9787 | 2756191.6212 | 1234022.5536
107 | 2756184.8015 | 1233993.9177 | 2756187.6464 | 1234005.0153
108 | 2756184.8015 | 1233993.9177 | 2756179.4879 | 1233972.3008
109 | 2756219.1385 | 1233982.0423 | 2756184.8015 | 1233993.9177
110 | 2756171.3384 | 1233935.8646 | 2756172.1373 | 1233940.6234 | 2756178.096 | 1233966.6379 | 2756179.4879 | 1233972.3008
111 | 2756219.1385 | 1233982.0423 | 2756247.493 | 1233969.8316 | 2756270.2433 | 1233956.7284
112 | 2756219.1385 | 1233982.0423 | 2756219.2747 | 1233992.0305
113 | 2756186.1489 | 1233928.8694 | 2756171.3384 | 1233935.8646
114 | 2756270.2433 | 1233956.7284 | 2756267.4387 | 1233977.455
115 | 2756270.2433 | 1233956.7284 | 2756280.9749 | 1233947.2906
116 | 2756219.5812 | 1234014.495 | 2756219.2747 | 1233992.0305
117 | 2756178.0794 | 1233901.3202 | 2756186.1489 | 1233928.8694
118 | 2756186.1489 | 1233928.8694 | 2756212.2003 | 1233912.3304
119 | 2756265.7151 | 1233990.1926 | 2756267.4387 | 1233977.455
120 | 2756219.7049 | 1234023.5631 | 2756219.5812 | 1234014.495
121 | 2756221.1735 | 1233906.6337 | 2756228.5552 | 1233901.9473 | 2756235.5334 | 1233906.1892
122 | 2756237.3229 | 1233907.277 | 2756235.5334 | 1233906.1892
123 | 2756221.1735 | 1233906.6337 | 2756212.2003 | 1233912.3304
124 | 2756178.0794 | 1233901.3202 | 2756187.9357 | 1233883.1357
125 | 2756178.0794 | 1233901.3202 | 2756166.5497 | 1233907.4119 | 2756165.2816 | 1233901.484
126 | 2756557.9189 | 1233670.5456 | 2756558.9114 | 1233671.7074
127 | 2756587.4692 | 1233702.3811 | 2756571.5122 | 1233686.4568 | 2756558.9114 | 1233671.7074
128 | 2756478.4165 | 1233817.5141 | 2756587.4692 | 1233702.3811
129 | 2756452.4432 | 1233795.9584 | 2756478.4165 | 1233817.5141
130 | 2756452.4432 | 1233795.9584 | 2756432.8405 | 1233813.2854
131 | 2756432.8405 | 1233813.2854 | 2756362.988 | 1233875.0285
132 | 2756657.2465 | 1233947.6745 | 2756639.756 | 1233941.3854 | 2756627.157 | 1233935.7369 | 2756612.1649 | 1233928.0568 | 2756608.0193 | 1233924.7308
133 | 2756657.2465 | 1233947.6745 | 2756653.9526 | 1233955.6731 | 2756649.9839 | 1233963.6983 | 2756642.0066 | 1233970.3499 | 2756607.3092 | 1233987.2553
134 | 2756657.2465 | 1233947.6745 | 2756675.4173 | 1233950.5674
135 | 2756562.1325 | 1234009.2664 | 2756607.3092 | 1233987.2553
136 | 2756562.1325 | 1234009.2664 | 2756616.0854 | 1234101.2104
137 | 2756560.5043 | 1234010.0597 | 2756562.1325 | 1234009.2664
138 | 2756691.9295 | 1234134.8552 | 2756616.0854 | 1234101.2104
139 | 2756691.9295 | 1234134.8552 | 2756684.0055 | 1234152.6966 | 2756671.3537 | 1234160.5483
140 | 2756090.5258 | 1233670.7467 | 2756214.0402 | 1233653.6311
141 | 2756123.0429 | 1233757.6915 | 2756123.9574 | 1233760.5196
142 | 2756123.9574 | 1233760.5196 | 2756129.0356 | 1233776.2245 | 2756134.6249 | 1233794.8068
143 | 2756138.8713 | 1233808.9249 | 2756134.6249 | 1233794.8068
144 | 2756138.8713 | 1233808.9249 | 2756140.2376 | 1233813.4647
145 | 2756145.1542 | 1233829.4872 | 2756143.6013 | 1233824.6418 | 2756140.2376 | 1233813.4647
146 | 2756145.1542 | 1233829.4872 | 2756145.1974 | 1233829.6217 | 2756147.8237 | 1233837.8009
147 | 2756121.6345 | 1233903.1702 | 2756126.2557 | 1233902.6932 | 2756140.9985 | 1233909.5092 | 2756148.5856 | 1233907.0018
148 | 2756119.5568 | 1233903.3846 | 2756121.6345 | 1233903.1702
149 | 2756165.2816 | 1233901.484 | 2756148.5856 | 1233907.0018
150 | 2756119.5568 | 1233903.3846 | 2756119.5568 | 1233903.3846 | 2756112.64 | 1233907.6571
151 | 2756165.2816 | 1233901.484 | 2756159.0669 | 1233872.8159 | 2756156.4313 | 1233864.6078
152 | 2756156.4313 | 1233864.6078 | 2756147.8237 | 1233837.8009
153 | 2756199.7672 | 1233861.3071 | 2756187.9357 | 1233883.1357
154 | 2756222.5652 | 1233838.263 | 2756201.8827 | 1233857.4041 | 2756199.7672 | 1233861.3071
155 | 2756215.4003 | 1233818.9453 | 2756219.8336 | 1233826.1647
156 | 2756215.4003 | 1233818.9453 | 2756215.4003 | 1233818.9453 | 2756232.3495 | 1233808.8299
157 | 2756219.8336 | 1233826.1647 | 2756220.7949 | 1233827.7303
158 | 2756222.5652 | 1233838.263 | 2756225.5837 | 1233835.5286 | 2756220.7949 | 1233827.7303
159 | 2756222.5652 | 1233838.263 | 2756229.9545 | 1233843.2953 | 2756234.1939 | 1233844.494
160 | 2756248.4714 | 1233848.1959 | 2756244.9168 | 1233847.5259 | 2756234.1939 | 1233844.494
161 | 2756248.4714 | 1233848.1959 | 2756253.9012 | 1233849.2193 | 2756258.0409 | 1233849.0724 | 2756260.997 | 1233846.6923 | 2756260.997 | 1233846.6923
162 | 2756264.4039 | 1233999.8824 | 2756265.7151 | 1233990.1926
163 | 2756228.9285 | 1234076.6113 | 2756235.2914 | 1234083.4428
164 | 2756228.9285 | 1234076.6113 | 2756234.0913 | 1234069.9603
165 | 2756235.2914 | 1234083.4428 | 2756241.6501 | 1234090.2698 | 2756259.6865 | 1234085.3059 | 2756268.2089 | 1234082.0936 | 2756276.5438 | 1234076.5075 | 2756274.209 | 1234070.6553
166 | 2756245.5105 | 1234055.2492 | 2756234.0913 | 1234069.9603
167 | 2756274.209 | 1234070.6553 | 2756272.4328 | 1234066.2032
168 | 2756272.4328 | 1234066.2032 | 2756267.316 | 1234053.3784
169 | 2756265.955 | 1234049.967 | 2756267.316 | 1234053.3784

## bus_geodata
| x | y | coords
0 | 2756219.0436 | 1234251.581
1 | 2756198.5712 | 1234211.4822
2 | 2756192.4376 | 1234199.4685
3 | 2756014.1723 | 1234611.9009
4 | 2756013.2899 | 1234615.6658
5 | 2756017.4164 | 1234587.8521
6 | 2756008.3068 | 1234631.591
7 | 2756020.3741 | 1234571.857
8 | 2756001.5071 | 1234645.9695
9 | 2756013.6542 | 1234556.6506
10 | 2756037.805 | 1234565.8458
11 | 2755854.2209 | 1234828.1157
12 | 2755825.7808 | 1234851.1373
13 | 2755824.5523 | 1234714.8101
14 | 2755821.6313 | 1234854.7036
15 | 2756009.1004 | 1235060.5241
16 | 2755801.7003 | 1234657.1897
17 | 2755949.7506 | 1234683.7641
18 | 2755943.5872 | 1234686.0959
19 | 2755971.7737 | 1234672.9349
20 | 2755972.5804 | 1234672.4444
21 | 2755990.8296 | 1234658.7437
22 | 2756055.7165 | 1234559.3196
23 | 2756045.4491 | 1234563.2097
24 | 2756067.129 | 1234552.3887
25 | 2756084.7466 | 1234538.3156
26 | 2756076.1132 | 1234523.5975
27 | 2756105.129 | 1234525.1046
28 | 2755995.8124 | 1234653.4339
29 | 2756118.7837 | 1234516.2541
30 | 2756145.4967 | 1234499.4079
31 | 2756115.115 | 1234454.7567
32 | 2756064.7186 | 1234504.172
33 | 2756004.5623 | 1234536.3194
34 | 2755984.7086 | 1234547.4844
35 | 2755993.4543 | 1234542.5661
36 | 2755976.5804 | 1234552.0554
37 | 2756003.0265 | 1234532.8868
38 | 2756025.1127 | 1235071.3614
39 | 2756036.279 | 1234455.6883
40 | 2756038.6876 | 1234459.7945
41 | 2756026.2477 | 1234438.587
42 | 2756102.731 | 1234436.5563
43 | 2756069.9731 | 1234391.8755
44 | 2756048.9314 | 1234477.2581
45 | 2756051.7847 | 1234482.1224
46 | 2756062.3473 | 1234500.1294
47 | 2755993.4196 | 1234511.4149
48 | 2755983.0349 | 1234488.6893
49 | 2756193.3132 | 1234163.0126
50 | 2756186.0329 | 1234224.1124
51 | 2756337.9683 | 1234221.548
52 | 2756356.6855 | 1234212.091
53 | 2756227.8992 | 1234197.4876
54 | 2756378.0328 | 1234199.5233
55 | 2756217.9246 | 1234163.4932
56 | 2756396.3443 | 1234186.4963
57 | 2756194.5837 | 1234110.1429
58 | 2756125.6133 | 1234084.3099
59 | 2756195.6326 | 1234066.4933
60 | 2756087.6294 | 1233995.5171
61 | 2756066.1858 | 1233947.7815
62 | 2756220.6051 | 1234074.082
63 | 2756195.6723 | 1234057.6173
64 | 2756084.1491 | 1233925.2561
65 | 2756104.9183 | 1233912.4268
66 | 2755742.2683 | 1234709.01
67 | 2755708.8887 | 1234744.8623
68 | 2755693.4612 | 1234761.3467
69 | 2755926.8258 | 1234503.4791
70 | 2755931.2173 | 1234501.0529
71 | 2755954.1745 | 1234487.7122
72 | 2755961.7456 | 1234483.1504
73 | 2755976.2572 | 1234474.4067
74 | 2755972.0328 | 1234466.1687
75 | 2755933.9808 | 1234452.8016
76 | 2755962.2151 | 1234447.0234
77 | 2755928.2606 | 1234453.9723
78 | 2755947.5072 | 1234421.2177
79 | 2755940.4587 | 1234408.8508
80 | 2755964.3885 | 1234394.5443
81 | 2755983.4409 | 1234393.0503
82 | 2756004.8009 | 1234390.8991
83 | 2756013.0337 | 1234416.0599
84 | 2756018.864 | 1234425.9993
85 | 2756034.091 | 1233806.5932
86 | 2756033.7146 | 1233723.7717
87 | 2756112.5243 | 1233816.7847
88 | 2756476.0036 | 1234056.4229
89 | 2756487.88 | 1234066.0472
90 | 2756514.5006 | 1234038.2522
91 | 2756506.4154 | 1234097.3427
92 | 2756527.0293 | 1234026.3694
93 | 2756538.1675 | 1234185.8184
94 | 2756544.7008 | 1234017.7595
95 | 2756394.6645 | 1233959.8263
96 | 2756345.3645 | 1234001.4353
97 | 2756358.6477 | 1233915.2623
98 | 2756341.489 | 1233894.0317
99 | 2756325.8389 | 1233907.8055
100 | 2756343.246 | 1233892.4787
101 | 2756219.0652 | 1234163.5163
102 | 2756187.6464 | 1234005.0153
103 | 2756191.6212 | 1234022.5536
104 | 2756184.8015 | 1233993.9177
105 | 2756179.4879 | 1233972.3008
106 | 2756219.1385 | 1233982.0423
107 | 2756171.3384 | 1233935.8646
108 | 2756270.2433 | 1233956.7284
109 | 2756219.2747 | 1233992.0305
110 | 2756186.1489 | 1233928.8694
111 | 2756267.4387 | 1233977.455
112 | 2756280.9749 | 1233947.2906
113 | 2756219.5812 | 1234014.495
114 | 2756235.5334 | 1233906.1892
115 | 2756221.1735 | 1233906.6337
116 | 2756237.3229 | 1233907.277
117 | 2756212.2003 | 1233912.3304
118 | 2756178.0794 | 1233901.3202
119 | 2756557.9189 | 1233670.5456
120 | 2756558.9114 | 1233671.7074
121 | 2756587.4692 | 1233702.3811
122 | 2756452.4432 | 1233795.9584
123 | 2756478.4165 | 1233817.5141
124 | 2756432.8405 | 1233813.2854
125 | 2756362.988 | 1233875.0285
126 | 2756608.0193 | 1233924.7308
127 | 2756657.2465 | 1233947.6745
128 | 2756607.3092 | 1233987.2553
129 | 2756675.4173 | 1233950.5674
130 | 2756562.1325 | 1234009.2664
131 | 2756616.0854 | 1234101.2104
132 | 2756560.5043 | 1234010.0597
133 | 2756691.9295 | 1234134.8552
134 | 2756671.3537 | 1234160.5483
135 | 2756214.0402 | 1233653.6311
136 | 2756090.5258 | 1233670.7467
137 | 2756123.0429 | 1233757.6915
138 | 2756123.9574 | 1233760.5196
139 | 2756134.6249 | 1233794.8068
140 | 2756138.8713 | 1233808.9249
141 | 2756140.2376 | 1233813.4647
142 | 2756145.1542 | 1233829.4872
143 | 2756121.6345 | 1233903.1702
144 | 2756148.5856 | 1233907.0018
145 | 2756119.5568 | 1233903.3846
146 | 2756165.2816 | 1233901.484
147 | 2756112.64 | 1233907.6571
148 | 2756156.4313 | 1233864.6078
149 | 2756187.9357 | 1233883.1357
150 | 2756147.8237 | 1233837.8009
151 | 2756199.7672 | 1233861.3071
152 | 2756215.4003 | 1233818.9453
153 | 2756219.8336 | 1233826.1647
154 | 2756232.3495 | 1233808.8299
155 | 2756220.7949 | 1233827.7303
156 | 2756222.5652 | 1233838.263
157 | 2756234.1939 | 1233844.494
158 | 2756260.997 | 1233846.6923
159 | 2756248.4714 | 1233848.1959
160 | 2756265.7151 | 1233990.1926
161 | 2756228.9285 | 1234076.6113
162 | 2756219.7049 | 1234023.5631
163 | 2756264.4039 | 1233999.8824
164 | 2756235.2914 | 1234083.4428
165 | 2756234.0913 | 1234069.9603
166 | 2756245.5105 | 1234055.2492
167 | 2756274.209 | 1234070.6553
168 | 2756272.4328 | 1234066.2032
169 | 2756267.316 | 1234053.3784
170 | 2756265.955 | 1234049.967
171 | 2756191.5893 | 1234227.9732

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1