## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3291-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3291-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3291-15_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3291-15_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3291-15_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3291-15_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3291-15_0_4_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_3291-15_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_3291-15_0_4_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_3291-15_0_4_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_3291-15_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_3291-15_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_3291-15_0_4_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_3291-15_0_4_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_3291-15_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_3291-15_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_3291-15_0_4_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_3291-15_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_3291-15_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_3291-15_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_3291-15_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_3291-15_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_3291-15_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_3291-15_0_4_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_3291-15_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_3291-15_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_3291-15_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_3291-15_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_3291-15_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_3291-15_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_3291-15_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_3291-15_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_3291-15_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_MV_149_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3291-15_0_4_load_0 | 0 | 0.041681 | 0.010446 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3291-15_0_4_load_1 | 1 | 0.0062781 | 0.0015734 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3291-15_0_4_load_3 | 3 | 0.0070929 | 0.0017776 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3291-15_0_4_load_4 | 4 | 0.006606 | 0.0016556 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3291-15_0_4_load_5 | 5 | 0.0092972 | 0.0023301 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3291-15_0_4_load_28 | 8 | 0.0081469 | 0.0020418 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3291-15_0_4_load_33 | 9 | 0.0032563 | 0.00081611 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3291-15_0_4_load_16 | 12 | 0.049038 | 0.01229 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3291-15_0_4_load_36 | 13 | 0.0061607 | 0.001544 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3291-15_0_4_load_9 | 14 | 0.026734 | 0.0067003 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3291-15_0_4_load_15 | 19 | 0.0058235 | 0.0014595 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3291-15_0_4_load_10 | 20 | 0.01239 | 0.0031051 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3291-15_0_4_load_34 | 23 | 0.0074129 | 0.0018579 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3291-15_0_4_load_22 | 25 | 0.015977 | 0.0040043 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3291-15_0_4_load_32 | 26 | 0.0023541 | 0.00058999 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3291-15_0_4_load_27 | 28 | 0.01699 | 0.0042582 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3291-15_0_4_load_29 | 30 | 0.0049502 | 0.0012406 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3291-15_0_4_load_30 | 31 | 0.003 | 0.00075187 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3291-15_0_4_load_31 | 32 | 0.0046974 | 0.0011773 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3291-15_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0059051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3291-15_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0091549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3291-15_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0016302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3291-15_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_3291-15_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.019155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_3291-15_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.025253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3291-15_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.016354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_3291-15_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0064843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3291-15_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.015547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3291-15_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.035292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3291-15_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.013539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3291-15_0_4_line_11 | NAYY 4x150 SE | 9 | 26 | 0.016154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3291-15_0_4_line_12 | NAYY 4x150 SE | 10 | 12 | 0.028596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3291-15_0_4_line_13 | NAYY 4x150 SE | 11 | 13 | 0.020092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3291-15_0_4_line_14 | NAYY 4x150 SE | 13 | 21 | 0.023247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3291-15_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.028181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3291-15_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.011427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3291-15_0_4_line_17 | NAYY 4x150 SE | 15 | 22 | 0.033452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3291-15_0_4_line_18 | NAYY 4x150 SE | 16 | 23 | 0.0039616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3291-15_0_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.010054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3291-15_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.023354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3291-15_0_4_line_21 | NAYY 4x150 SE | 17 | 20 | 0.013817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3291-15_0_4_line_22 | NAYY 4x150 SE | 18 | 23 | 0.0063402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3291-15_0_4_line_23 | NAYY 4x150 SE | 19 | 24 | 0.017851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3291-15_0_4_line_24 | NAYY 4x150 SE | 21 | 24 | 0.008756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3291-15_0_4_line_25 | NAYY 4x150 SE | 22 | 25 | 0.0112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3291-15_0_4_line_26 | NAYY 4x150 SE | 25 | 27 | 0.021224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3291-15_0_4_line_27 | NAYY 4x150 SE | 26 | 32 | 0.0022505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3291-15_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.018856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3291-15_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.021727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3291-15_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.014871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3291-15_0_4_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0074722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3291-15_0_4_trafo_5 | 0.25 MVA 20/0.4 kV | 33 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2756834.3948 | 1207777.5952 | 2756838.3933 | 1207773.2498
1 | 2756827.2002 | 1207782.8643 | 2756830.8199 | 1207781.4804 | 2756834.3948 | 1207777.5952
2 | 2756838.3933 | 1207773.2498 | 2756838.3933 | 1207773.2498 | 2756838.9238 | 1207771.7084
3 | 2756827.2002 | 1207782.8643 | 2756816.1478 | 1207787.8301
4 | 2756827.2002 | 1207782.8643 | 2756836.3005 | 1207795.548 | 2756838.6508 | 1207798.201
5 | 2756855.4581 | 1207753.8587 | 2756844.6899 | 1207761.2045 | 2756842.5585 | 1207763.2726 | 2756841.0374 | 1207765.568 | 2756838.9238 | 1207771.7084
6 | 2756801.2318 | 1207794.5369 | 2756810.8786 | 1207790.1976 | 2756816.1478 | 1207787.8301
7 | 2756842.9506 | 1207803.0547 | 2756838.6508 | 1207798.201
8 | 2756855.4581 | 1207753.8587 | 2756868.6848 | 1207762.03
9 | 2756801.2318 | 1207794.5369 | 2756794.8415 | 1207770.7924 | 2756793.3857 | 1207760.1891
10 | 2756800.1847 | 1207808.0326 | 2756801.2318 | 1207794.5369
11 | 2756868.6848 | 1207762.03 | 2756882.4279 | 1207770.5204
12 | 2756793.3857 | 1207760.1891 | 2756767.5632 | 1207772.4744
13 | 2756800.1847 | 1207808.0326 | 2756790.8028 | 1207812.7125 | 2756782.2046 | 1207817.0006
14 | 2756761.4009 | 1207827.3756 | 2756782.2046 | 1207817.0006
15 | 2756837.5166 | 1207873.416 | 2756826.298 | 1207847.5538
16 | 2756815.188 | 1207849.9641 | 2756819.844 | 1207848.2293 | 2756826.298 | 1207847.5538
17 | 2756837.5166 | 1207873.416 | 2756846.4571 | 1207866.4225 | 2756864.7189 | 1207853.8689
18 | 2756815.188 | 1207849.9641 | 2756811.9303 | 1207847.7098
19 | 2756800.9395 | 1207857.452 | 2756807.5686 | 1207855.9025 | 2756809.823 | 1207854.0712 | 2756809.9537 | 1207853.7299
20 | 2756800.9395 | 1207857.452 | 2756794.2927 | 1207854.7528 | 2756781.7679 | 1207844.5093
21 | 2756800.9395 | 1207857.452 | 2756801.194 | 1207862.819 | 2756803.2518 | 1207871.0086
22 | 2756809.9537 | 1207853.7299 | 2756810.6391 | 1207851.9686 | 2756811.9303 | 1207847.7098
23 | 2756767.9501 | 1207833.2084 | 2756781.7679 | 1207844.5093
24 | 2756767.9501 | 1207833.2084 | 2756761.4009 | 1207827.3756
25 | 2756864.7189 | 1207853.8689 | 2756873.8075 | 1207847.3241
26 | 2756891.0308 | 1207834.9213 | 2756873.8075 | 1207847.3241
27 | 2756884.3425 | 1207771.7033 | 2756882.4279 | 1207770.5204
28 | 2756891.0308 | 1207834.9213 | 2756884.5141 | 1207824.3851 | 2756878.9679 | 1207821.0576
29 | 2756891.0308 | 1207834.9213 | 2756908.5565 | 1207822.0149
30 | 2756908.5565 | 1207822.0149 | 2756900.4091 | 1207809.5743
31 | 2756884.3425 | 1207771.7033 | 2756890.6994 | 1207775.6306

## bus_geodata
| x | y | coords
0 | 2756834.3948 | 1207777.5952
1 | 2756838.3933 | 1207773.2498
2 | 2756827.2002 | 1207782.8643
3 | 2756838.9238 | 1207771.7084
4 | 2756816.1478 | 1207787.8301
5 | 2756838.6508 | 1207798.201
6 | 2756855.4581 | 1207753.8587
7 | 2756801.2318 | 1207794.5369
8 | 2756842.9506 | 1207803.0547
9 | 2756868.6848 | 1207762.03
10 | 2756793.3857 | 1207760.1891
11 | 2756800.1847 | 1207808.0326
12 | 2756767.5632 | 1207772.4744
13 | 2756782.2046 | 1207817.0006
14 | 2756826.298 | 1207847.5538
15 | 2756837.5166 | 1207873.416
16 | 2756815.188 | 1207849.9641
17 | 2756800.9395 | 1207857.452
18 | 2756809.9537 | 1207853.7299
19 | 2756781.7679 | 1207844.5093
20 | 2756803.2518 | 1207871.0086
21 | 2756761.4009 | 1207827.3756
22 | 2756864.7189 | 1207853.8689
23 | 2756811.9303 | 1207847.7098
24 | 2756767.9501 | 1207833.2084
25 | 2756873.8075 | 1207847.3241
26 | 2756882.4279 | 1207770.5204
27 | 2756891.0308 | 1207834.9213
28 | 2756878.9679 | 1207821.0576
29 | 2756908.5565 | 1207822.0149
30 | 2756900.4091 | 1207809.5743
31 | 2756890.6994 | 1207775.6306
32 | 2756884.3425 | 1207771.7033
33 | 2756827.2002 | 1207782.8643

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99707 | -0.020357 | 0.041681 | 0.010446
1 | 0.99685 | -0.02194 | 0.0062781 | 0.0015734
2 | 0.99797 | -0.01408 | 0 | 0
3 | 0.9968 | -0.022274 | 0.0070929 | 0.0017776
4 | 0.99708 | -0.020242 | 0.006606 | 0.0016556
5 | 1 | 0 | -0.23219 | -0.058358
6 | 0.99632 | -0.025652 | 0 | 0
7 | 0.99535 | -0.032208 | 0 | 0
8 | 0.99992 | -0.00052729 | 0.0081469 | 0.0020418
9 | 0.99602 | -0.027734 | 0.0032563 | 0.00081611
10 | 0.99286 | -0.049688 | 0 | 0
11 | 0.99345 | -0.04539 | 0 | 0
12 | 0.99084 | -0.063914 | 0.049038 | 0.01229
13 | 0.99062 | -0.065046 | 0.0061607 | 0.001544
14 | 0.97799 | -0.15417 | 0.026734 | 0.0067003
15 | 0.97643 | -0.16534 | 0 | 0
16 | 0.97907 | -0.14647 | 0 | 0
17 | 0.98117 | -0.13153 | 0 | 0
18 | 0.98012 | -0.13905 | 0 | 0
19 | 0.98405 | -0.11114 | 0.0058235 | 0.0014595
20 | 0.98093 | -0.1333 | 0.01239 | 0.0031051
21 | 0.98756 | -0.086463 | 0 | 0
22 | 0.97457 | -0.17865 | 0 | 0
23 | 0.97945 | -0.1438 | 0.0074129 | 0.0018579
24 | 0.9864 | -0.094563 | 0 | 0
25 | 0.97395 | -0.18311 | 0.015977 | 0.0040043
26 | 0.99579 | -0.029368 | 0.0023541 | 0.00058999
27 | 0.97327 | -0.18802 | 0 | 0
28 | 0.9728 | -0.1914 | 0.01699 | 0.0042582
29 | 0.97311 | -0.18915 | 0 | 0
30 | 0.973 | -0.18993 | 0.0049502 | 0.0012406
31 | 0.99573 | -0.029768 | 0.003 | 0.00075187
32 | 0.99577 | -0.029542 | 0.0046974 | 0.0011773
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.026698 | 0.0066928 | -0.026692 | -0.0066907 | 5.85e-06 | 2.173e-06 | 0.039845 | 0.039845 | 0.039845 | 0.99707 | -0.020357 | 0.99685 | -0.02194 | 14.7573
1 | -0.06838 | -0.017139 | 0.068439 | 0.017162 | 5.9492e-05 | 2.2762e-05 | 0.10205 | 0.10205 | 0.10205 | 0.99707 | -0.020357 | 0.99797 | -0.01408 | 37.796
2 | 0.020414 | 0.0051172 | -0.020413 | -0.0051169 | 9.4462e-07 | 3.4206e-07 | 0.030473 | 0.030473 | 0.030473 | 0.99685 | -0.02194 | 0.9968 | -0.022274 | 11.2864
3 | 0.15436 | 0.038986 | -0.15423 | -0.038935 | 0.00013363 | 5.0921e-05 | 0.23026 | 0.23026 | 0.23026 | 0.99797 | -0.01408 | 0.99708 | -0.020242 | 28.4276
4 | -0.2228 | -0.056148 | 0.22324 | 0.056316 | 0.00043998 | 0.00016847 | 0.33231 | 0.33231 | 0.33231 | 0.99797 | -0.01408 | 1 | 0 | 41.0262
5 | 0.01332 | 0.0033392 | -0.013314 | -0.0033372 | 6.2308e-06 | 2.0674e-06 | 0.019885 | 0.019885 | 0.019885 | 0.9968 | -0.022274 | 0.99632 | -0.025652 | 7.3649
6 | 0.14762 | 0.037279 | -0.14737 | -0.037184 | 0.00024788 | 9.4911e-05 | 0.2204 | 0.2204 | 0.2204 | 0.99708 | -0.020242 | 0.99535 | -0.032208 | 40.8157
7 | 0.0081474 | 0.0020419 | -0.0081469 | -0.0020418 | 5.9472e-07 | 1.4367e-07 | 0.012124 | 0.012124 | 0.012124 | 1 | 0 | 0.99992 | -0.00052729 | 4.4902
8 | 0.013314 | 0.0033372 | -0.01331 | -0.0033359 | 3.8362e-06 | 1.273e-06 | 0.019885 | 0.019885 | 0.019885 | 0.99632 | -0.025652 | 0.99602 | -0.027734 | 7.3649
9 | 0.049255 | 0.012372 | -0.049135 | -0.012327 | 0.00011944 | 4.5479e-05 | 0.073644 | 0.073644 | 0.073644 | 0.99535 | -0.032208 | 0.99286 | -0.049688 | 27.2756
10 | 0.098118 | 0.024812 | -0.097936 | -0.024742 | 0.00018197 | 6.9812e-05 | 0.14676 | 0.14676 | 0.14676 | 0.99535 | -0.032208 | 0.99345 | -0.04539 | 54.3559
11 | 0.010054 | 0.0025198 | -0.010052 | -0.0025191 | 2.2742e-06 | 6.645e-07 | 0.01502 | 0.01502 | 0.01502 | 0.99602 | -0.027734 | 0.99579 | -0.029368 | 5.5631
12 | 0.049135 | 0.012327 | -0.049038 | -0.01229 | 9.6775e-05 | 3.6852e-05 | 0.073644 | 0.073644 | 0.073644 | 0.99286 | -0.049688 | 0.99084 | -0.063914 | 27.2756
13 | 0.097936 | 0.024742 | -0.097666 | -0.024638 | 0.00027005 | 0.0001036 | 0.14676 | 0.14676 | 0.14676 | 0.99345 | -0.04539 | 0.99062 | -0.065046 | 54.356
14 | 0.091505 | 0.023094 | -0.091231 | -0.022989 | 0.00027429 | 0.0001052 | 0.13751 | 0.13751 | 0.13751 | 0.99062 | -0.065046 | 0.98756 | -0.086463 | 50.9286
15 | 0.038095 | 0.0095693 | -0.038036 | -0.0095469 | 5.9093e-05 | 2.2375e-05 | 0.057969 | 0.057969 | 0.057969 | 0.97799 | -0.15417 | 0.97643 | -0.16534 | 21.4701
16 | -0.064829 | -0.01627 | 0.064899 | 0.016296 | 6.9386e-05 | 2.6543e-05 | 0.098645 | 0.098645 | 0.098645 | 0.97799 | -0.15417 | 0.97907 | -0.14647 | 36.5353
17 | 0.038036 | 0.0095469 | -0.037966 | -0.0095204 | 7.0146e-05 | 2.6562e-05 | 0.057969 | 0.057969 | 0.057969 | 0.97643 | -0.16534 | 0.97457 | -0.17865 | 21.4701
18 | -0.064899 | -0.016296 | 0.064923 | 0.016305 | 2.4055e-05 | 9.2022e-06 | 0.098645 | 0.098645 | 0.098645 | 0.97907 | -0.14647 | 0.97945 | -0.1438 | 36.5353
19 | 0.072459 | 0.01821 | -0.072383 | -0.018181 | 7.5784e-05 | 2.9021e-05 | 0.10991 | 0.10991 | 0.10991 | 0.98117 | -0.13153 | 0.98012 | -0.13905 | 40.7064
20 | -0.084852 | -0.021317 | 0.085093 | 0.021409 | 0.00024139 | 9.2546e-05 | 0.1287 | 0.1287 | 0.1287 | 0.98117 | -0.13153 | 0.98405 | -0.11114 | 47.6673
21 | 0.012393 | 0.0031061 | -0.01239 | -0.0031051 | 3.0455e-06 | 9.969e-07 | 0.018794 | 0.018794 | 0.018794 | 0.98117 | -0.13153 | 0.98093 | -0.1333 | 6.9609
22 | 0.072383 | 0.018181 | -0.072336 | -0.018163 | 4.779e-05 | 1.8301e-05 | 0.10991 | 0.10991 | 0.10991 | 0.98012 | -0.13905 | 0.97945 | -0.1438 | 40.7064
23 | -0.090917 | -0.022869 | 0.091127 | 0.022949 | 0.00021061 | 8.0778e-05 | 0.13751 | 0.13751 | 0.13751 | 0.98405 | -0.11114 | 0.9864 | -0.094563 | 50.9287
24 | 0.091231 | 0.022989 | -0.091127 | -0.022949 | 0.00010331 | 3.9623e-05 | 0.13751 | 0.13751 | 0.13751 | 0.98756 | -0.086463 | 0.9864 | -0.094563 | 50.9286
25 | 0.037966 | 0.0095204 | -0.037942 | -0.0095115 | 2.3485e-05 | 8.8934e-06 | 0.057969 | 0.057969 | 0.057969 | 0.97457 | -0.17865 | 0.97395 | -0.18311 | 21.4702
26 | 0.021965 | 0.0055072 | -0.02195 | -0.0055017 | 1.4915e-05 | 5.4727e-06 | 0.033559 | 0.033559 | 0.033559 | 0.97395 | -0.18311 | 0.97327 | -0.18802 | 12.4292
27 | 0.0076977 | 0.0019291 | -0.0076975 | -0.0019291 | 1.8581e-07 | 4.2188e-08 | 0.011503 | 0.011503 | 0.011503 | 0.99579 | -0.029368 | 0.99577 | -0.029542 | 4.2603
28 | 0.016998 | 0.004261 | -0.01699 | -0.0042582 | 7.9472e-06 | 2.8224e-06 | 0.025989 | 0.025989 | 0.025989 | 0.97327 | -0.18802 | 0.9728 | -0.1914 | 9.6255
29 | 0.0049515 | 0.0012407 | -0.0049508 | -0.0012407 | 7.7698e-07 | 2.8877e-08 | 0.0075703 | 0.0075704 | 0.0075704 | 0.97327 | -0.18802 | 0.97311 | -0.18915 | 2.8038
30 | 0.0049508 | 0.0012407 | -0.0049502 | -0.0012406 | 5.3182e-07 | 1.9819e-08 | 0.0075704 | 0.0075704 | 0.0075704 | 0.97311 | -0.18915 | 0.973 | -0.18993 | 2.8039
31 | -0.003 | -0.00075187 | 0.0030001 | 0.00075181 | 9.3714e-08 | -6.1155e-08 | 0.0044832 | 0.0044832 | 0.0044832 | 0.99573 | -0.029768 | 0.99577 | -0.029542 | 1.6604

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24148 | 0.060688

## res_load
| p_mw | q_mvar
0 | 0.041681 | 0.010446
1 | 0.0062781 | 0.0015734
2 | 0.0070929 | 0.0017776
3 | 0.006606 | 0.0016556
4 | 0.0092972 | 0.0023301
5 | 0.0081469 | 0.0020418
6 | 0.0032563 | 0.00081611
7 | 0.049038 | 0.01229
8 | 0.0061607 | 0.001544
9 | 0.026734 | 0.0067003
10 | 0.0058235 | 0.0014595
11 | 0.01239 | 0.0031051
12 | 0.0074129 | 0.0018579
13 | 0.015977 | 0.0040043
14 | 0.0023541 | 0.00058999
15 | 0.01699 | 0.0042582
16 | 0.0049502 | 0.0012406
17 | 0.003 | 0.00075187
18 | 0.0046974 | 0.0011773

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1