## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3291-17_1_3_node_29 | 0.4 | n |  | TRUE
1 | bus_LV_3291-17_1_3_node_30 | 0.4 | n |  | TRUE
2 | bus_LV_3291-17_1_3_node_31 | 0.4 | n |  | TRUE
3 | bus_LV_3291-17_1_3_node_32 | 0.4 | n |  | TRUE
4 | bus_LV_3291-17_1_3_node_42 | 0.4 | n |  | TRUE
5 | bus_LV_3291-17_1_3_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_3291-17_1_3_node_69 | 0.4 | n |  | TRUE
7 | bus_LV_3291-17_1_3_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_3291-17_1_3_node_77 | 0.4 | n |  | TRUE
9 | bus_LV_3291-17_1_3_node_76 | 0.4 | n |  | TRUE
10 | bus_LV_3291-17_1_3_node_73 | 0.4 | n |  | TRUE
11 | bus_LV_3291-17_1_3_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_3291-17_1_3_node_67 | 0.4 | n |  | TRUE
13 | bus_LV_3291-17_1_3_node_85 | 0.4 | n |  | TRUE
14 | bus_LV_3291-17_1_3_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_3291-17_1_3_node_79 | 0.4 | n |  | TRUE
16 | bus_LV_3291-17_1_3_node_70 | 0.4 | n |  | TRUE
17 | bus_LV_3291-17_1_3_node_71 | 0.4 | n |  | TRUE
18 | bus_LV_3291-17_1_3_node_72 | 0.4 | n |  | TRUE
19 | bus_LV_3291-17_1_3_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_3291-17_1_3_node_75 | 0.4 | n |  | TRUE
21 | bus_LV_3291-17_1_3_node_83 | 0.4 | n |  | TRUE
22 | bus_LV_3291-17_1_3_node_78 | 0.4 | n |  | TRUE
23 | bus_LV_3291-17_1_3_node_86 | 0.4 | n |  | TRUE
24 | bus_MV_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3291-17_1_3_load_29 | 0 | 0.0011564 | 0.00028982 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3291-17_1_3_load_30 | 1 | 0.00038141 | 9.559e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3291-17_1_3_load_32 | 3 | 0.00039191 | 9.8222e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3291-17_1_3_load_69 | 6 | 0.00096303 | 0.00024136 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3291-17_1_3_load_76 | 9 | 0.003857 | 0.00096666 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3291-17_1_3_load_73 | 10 | 0.0023114 | 0.00057928 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3291-17_1_3_load_66 | 11 | 0.0088992 | 0.0022304 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3291-17_1_3_load_67 | 12 | 0.0058666 | 0.0014703 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3291-17_1_3_load_68 | 14 | 0.0046365 | 0.001162 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3291-17_1_3_load_70 | 16 | 0.0048727 | 0.0012212 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3291-17_1_3_load_72 | 18 | 0.0010387 | 0.00026032 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3291-17_1_3_load_75 | 20 | 0.0013297 | 0.00033327 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3291-17_1_3_load_83 | 21 | 0.0075192 | 0.0018845 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3291-17_1_3_load_78 | 22 | 0.0052569 | 0.0013175 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3291-17_1_3_load_86 | 23 | 0.0065796 | 0.001649 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3291-17_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.034771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3291-17_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.028078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3291-17_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.036617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3291-17_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.34142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3291-17_1_3_line_4 | NAYY 4x150 SE | 4 | 10 | 0.13074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3291-17_1_3_line_5 | NAYY 4x150 SE | 4 | 5 | 0.15727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3291-17_1_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.066357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3291-17_1_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.089137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3291-17_1_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.094275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3291-17_1_3_line_9 | NAYY 4x150 SE | 8 | 21 | 0.073771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3291-17_1_3_line_10 | NAYY 4x150 SE | 8 | 15 | 0.053741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3291-17_1_3_line_11 | NAYY 4x150 SE | 9 | 20 | 0.041161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3291-17_1_3_line_12 | NAYY 4x150 SE | 10 | 19 | 0.029052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3291-17_1_3_line_13 | NAYY 4x150 SE | 11 | 12 | 0.0016624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3291-17_1_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.13662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3291-17_1_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.027018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3291-17_1_3_line_16 | NAYY 4x150 SE | 13 | 23 | 0.03148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3291-17_1_3_line_17 | NAYY 4x150 SE | 14 | 15 | 0.0016274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3291-17_1_3_line_18 | NAYY 4x150 SE | 15 | 22 | 0.064942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3291-17_1_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.016634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3291-17_1_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.017111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3291-17_1_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.019819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3291-17_1_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.015116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3291-17_1_3_trafo_77 | 0.25 MVA 20/0.4 kV | 24 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2758035.7235 | 1207426.0796 | 2758042.4862 | 1207426.6744 | 2758049.4162 | 1207425.2899 | 2758054.2136 | 1207423.1261 | 2758057.7565 | 1207419.4944 | 2758059.4629 | 1207414.5352 | 2758060.1812 | 1207409.2495 | 2758060.1812 | 1207409.2495
1 | 2758010.9494 | 1207417.1866 | 2758016.0684 | 1207415.8098 | 2758021.1929 | 1207417.3801 | 2758028.3443 | 1207424.0087 | 2758035.609 | 1207426.0695 | 2758035.7235 | 1207426.0796
2 | 2758041.7944 | 1207377.8895 | 2758048.2652 | 1207387.47 | 2758058.4737 | 1207403.0543 | 2758060.1812 | 1207409.2495
3 | 2757722.876 | 1207317.4128 | 2757728.2258 | 1207323.9933 | 2757732.544 | 1207329.8794 | 2757755.7828 | 1207362.8785 | 2757845.8762 | 1207383.5451 | 2757891.7002 | 1207400.005 | 2757920.4584 | 1207412.4323 | 2757929.8738 | 1207417.7528 | 2757958.7547 | 1207433.5867 | 2757974.772 | 1207441.2841 | 2757989.0229 | 1207444.7198 | 2758006.0461 | 1207431.3918 | 2758010.9494 | 1207417.1866
4 | 2757722.876 | 1207317.4128 | 2757710.6436 | 1207300.3521 | 2757681.0301 | 1207267.2848 | 2757654.2909 | 1207229.378 | 2757643.0509 | 1207214.0941
5 | 2757596.4107 | 1207355.5403 | 2757610.7933 | 1207351.1272 | 2757623.8129 | 1207347.0451 | 2757630.1196 | 1207346.5 | 2757630.952 | 1207352.4273 | 2757631.219 | 1207362.7658 | 2757646.8212 | 1207359.7084 | 2757663.2722 | 1207355.0498 | 2757674.8268 | 1207350.2618 | 2757686.0501 | 1207343.3298 | 2757692.5956 | 1207338.9321 | 2757703.4948 | 1207334.7607 | 2757713.4862 | 1207331.2549 | 2757718.3994 | 1207327.0142 | 2757720.4569 | 1207322.2866 | 2757722.876 | 1207317.4128
6 | 2757596.4107 | 1207355.5403 | 2757585.3257 | 1207356.9601 | 2757576.445 | 1207357.882 | 2757565.2041 | 1207361.4552 | 2757555.8884 | 1207361.2759 | 2757547.422 | 1207357.7493 | 2757544.2908 | 1207356.4655 | 2757540.4148 | 1207356.8747 | 2757537.5238 | 1207360.0345 | 2757535.163 | 1207363.7527
7 | 2757471.3689 | 1207186.2117 | 2757469.1138 | 1207191.2233 | 2757462.7146 | 1207194.4018 | 2757456.0787 | 1207200.4989 | 2757453.2923 | 1207207.1869 | 2757452.4726 | 1207217.1965 | 2757456.4442 | 1207225.2751 | 2757461.8048 | 1207229.7316 | 2757467.826 | 1207233.3714 | 2757479.2761 | 1207238.0221 | 2757482.9117 | 1207240.9539 | 2757485.4371 | 1207244.7239 | 2757488.1341 | 1207249.7773
8 | 2757488.1341 | 1207249.7773 | 2757513.1505 | 1207245.7782 | 2757547.0707 | 1207233.073 | 2757570.5235 | 1207219.7134 | 2757575.5991 | 1207217.0582
9 | 2757471.3689 | 1207186.2117 | 2757491.2775 | 1207175.3938 | 2757494.8051 | 1207166.2788 | 2757512.8163 | 1207157.0123 | 2757515.0058 | 1207151.3206 | 2757527.4076 | 1207142.6956
10 | 2757471.3689 | 1207186.2117 | 2757467.5908 | 1207180.3179 | 2757458.5422 | 1207178.6555 | 2757439.0986 | 1207184.548 | 2757430.4037 | 1207191.9697 | 2757425.6913 | 1207195.5264
11 | 2757575.5991 | 1207217.0582 | 2757612.0709 | 1207197.9783
12 | 2757625.4646 | 1207190.9714 | 2757638.8523 | 1207208.3849 | 2757643.0509 | 1207214.0941
13 | 2757405.471 | 1207216.4105 | 2757406.951 | 1207215.6533
14 | 2757405.471 | 1207216.4105 | 2757296.1817 | 1207134.4249
15 | 2757424.8842 | 1207196.9396 | 2757417.1875 | 1207210.4155 | 2757406.951 | 1207215.6533
16 | 2757296.1817 | 1207134.4249 | 2757292.9577 | 1207137.5205 | 2757283.4558 | 1207139.7721 | 2757266.4135 | 1207142.8926
17 | 2757425.6913 | 1207195.5264 | 2757424.8842 | 1207196.9396
18 | 2757425.6913 | 1207195.5264 | 2757431.4647 | 1207177.7183 | 2757441.795 | 1207168.2934 | 2757471.0534 | 1207154.7582
19 | 2757656.5411 | 1207171.0186 | 2757666.3094 | 1207164.7376 | 2757670.6442 | 1207162.2051
20 | 2757656.5411 | 1207171.0186 | 2757642.1423 | 1207180.2634
21 | 2757625.4646 | 1207190.9714 | 2757642.1423 | 1207180.2634
22 | 2757625.4646 | 1207190.9714 | 2757612.0709 | 1207197.9783

## bus_geodata
| x | y | coords
0 | 2758035.7235 | 1207426.0796
1 | 2758060.1812 | 1207409.2495
2 | 2758010.9494 | 1207417.1866
3 | 2758041.7944 | 1207377.8895
4 | 2757722.876 | 1207317.4128
5 | 2757596.4107 | 1207355.5403
6 | 2757535.163 | 1207363.7527
7 | 2757488.1341 | 1207249.7773
8 | 2757471.3689 | 1207186.2117
9 | 2757575.5991 | 1207217.0582
10 | 2757643.0509 | 1207214.0941
11 | 2757405.471 | 1207216.4105
12 | 2757406.951 | 1207215.6533
13 | 2757296.1817 | 1207134.4249
14 | 2757424.8842 | 1207196.9396
15 | 2757425.6913 | 1207195.5264
16 | 2757670.6442 | 1207162.2051
17 | 2757656.5411 | 1207171.0186
18 | 2757642.1423 | 1207180.2634
19 | 2757625.4646 | 1207190.9714
20 | 2757612.0709 | 1207197.9783
21 | 2757527.4076 | 1207142.6957
22 | 2757471.0534 | 1207154.7582
23 | 2757266.4135 | 1207142.8926
24 | 2757471.3689 | 1207186.2117

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99296 | -0.049819 | 0.0011564 | 0.00028982
1 | 0.99292 | -0.050093 | 0.00038141 | 9.559e-05
2 | 0.99304 | -0.049268 | 0 | 0
3 | 0.9929 | -0.050239 | 0.00039191 | 9.8222e-05
4 | 0.99398 | -0.042516 | 0 | 0
5 | 0.99377 | -0.044069 | 0 | 0
6 | 0.99367 | -0.044717 | 0.00096303 | 0.00024136
7 | 0.99792 | -0.014626 | 0 | 0
8 | 1 | 0 | -0.056057 | -0.013856
9 | 0.99572 | -0.030152 | 0.003857 | 0.00096666
10 | 0.99452 | -0.038605 | 0.0023114 | 0.00057928
11 | 0.99668 | -0.023287 | 0.0088992 | 0.0022304
12 | 0.99671 | -0.023029 | 0.0058666 | 0.0014703
13 | 0.99539 | -0.032344 | 0 | 0
14 | 0.99754 | -0.017235 | 0.0046365 | 0.001162
15 | 0.9976 | -0.016811 | 0 | 0
16 | 0.99434 | -0.039899 | 0.0048727 | 0.0012212
17 | 0.99445 | -0.039081 | 0 | 0
18 | 0.99457 | -0.038239 | 0.0010387 | 0.00026032
19 | 0.99474 | -0.037057 | 0 | 0
20 | 0.99498 | -0.035349 | 0.0013297 | 0.00033327
21 | 0.99921 | -0.0055431 | 0.0075192 | 0.0018845
22 | 0.99711 | -0.020238 | 0.0052569 | 0.0013175
23 | 0.99509 | -0.034431 | 0.0065796 | 0.001649
24 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00077336 | 0.0001929 | -0.00077333 | -0.00019334 | 2.9129e-08 | -4.3855e-07 | 0.0011586 | 0.0011588 | 0.0011588 | 0.99296 | -0.049819 | 0.99292 | -0.050093 | 0.42917
1 | -0.0019297 | -0.00048272 | 0.0019299 | 0.00048241 | 1.4648e-07 | -3.0688e-07 | 0.0028915 | 0.0028914 | 0.0028915 | 0.99296 | -0.049819 | 0.99304 | -0.049268 | 1.0709
2 | 0.00039192 | 9.7751e-05 | -0.00039191 | -9.8222e-05 | 7.88e-09 | -4.7057e-07 | 0.00058717 | 0.00058734 | 0.00058734 | 0.99292 | -0.050093 | 0.9929 | -0.050239 | 0.21753
3 | -0.0019299 | -0.00048241 | 0.0019317 | 0.00047868 | 1.7802e-06 | -3.7366e-06 | 0.0028914 | 0.0028898 | 0.0028914 | 0.99304 | -0.049268 | 0.99398 | -0.042516 | 1.0709
4 | -0.002895 | -0.00071725 | 0.0028965 | 0.00071614 | 1.5301e-06 | -1.1071e-06 | 0.004331 | 0.0043304 | 0.004331 | 0.99398 | -0.042516 | 0.99452 | -0.038605 | 1.6041
5 | 0.00096332 | 0.00023857 | -0.00096312 | -0.00024053 | 2.0392e-07 | -1.9597e-06 | 0.0014411 | 0.0014418 | 0.0014418 | 0.99398 | -0.042516 | 0.99377 | -0.044069 | 0.53401
6 | 0.00096312 | 0.00024053 | -0.00096303 | -0.00024136 | 8.6098e-08 | -8.2654e-07 | 0.0014418 | 0.0014421 | 0.0014421 | 0.99377 | -0.044069 | 0.99367 | -0.044717 | 0.53412
7 | -0.016356 | -0.004093 | 0.016389 | 0.0041045 | 3.3077e-05 | 1.1555e-05 | 0.024386 | 0.024386 | 0.024386 | 0.99792 | -0.014626 | 1 | 0 | 9.0319
8 | 0.016356 | 0.004093 | -0.016321 | -0.0040807 | 3.4985e-05 | 1.2227e-05 | 0.024386 | 0.024387 | 0.024387 | 0.99792 | -0.014626 | 0.99572 | -0.030152 | 9.0321
9 | 0.007525 | 0.0018858 | -0.0075192 | -0.0018845 | 5.7718e-06 | 1.2528e-06 | 0.011197 | 0.011198 | 0.011198 | 1 | 0 | 0.99921 | -0.0055431 | 4.1473
10 | 0.031344 | 0.0078654 | -0.031271 | -0.007838 | 7.2958e-05 | 2.7357e-05 | 0.046643 | 0.046644 | 0.046644 | 1 | 0 | 0.9976 | -0.016811 | 17.2754
11 | 0.012464 | 0.0031141 | -0.012455 | -0.0031112 | 8.9076e-06 | 2.891e-06 | 0.018623 | 0.018623 | 0.018623 | 0.99572 | -0.030152 | 0.99498 | -0.035349 | 6.8974
12 | -0.0052079 | -0.0012954 | 0.005209 | 0.0012955 | 1.0997e-06 | 4.5902e-08 | 0.0077886 | 0.0077885 | 0.0077886 | 0.99452 | -0.038605 | 0.99474 | -0.037057 | 2.8847
13 | -0.015489 | -0.0038811 | 0.01549 | 0.0038813 | 5.5471e-07 | 1.9169e-07 | 0.023124 | 0.023124 | 0.023124 | 0.99668 | -0.023287 | 0.99671 | -0.023029 | 8.5646
14 | 0.0065898 | 0.0016507 | -0.0065815 | -0.0016493 | 8.252e-06 | 1.3956e-06 | 0.0098381 | 0.0098387 | 0.0098387 | 0.99668 | -0.023287 | 0.99539 | -0.032344 | 3.644
15 | -0.021356 | -0.0053516 | 0.021373 | 0.0053578 | 1.7137e-05 | 6.2389e-06 | 0.031883 | 0.031883 | 0.031883 | 0.99671 | -0.023029 | 0.99754 | -0.017235 | 11.8085
16 | 0.0065815 | 0.0016493 | -0.0065796 | -0.001649 | 1.9015e-06 | 3.2229e-07 | 0.0098387 | 0.0098389 | 0.0098389 | 0.99539 | -0.032344 | 0.99509 | -0.034431 | 3.644
17 | -0.02601 | -0.0065198 | 0.026011 | 0.0065204 | 1.5287e-06 | 5.6672e-07 | 0.038799 | 0.038799 | 0.038799 | 0.99754 | -0.017235 | 0.9976 | -0.016811 | 14.37
18 | 0.0052594 | 0.0013176 | -0.0052569 | -0.0013175 | 2.4939e-06 | 1.1169e-07 | 0.0078447 | 0.007845 | 0.007845 | 0.9976 | -0.016811 | 0.99711 | -0.020238 | 2.9055
19 | -0.0048727 | -0.0012212 | 0.0048733 | 0.0012212 | 5.519e-07 | -3.513e-09 | 0.007292 | 0.0072919 | 0.007292 | 0.99434 | -0.039899 | 0.99445 | -0.039081 | 2.7007
20 | -0.0048733 | -0.0012212 | 0.0048739 | 0.0012212 | 5.6773e-07 | -3.6711e-09 | 0.0072919 | 0.0072918 | 0.0072919 | 0.99445 | -0.039081 | 0.99457 | -0.038239 | 2.7007
21 | -0.0059125 | -0.0014815 | 0.0059135 | 0.0014816 | 9.6772e-07 | 1.1495e-07 | 0.0088458 | 0.0088458 | 0.0088458 | 0.99457 | -0.038239 | 0.99474 | -0.037057 | 3.2762
22 | -0.011122 | -0.0027771 | 0.011125 | 0.0027779 | 2.6099e-06 | 8.0753e-07 | 0.016634 | 0.016634 | 0.016634 | 0.99474 | -0.037057 | 0.99498 | -0.035349 | 6.1608

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.056057 | 0.013856

## res_load
| p_mw | q_mvar
0 | 0.0011564 | 0.00028982
1 | 0.00038141 | 9.559e-05
2 | 0.00039191 | 9.8222e-05
3 | 0.00096303 | 0.00024136
4 | 0.003857 | 0.00096666
5 | 0.0023114 | 0.00057928
6 | 0.0088992 | 0.0022304
7 | 0.0058666 | 0.0014703
8 | 0.0046365 | 0.001162
9 | 0.0048727 | 0.0012212
10 | 0.0010387 | 0.00026032
11 | 0.0013297 | 0.00033327
12 | 0.0075192 | 0.0018845
13 | 0.0052569 | 0.0013175
14 | 0.0065796 | 0.001649

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1