## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3295-3_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_3295-3_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_3295-3_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_3295-3_1_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_3295-3_1_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_3295-3_1_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_3295-3_1_3_node_121 | 0.4 | n |  | TRUE
7 | bus_LV_3295-3_1_3_node_118 | 0.4 | n |  | TRUE
8 | bus_LV_3295-3_1_3_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_3295-3_1_3_node_223 | 0.4 | n |  | TRUE
10 | bus_LV_3295-3_1_3_node_119 | 0.4 | n |  | TRUE
11 | bus_LV_3295-3_1_3_node_117 | 0.4 | n |  | TRUE
12 | bus_LV_3295-3_1_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_3295-3_1_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_3295-3_1_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_3295-3_1_3_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_3295-3_1_3_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_3295-3_1_3_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_3295-3_1_3_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_3295-3_1_3_node_159 | 0.4 | n |  | TRUE
20 | bus_LV_3295-3_1_3_node_156 | 0.4 | n |  | TRUE
21 | bus_LV_3295-3_1_3_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_3295-3_1_3_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_3295-3_1_3_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_3295-3_1_3_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_3295-3_1_3_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_3295-3_1_3_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_3295-3_1_3_node_47 | 0.4 | n |  | TRUE
28 | bus_LV_3295-3_1_3_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_3295-3_1_3_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_3295-3_1_3_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_3295-3_1_3_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_3295-3_1_3_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_3295-3_1_3_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_3295-3_1_3_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_3295-3_1_3_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_3295-3_1_3_node_53 | 0.4 | n |  | TRUE
37 | bus_LV_3295-3_1_3_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_3295-3_1_3_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_3295-3_1_3_node_238 | 0.4 | n |  | TRUE
40 | bus_LV_3295-3_1_3_node_262 | 0.4 | n |  | TRUE
41 | bus_LV_3295-3_1_3_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_3295-3_1_3_node_260 | 0.4 | n |  | TRUE
43 | bus_LV_3295-3_1_3_node_237 | 0.4 | n |  | TRUE
44 | bus_LV_3295-3_1_3_node_263 | 0.4 | n |  | TRUE
45 | bus_LV_3295-3_1_3_node_167 | 0.4 | n |  | TRUE
46 | bus_LV_3295-3_1_3_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_3295-3_1_3_node_58 | 0.4 | n |  | TRUE
48 | bus_LV_3295-3_1_3_node_59 | 0.4 | n |  | TRUE
49 | bus_LV_3295-3_1_3_node_60 | 0.4 | n |  | TRUE
50 | bus_LV_3295-3_1_3_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_3295-3_1_3_node_225 | 0.4 | n |  | TRUE
52 | bus_LV_3295-3_1_3_node_226 | 0.4 | n |  | TRUE
53 | bus_LV_3295-3_1_3_node_258 | 0.4 | n |  | TRUE
54 | bus_LV_3295-3_1_3_node_264 | 0.4 | n |  | TRUE
55 | bus_LV_3295-3_1_3_node_62 | 0.4 | n |  | TRUE
56 | bus_LV_3295-3_1_3_node_63 | 0.4 | n |  | TRUE
57 | bus_LV_3295-3_1_3_node_64 | 0.4 | n |  | TRUE
58 | bus_LV_3295-3_1_3_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_3295-3_1_3_node_66 | 0.4 | n |  | TRUE
60 | bus_LV_3295-3_1_3_node_67 | 0.4 | n |  | TRUE
61 | bus_LV_3295-3_1_3_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_3295-3_1_3_node_69 | 0.4 | n |  | TRUE
63 | bus_LV_3295-3_1_3_node_251 | 0.4 | n |  | TRUE
64 | bus_LV_3295-3_1_3_node_250 | 0.4 | n |  | TRUE
65 | bus_LV_3295-3_1_3_node_246 | 0.4 | n |  | TRUE
66 | bus_LV_3295-3_1_3_node_252 | 0.4 | n |  | TRUE
67 | bus_LV_3295-3_1_3_node_247 | 0.4 | n |  | TRUE
68 | bus_LV_3295-3_1_3_node_70 | 0.4 | n |  | TRUE
69 | bus_LV_3295-3_1_3_node_71 | 0.4 | n |  | TRUE
70 | bus_LV_3295-3_1_3_node_72 | 0.4 | n |  | TRUE
71 | bus_LV_3295-3_1_3_node_304 | 0.4 | n |  | TRUE
72 | bus_LV_3295-3_1_3_node_74 | 0.4 | n |  | TRUE
73 | bus_LV_3295-3_1_3_node_303 | 0.4 | n |  | TRUE
74 | bus_LV_3295-3_1_3_node_78 | 0.4 | n |  | TRUE
75 | bus_LV_3295-3_1_3_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_3295-3_1_3_node_76 | 0.4 | n |  | TRUE
77 | bus_LV_3295-3_1_3_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_3295-3_1_3_node_115 | 0.4 | n |  | TRUE
79 | bus_LV_3295-3_1_3_node_116 | 0.4 | n |  | TRUE
80 | bus_LV_3295-3_1_3_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_3295-3_1_3_node_81 | 0.4 | n |  | TRUE
82 | bus_LV_3295-3_1_3_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_3295-3_1_3_node_83 | 0.4 | n |  | TRUE
84 | bus_LV_3295-3_1_3_node_84 | 0.4 | n |  | TRUE
85 | bus_LV_3295-3_1_3_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_3295-3_1_3_node_86 | 0.4 | n |  | TRUE
87 | bus_LV_3295-3_1_3_node_87 | 0.4 | n |  | TRUE
88 | bus_LV_3295-3_1_3_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_3295-3_1_3_node_123 | 0.4 | n |  | TRUE
90 | bus_LV_3295-3_1_3_node_130 | 0.4 | n |  | TRUE
91 | bus_LV_3295-3_1_3_node_185 | 0.4 | n |  | TRUE
92 | bus_LV_3295-3_1_3_node_131 | 0.4 | n |  | TRUE
93 | bus_LV_3295-3_1_3_node_168 | 0.4 | n |  | TRUE
94 | bus_LV_3295-3_1_3_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_3295-3_1_3_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_3295-3_1_3_node_98 | 0.4 | n |  | TRUE
97 | bus_LV_3295-3_1_3_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_3295-3_1_3_node_100 | 0.4 | n |  | TRUE
99 | bus_LV_3295-3_1_3_node_101 | 0.4 | n |  | TRUE
100 | bus_LV_3295-3_1_3_node_102 | 0.4 | n |  | TRUE
101 | bus_LV_3295-3_1_3_node_142 | 0.4 | n |  | TRUE
102 | bus_LV_3295-3_1_3_node_140 | 0.4 | n |  | TRUE
103 | bus_LV_3295-3_1_3_node_105 | 0.4 | n |  | TRUE
104 | bus_LV_3295-3_1_3_node_106 | 0.4 | n |  | TRUE
105 | bus_LV_3295-3_1_3_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_3295-3_1_3_node_108 | 0.4 | n |  | TRUE
107 | bus_LV_3295-3_1_3_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_3295-3_1_3_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_3295-3_1_3_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_3295-3_1_3_node_201 | 0.4 | n |  | TRUE
111 | bus_LV_3295-3_1_3_node_227 | 0.4 | n |  | TRUE
112 | bus_LV_3295-3_1_3_node_199 | 0.4 | n |  | TRUE
113 | bus_LV_3295-3_1_3_node_120 | 0.4 | n |  | TRUE
114 | bus_LV_3295-3_1_3_node_144 | 0.4 | n |  | TRUE
115 | bus_LV_3295-3_1_3_node_145 | 0.4 | n |  | TRUE
116 | bus_LV_3295-3_1_3_node_222 | 0.4 | n |  | TRUE
117 | bus_LV_3295-3_1_3_node_186 | 0.4 | n |  | TRUE
118 | bus_LV_3295-3_1_3_node_132 | 0.4 | n |  | TRUE
119 | bus_LV_3295-3_1_3_node_133 | 0.4 | n |  | TRUE
120 | bus_LV_3295-3_1_3_node_134 | 0.4 | n |  | TRUE
121 | bus_LV_3295-3_1_3_node_135 | 0.4 | n |  | TRUE
122 | bus_LV_3295-3_1_3_node_141 | 0.4 | n |  | TRUE
123 | bus_LV_3295-3_1_3_node_139 | 0.4 | n |  | TRUE
124 | bus_LV_3295-3_1_3_node_136 | 0.4 | n |  | TRUE
125 | bus_LV_3295-3_1_3_node_137 | 0.4 | n |  | TRUE
126 | bus_LV_3295-3_1_3_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_3295-3_1_3_node_148 | 0.4 | n |  | TRUE
128 | bus_LV_3295-3_1_3_node_146 | 0.4 | n |  | TRUE
129 | bus_LV_3295-3_1_3_node_147 | 0.4 | n |  | TRUE
130 | bus_LV_3295-3_1_3_node_149 | 0.4 | n |  | TRUE
131 | bus_LV_3295-3_1_3_node_150 | 0.4 | n |  | TRUE
132 | bus_LV_3295-3_1_3_node_151 | 0.4 | n |  | TRUE
133 | bus_LV_3295-3_1_3_node_170 | 0.4 | n |  | TRUE
134 | bus_LV_3295-3_1_3_node_210 | 0.4 | n |  | TRUE
135 | bus_LV_3295-3_1_3_node_165 | 0.4 | n |  | TRUE
136 | bus_LV_3295-3_1_3_node_211 | 0.4 | n |  | TRUE
137 | bus_LV_3295-3_1_3_node_152 | 0.4 | n |  | TRUE
138 | bus_LV_3295-3_1_3_node_153 | 0.4 | n |  | TRUE
139 | bus_LV_3295-3_1_3_node_154 | 0.4 | n |  | TRUE
140 | bus_LV_3295-3_1_3_node_155 | 0.4 | n |  | TRUE
141 | bus_LV_3295-3_1_3_node_157 | 0.4 | n |  | TRUE
142 | bus_LV_3295-3_1_3_node_158 | 0.4 | n |  | TRUE
143 | bus_LV_3295-3_1_3_node_202 | 0.4 | n |  | TRUE
144 | bus_LV_3295-3_1_3_node_182 | 0.4 | n |  | TRUE
145 | bus_LV_3295-3_1_3_node_204 | 0.4 | n |  | TRUE
146 | bus_LV_3295-3_1_3_node_191 | 0.4 | n |  | TRUE
147 | bus_LV_3295-3_1_3_node_180 | 0.4 | n |  | TRUE
148 | bus_LV_3295-3_1_3_node_160 | 0.4 | n |  | TRUE
149 | bus_LV_3295-3_1_3_node_161 | 0.4 | n |  | TRUE
150 | bus_LV_3295-3_1_3_node_162 | 0.4 | n |  | TRUE
151 | bus_LV_3295-3_1_3_node_163 | 0.4 | n |  | TRUE
152 | bus_LV_3295-3_1_3_node_164 | 0.4 | n |  | TRUE
153 | bus_LV_3295-3_1_3_node_169 | 0.4 | n |  | TRUE
154 | bus_LV_3295-3_1_3_node_166 | 0.4 | n |  | TRUE
155 | bus_LV_3295-3_1_3_node_213 | 0.4 | n |  | TRUE
156 | bus_LV_3295-3_1_3_node_214 | 0.4 | n |  | TRUE
157 | bus_LV_3295-3_1_3_node_224 | 0.4 | n |  | TRUE
158 | bus_LV_3295-3_1_3_node_215 | 0.4 | n |  | TRUE
159 | bus_LV_3295-3_1_3_node_216 | 0.4 | n |  | TRUE
160 | bus_LV_3295-3_1_3_node_184 | 0.4 | n |  | TRUE
161 | bus_LV_3295-3_1_3_node_183 | 0.4 | n |  | TRUE
162 | bus_LV_3295-3_1_3_node_171 | 0.4 | n |  | TRUE
163 | bus_LV_3295-3_1_3_node_172 | 0.4 | n |  | TRUE
164 | bus_LV_3295-3_1_3_node_173 | 0.4 | n |  | TRUE
165 | bus_LV_3295-3_1_3_node_174 | 0.4 | n |  | TRUE
166 | bus_LV_3295-3_1_3_node_175 | 0.4 | n |  | TRUE
167 | bus_LV_3295-3_1_3_node_178 | 0.4 | n |  | TRUE
168 | bus_LV_3295-3_1_3_node_176 | 0.4 | n |  | TRUE
169 | bus_LV_3295-3_1_3_node_189 | 0.4 | n |  | TRUE
170 | bus_LV_3295-3_1_3_node_177 | 0.4 | n |  | TRUE
171 | bus_LV_3295-3_1_3_node_190 | 0.4 | n |  | TRUE
172 | bus_LV_3295-3_1_3_node_188 | 0.4 | n |  | TRUE
173 | bus_LV_3295-3_1_3_node_193 | 0.4 | n |  | TRUE
174 | bus_LV_3295-3_1_3_node_192 | 0.4 | n |  | TRUE
175 | bus_LV_3295-3_1_3_node_194 | 0.4 | n |  | TRUE
176 | bus_LV_3295-3_1_3_node_179 | 0.4 | n |  | TRUE
177 | bus_LV_3295-3_1_3_node_181 | 0.4 | n |  | TRUE
178 | bus_LV_3295-3_1_3_node_187 | 0.4 | n |  | TRUE
179 | bus_LV_3295-3_1_3_node_203 | 0.4 | n |  | TRUE
180 | bus_LV_3295-3_1_3_node_195 | 0.4 | n |  | TRUE
181 | bus_LV_3295-3_1_3_node_196 | 0.4 | n |  | TRUE
182 | bus_LV_3295-3_1_3_node_197 | 0.4 | n |  | TRUE
183 | bus_LV_3295-3_1_3_node_198 | 0.4 | n |  | TRUE
184 | bus_LV_3295-3_1_3_node_200 | 0.4 | n |  | TRUE
185 | bus_LV_3295-3_1_3_node_228 | 0.4 | n |  | TRUE
186 | bus_LV_3295-3_1_3_node_217 | 0.4 | n |  | TRUE
187 | bus_LV_3295-3_1_3_node_209 | 0.4 | n |  | TRUE
188 | bus_LV_3295-3_1_3_node_205 | 0.4 | n |  | TRUE
189 | bus_LV_3295-3_1_3_node_206 | 0.4 | n |  | TRUE
190 | bus_LV_3295-3_1_3_node_207 | 0.4 | n |  | TRUE
191 | bus_LV_3295-3_1_3_node_208 | 0.4 | n |  | TRUE
192 | bus_LV_3295-3_1_3_node_212 | 0.4 | n |  | TRUE
193 | bus_LV_3295-3_1_3_node_218 | 0.4 | n |  | TRUE
194 | bus_LV_3295-3_1_3_node_219 | 0.4 | n |  | TRUE
195 | bus_LV_3295-3_1_3_node_231 | 0.4 | n |  | TRUE
196 | bus_LV_3295-3_1_3_node_232 | 0.4 | n |  | TRUE
197 | bus_LV_3295-3_1_3_node_235 | 0.4 | n |  | TRUE
198 | bus_LV_3295-3_1_3_node_233 | 0.4 | n |  | TRUE
199 | bus_LV_3295-3_1_3_node_234 | 0.4 | n |  | TRUE
200 | bus_LV_3295-3_1_3_node_220 | 0.4 | n |  | TRUE
201 | bus_LV_3295-3_1_3_node_221 | 0.4 | n |  | TRUE
202 | bus_LV_3295-3_1_3_node_249 | 0.4 | n |  | TRUE
203 | bus_LV_3295-3_1_3_node_229 | 0.4 | n |  | TRUE
204 | bus_LV_3295-3_1_3_node_230 | 0.4 | n |  | TRUE
205 | bus_LV_3295-3_1_3_node_253 | 0.4 | n |  | TRUE
206 | bus_LV_3295-3_1_3_node_236 | 0.4 | n |  | TRUE
207 | bus_LV_3295-3_1_3_node_261 | 0.4 | n |  | TRUE
208 | bus_LV_3295-3_1_3_node_248 | 0.4 | n |  | TRUE
209 | bus_MV_150_0_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3295-3_1_3_load_5 | 0 | 0.00085309 | 0.0002138 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3295-3_1_3_load_8 | 3 | 0.0012689 | 0.00031801 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3295-3_1_3_load_121 | 6 | 0.0006957 | 0.00017436 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3295-3_1_3_load_14 | 8 | 0.0020006 | 0.00050139 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3295-3_1_3_load_223 | 9 | 0.00078254 | 0.00019612 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3295-3_1_3_load_119 | 10 | 0.0012923 | 0.00032389 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3295-3_1_3_load_117 | 11 | 0.00072786 | 0.00018242 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3295-3_1_3_load_11 | 13 | 0.00064715 | 0.00016219 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3295-3_1_3_load_13 | 14 | 0.00084424 | 0.00021159 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3295-3_1_3_load_37 | 15 | 0.0004677 | 0.00011722 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3295-3_1_3_load_38 | 16 | 0.00021886 | 5.4851e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3295-3_1_3_load_39 | 17 | 0.0002327 | 5.8321e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3295-3_1_3_load_40 | 18 | 0.00074899 | 0.00018771 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3295-3_1_3_load_159 | 19 | 0.0011011 | 0.00027595 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3295-3_1_3_load_156 | 20 | 0.00082933 | 0.00020785 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3295-3_1_3_load_41 | 21 | 0.00088279 | 0.00022125 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3295-3_1_3_load_42 | 22 | 0.00037832 | 9.4816e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3295-3_1_3_load_43 | 23 | 0.00079481 | 0.0001992 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3295-3_1_3_load_44 | 24 | 0.00051678 | 0.00012952 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3295-3_1_3_load_45 | 25 | 0.00044197 | 0.00011077 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3295-3_1_3_load_46 | 26 | 0.0006079 | 0.00015236 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3295-3_1_3_load_56 | 28 | 0.0012147 | 0.00030442 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3295-3_1_3_load_77 | 29 | 0.0002631 | 6.5938e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3295-3_1_3_load_48 | 32 | 0.0006268 | 0.00015709 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3295-3_1_3_load_49 | 33 | 0.00043635 | 0.00010936 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3295-3_1_3_load_50 | 34 | 0.00052227 | 0.00013089 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3295-3_1_3_load_53 | 36 | 0.00088514 | 0.00022184 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3295-3_1_3_load_54 | 37 | 0.00081588 | 0.00020448 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3295-3_1_3_load_55 | 38 | 0.00046011 | 0.00011532 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3295-3_1_3_load_262 | 40 | 0.0009816 | 0.00024601 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3295-3_1_3_load_88 | 41 | 0.00094373 | 0.00023652 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3295-3_1_3_load_260 | 42 | 0.00098612 | 0.00024715 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3295-3_1_3_load_237 | 43 | 0.00087286 | 0.00021876 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3295-3_1_3_load_263 | 44 | 0.00087857 | 0.00022019 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3295-3_1_3_load_167 | 45 | 0.0007999 | 0.00020047 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3295-3_1_3_load_57 | 46 | 0.00042564 | 0.00010668 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3295-3_1_3_load_61 | 50 | 0.00067042 | 0.00016802 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3295-3_1_3_load_225 | 51 | 0.0009403 | 0.00023566 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3295-3_1_3_load_258 | 53 | 0.0013948 | 0.00034958 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3295-3_1_3_load_264 | 54 | 0.00060081 | 0.00015058 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3295-3_1_3_load_62 | 55 | 0.0006316 | 0.0001583 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3295-3_1_3_load_63 | 56 | 0.00081878 | 0.00020521 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3295-3_1_3_load_64 | 57 | 0.0010572 | 0.00026495 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3295-3_1_3_load_66 | 59 | 0.0012817 | 0.00032122 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3295-3_1_3_load_67 | 60 | 0.00086983 | 0.000218 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3295-3_1_3_load_68 | 61 | 0.00082215 | 0.00020605 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3295-3_1_3_load_69 | 62 | 0.00078433 | 0.00019657 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3295-3_1_3_load_251 | 63 | 0.0008595 | 0.00021541 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3295-3_1_3_load_250 | 64 | 0.0008741 | 0.00021907 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3295-3_1_3_load_246 | 65 | 0.0012544 | 0.00031438 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3295-3_1_3_load_252 | 66 | 0.00081161 | 0.00020341 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3295-3_1_3_load_247 | 67 | 0.00061601 | 0.00015439 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3295-3_1_3_load_70 | 68 | 0.0010967 | 0.00027486 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3295-3_1_3_load_71 | 69 | 0.001068 | 0.00026765 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3295-3_1_3_load_304 | 71 | 0.00061937 | 0.00015523 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3295-3_1_3_load_74 | 72 | 0.00022908 | 5.7414e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3295-3_1_3_load_303 | 73 | 0.00069205 | 0.00017344 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3295-3_1_3_load_78 | 74 | 0.00014009 | 3.5111e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3295-3_1_3_load_112 | 75 | 0.0002698 | 6.7617e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3295-3_1_3_load_114 | 77 | 0.0011593 | 0.00029054 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3295-3_1_3_load_116 | 79 | 0.00090089 | 0.00022578 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3295-3_1_3_load_80 | 80 | 0.0015887 | 0.00039816 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3295-3_1_3_load_81 | 81 | 0.0012631 | 0.00031657 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3295-3_1_3_load_82 | 82 | 0.0012909 | 0.00032352 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3295-3_1_3_load_84 | 84 | 0.0007962 | 0.00019955 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3295-3_1_3_load_85 | 85 | 0.00026283 | 6.5873e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3295-3_1_3_load_86 | 86 | 0.00017612 | 4.414e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3295-3_1_3_load_122 | 88 | 0.00017143 | 4.2963e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3295-3_1_3_load_123 | 89 | 0.00047953 | 0.00012018 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3295-3_1_3_load_130 | 90 | 0.00091813 | 0.00023011 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3295-3_1_3_load_185 | 91 | 0.0008684 | 0.00021764 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3295-3_1_3_load_131 | 92 | 0.00067758 | 0.00016982 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3295-3_1_3_load_168 | 93 | 0.00071178 | 0.00017839 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3295-3_1_3_load_96 | 94 | 0.00080045 | 0.00020061 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3295-3_1_3_load_97 | 95 | 0.00086075 | 0.00021572 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3295-3_1_3_load_98 | 96 | 0.0007877 | 0.00019742 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3295-3_1_3_load_99 | 97 | 0.00075482 | 0.00018918 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3295-3_1_3_load_100 | 98 | 0.00083112 | 0.0002083 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3295-3_1_3_load_101 | 99 | 0.00091022 | 0.00022812 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3295-3_1_3_load_102 | 100 | 0.00065349 | 0.00016378 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3295-3_1_3_load_142 | 101 | 0.00075805 | 0.00018999 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3295-3_1_3_load_140 | 102 | 0.0007765 | 0.00019461 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3295-3_1_3_load_105 | 103 | 0.00093267 | 0.00023375 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3295-3_1_3_load_106 | 104 | 0.00089099 | 0.0002233 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3295-3_1_3_load_107 | 105 | 0.00088812 | 0.00022258 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3295-3_1_3_load_108 | 106 | 0.00089323 | 0.00022387 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3295-3_1_3_load_109 | 107 | 0.0012968 | 0.00032501 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3295-3_1_3_load_110 | 108 | 0.0006471 | 0.00016218 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3295-3_1_3_load_111 | 109 | 0.00078282 | 0.00019619 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3295-3_1_3_load_227 | 111 | 0.00085236 | 0.00021362 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3295-3_1_3_load_199 | 112 | 0.0008967 | 0.00022473 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3295-3_1_3_load_120 | 113 | 0.00076511 | 0.00019175 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3295-3_1_3_load_144 | 114 | 0.00047556 | 0.00011919 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3295-3_1_3_load_145 | 115 | 0.00075336 | 0.00018881 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3295-3_1_3_load_222 | 116 | 0.00060219 | 0.00015092 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3295-3_1_3_load_186 | 117 | 0.00021245 | 5.3244e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3295-3_1_3_load_132 | 118 | 0.00069278 | 0.00017363 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3295-3_1_3_load_133 | 119 | 0.00075876 | 0.00019016 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3295-3_1_3_load_134 | 120 | 0.00077614 | 0.00019452 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3295-3_1_3_load_135 | 121 | 0.00084708 | 0.0002123 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3295-3_1_3_load_141 | 122 | 0.00078055 | 0.00019562 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3295-3_1_3_load_139 | 123 | 0.00079413 | 0.00019903 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3295-3_1_3_load_136 | 124 | 0.00078899 | 0.00019774 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3295-3_1_3_load_137 | 125 | 0.0007661 | 0.000192 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3295-3_1_3_load_138 | 126 | 0.0008171 | 0.00020479 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3295-3_1_3_load_148 | 127 | 0.00082018 | 0.00020556 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3295-3_1_3_load_146 | 128 | 0.0012291 | 0.00030803 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3295-3_1_3_load_147 | 129 | 0.00057399 | 0.00014386 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3295-3_1_3_load_150 | 131 | 0.00078498 | 0.00019674 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3295-3_1_3_load_170 | 133 | 0.00041348 | 0.00010363 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3295-3_1_3_load_210 | 134 | 0.00057271 | 0.00014353 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3295-3_1_3_load_152 | 137 | 0.00090478 | 0.00022676 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3295-3_1_3_load_153 | 138 | 0.0010469 | 0.00026239 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3295-3_1_3_load_154 | 139 | 0.0015031 | 0.00037672 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3295-3_1_3_load_155 | 140 | 0.0013293 | 0.00033316 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3295-3_1_3_load_157 | 141 | 0.003497 | 0.00087643 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3295-3_1_3_load_182 | 144 | 0.0018818 | 0.00047161 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3295-3_1_3_load_204 | 145 | 0.001118 | 0.00028019 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3295-3_1_3_load_191 | 146 | 0.001308 | 0.00032781 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3295-3_1_3_load_180 | 147 | 0.0016391 | 0.0004108 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3295-3_1_3_load_160 | 148 | 0.00072188 | 0.00018092 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3295-3_1_3_load_161 | 149 | 0.0007485 | 0.00018759 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3295-3_1_3_load_162 | 150 | 0.0015445 | 0.00038708 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_3295-3_1_3_load_163 | 151 | 0.00045573 | 0.00011422 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_3295-3_1_3_load_164 | 152 | 0.0016501 | 0.00041356 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_3295-3_1_3_load_169 | 153 | 0.00078978 | 0.00019794 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_3295-3_1_3_load_213 | 155 | 0.0024304 | 0.00060912 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_3295-3_1_3_load_214 | 156 | 0.00092165 | 0.00023099 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_3295-3_1_3_load_224 | 157 | 0.00053994 | 0.00013532 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_3295-3_1_3_load_216 | 159 | 0.00094016 | 0.00023563 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_3295-3_1_3_load_184 | 160 | 0.00083729 | 0.00020985 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_3295-3_1_3_load_183 | 161 | 0.0006372 | 0.0001597 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_3295-3_1_3_load_171 | 162 | 0.0014479 | 0.00036287 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_3295-3_1_3_load_172 | 163 | 0.00020873 | 5.2312e-05 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_3295-3_1_3_load_174 | 165 | 0.00022636 | 5.6731e-05 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_3295-3_1_3_load_175 | 166 | 0.00033857 | 8.4854e-05 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_3295-3_1_3_load_178 | 167 | 0.00025521 | 6.3963e-05 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_3295-3_1_3_load_189 | 169 | 0.0010447 | 0.00026182 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_3295-3_1_3_load_190 | 171 | 0.00021921 | 5.494e-05 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_3295-3_1_3_load_188 | 172 | 0.00099129 | 0.00024844 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_3295-3_1_3_load_192 | 174 | 0.0011203 | 0.00028077 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_3295-3_1_3_load_194 | 175 | 0.00026044 | 6.5272e-05 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_3295-3_1_3_load_179 | 176 | 0.00061579 | 0.00015433 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_3295-3_1_3_load_181 | 177 | 0.0011388 | 0.00028541 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_3295-3_1_3_load_187 | 178 | 0.00023604 | 5.9157e-05 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_3295-3_1_3_load_203 | 179 | 0.0010198 | 0.00025558 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_3295-3_1_3_load_195 | 180 | 0.00078381 | 0.00019644 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_3295-3_1_3_load_196 | 181 | 0.00090966 | 0.00022798 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_3295-3_1_3_load_197 | 182 | 0.00085424 | 0.00021409 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_3295-3_1_3_load_198 | 183 | 0.0005506 | 0.00013799 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_3295-3_1_3_load_200 | 184 | 0.00098946 | 0.00024798 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_3295-3_1_3_load_228 | 185 | 0.00074345 | 0.00018633 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_3295-3_1_3_load_217 | 186 | 0.00057926 | 0.00014518 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_3295-3_1_3_load_205 | 188 | 0.00077736 | 0.00019483 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_3295-3_1_3_load_206 | 189 | 0.00079848 | 0.00020012 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_3295-3_1_3_load_212 | 192 | 0.0010263 | 0.00025722 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_3295-3_1_3_load_218 | 193 | 0.00089997 | 0.00022555 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_3295-3_1_3_load_219 | 194 | 0.0016867 | 0.00042273 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_3295-3_1_3_load_231 | 195 | 0.0011266 | 0.00028236 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_3295-3_1_3_load_232 | 196 | 0.0010445 | 0.00026178 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_3295-3_1_3_load_235 | 197 | 0.0007031 | 0.00017621 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_3295-3_1_3_load_233 | 198 | 0.00063834 | 0.00015998 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_3295-3_1_3_load_234 | 199 | 0.00096097 | 0.00024084 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_3295-3_1_3_load_220 | 200 | 0.0010527 | 0.00026384 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_3295-3_1_3_load_221 | 201 | 0.0027195 | 0.00068157 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_3295-3_1_3_load_249 | 202 | 0.001486 | 0.00037243 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_3295-3_1_3_load_229 | 203 | 0.0010047 | 0.00025181 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_3295-3_1_3_load_230 | 204 | 0.0008161 | 0.00020454 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_3295-3_1_3_load_253 | 205 | 0.00048183 | 0.00012076 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_3295-3_1_3_load_236 | 206 | 0.00093901 | 0.00023534 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_3295-3_1_3_load_261 | 207 | 0.0011257 | 0.00028214 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_3295-3_1_3_load_248 | 208 | 0.00052318 | 0.00013112 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 161 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3295-3_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0050016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3295-3_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.040113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3295-3_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.021357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3295-3_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.099172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3295-3_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3295-3_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.019024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3295-3_1_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.070371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3295-3_1_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0093863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3295-3_1_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.0020559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3295-3_1_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.014128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3295-3_1_3_line_10 | NAYY 4x150 SE | 7 | 11 | 0.011293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3295-3_1_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.063246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3295-3_1_3_line_12 | NAYY 4x150 SE | 9 | 116 | 0.030641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3295-3_1_3_line_13 | NAYY 4x150 SE | 10 | 113 | 0.022966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3295-3_1_3_line_14 | NAYY 4x150 SE | 11 | 100 | 0.012147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3295-3_1_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.032677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3295-3_1_3_line_16 | NAYY 4x150 SE | 12 | 13 | 0.048493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3295-3_1_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.24799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3295-3_1_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.0050532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3295-3_1_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.017267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3295-3_1_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.013268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3295-3_1_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.0046867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3295-3_1_3_line_22 | NAYY 4x150 SE | 20 | 139 | 0.0056878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3295-3_1_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.097631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3295-3_1_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.11934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3295-3_1_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.080258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3295-3_1_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.072287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3295-3_1_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.043756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3295-3_1_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.068524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3295-3_1_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.0078338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3295-3_1_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.13934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3295-3_1_3_line_31 | NAYY 4x150 SE | 28 | 30 | 0.061314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3295-3_1_3_line_32 | NAYY 4x150 SE | 29 | 31 | 0.15836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3295-3_1_3_line_33 | NAYY 4x150 SE | 30 | 38 | 0.044224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3295-3_1_3_line_34 | NAYY 4x150 SE | 30 | 34 | 0.070232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3295-3_1_3_line_35 | NAYY 4x150 SE | 31 | 74 | 0.054816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3295-3_1_3_line_36 | NAYY 4x150 SE | 31 | 70 | 0.13118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3295-3_1_3_line_37 | NAYY 4x150 SE | 32 | 33 | 0.018037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3295-3_1_3_line_38 | NAYY 4x150 SE | 32 | 34 | 0.023181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3295-3_1_3_line_39 | NAYY 4x150 SE | 33 | 35 | 0.025466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3295-3_1_3_line_40 | NAYY 4x150 SE | 35 | 36 | 0.040573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3295-3_1_3_line_41 | NAYY 4x150 SE | 35 | 37 | 0.0062877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3295-3_1_3_line_42 | NAYY 4x150 SE | 36 | 39 | 0.0024596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3295-3_1_3_line_43 | NAYY 4x150 SE | 37 | 40 | 0.019582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3295-3_1_3_line_44 | NAYY 4x150 SE | 38 | 41 | 0.0074198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3295-3_1_3_line_45 | NAYY 4x150 SE | 39 | 42 | 0.022514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3295-3_1_3_line_46 | NAYY 4x150 SE | 39 | 43 | 0.016149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3295-3_1_3_line_47 | NAYY 4x150 SE | 40 | 44 | 0.041007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3295-3_1_3_line_48 | NAYY 4x150 SE | 41 | 45 | 0.0068127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3295-3_1_3_line_49 | NAYY 4x150 SE | 42 | 207 | 0.017343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3295-3_1_3_line_50 | NAYY 4x150 SE | 43 | 206 | 0.0061992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3295-3_1_3_line_51 | NAYY 4x150 SE | 44 | 54 | 0.0068884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3295-3_1_3_line_52 | NAYY 4x150 SE | 45 | 93 | 0.0073621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3295-3_1_3_line_53 | NAYY 4x150 SE | 46 | 47 | 0.088542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3295-3_1_3_line_54 | NAYY 4x150 SE | 47 | 48 | 0.19307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3295-3_1_3_line_55 | NAYY 4x150 SE | 48 | 49 | 0.23551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3295-3_1_3_line_56 | NAYY 4x150 SE | 48 | 50 | 0.10836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3295-3_1_3_line_57 | NAYY 4x150 SE | 49 | 51 | 0.10706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3295-3_1_3_line_58 | NAYY 4x150 SE | 49 | 52 | 0.30481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3295-3_1_3_line_59 | NAYY 4x150 SE | 52 | 53 | 0.015553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3295-3_1_3_line_60 | NAYY 4x150 SE | 52 | 54 | 0.028151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3295-3_1_3_line_61 | NAYY 4x150 SE | 53 | 202 | 0.025388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3295-3_1_3_line_62 | NAYY 4x150 SE | 55 | 56 | 0.042873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3295-3_1_3_line_63 | NAYY 4x150 SE | 55 | 57 | 0.019072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3295-3_1_3_line_64 | NAYY 4x150 SE | 56 | 58 | 0.0092728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3295-3_1_3_line_65 | NAYY 4x150 SE | 57 | 59 | 0.019573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3295-3_1_3_line_66 | NAYY 4x150 SE | 58 | 60 | 0.034116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3295-3_1_3_line_67 | NAYY 4x150 SE | 58 | 61 | 0.015073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3295-3_1_3_line_68 | NAYY 4x150 SE | 59 | 62 | 0.0042026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3295-3_1_3_line_69 | NAYY 4x150 SE | 60 | 63 | 0.044082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3295-3_1_3_line_70 | NAYY 4x150 SE | 61 | 64 | 0.00011378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3295-3_1_3_line_71 | NAYY 4x150 SE | 62 | 65 | 0.017926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3295-3_1_3_line_72 | NAYY 4x150 SE | 63 | 66 | 0.020044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3295-3_1_3_line_73 | NAYY 4x150 SE | 65 | 67 | 0.0026955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3295-3_1_3_line_74 | NAYY 4x150 SE | 66 | 79 | 0.021801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3295-3_1_3_line_75 | NAYY 4x150 SE | 67 | 208 | 0.019368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3295-3_1_3_line_76 | NAYY 4x150 SE | 68 | 69 | 0.018457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3295-3_1_3_line_77 | NAYY 4x150 SE | 68 | 70 | 0.059128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3295-3_1_3_line_78 | NAYY 4x150 SE | 69 | 71 | 0.10554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3295-3_1_3_line_79 | NAYY 4x150 SE | 70 | 72 | 0.084537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3295-3_1_3_line_80 | NAYY 4x150 SE | 71 | 73 | 0.0027655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3295-3_1_3_line_81 | NAYY 4x150 SE | 74 | 75 | 0.017027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3295-3_1_3_line_82 | NAYY 4x150 SE | 76 | 77 | 0.040484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3295-3_1_3_line_83 | NAYY 4x150 SE | 76 | 78 | 0.27414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3295-3_1_3_line_84 | NAYY 4x150 SE | 78 | 79 | 0.20326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3295-3_1_3_line_85 | NAYY 4x150 SE | 80 | 81 | 0.0020513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_3295-3_1_3_line_86 | NAYY 4x150 SE | 80 | 82 | 0.024619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_3295-3_1_3_line_87 | NAYY 4x150 SE | 81 | 83 | 0.009163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_3295-3_1_3_line_88 | NAYY 4x150 SE | 82 | 84 | 0.0080003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_3295-3_1_3_line_89 | NAYY 4x150 SE | 83 | 85 | 0.01639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_3295-3_1_3_line_90 | NAYY 4x150 SE | 83 | 86 | 0.01122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3295-3_1_3_line_91 | NAYY 4x150 SE | 84 | 87 | 0.0097844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_3295-3_1_3_line_92 | NAYY 4x150 SE | 85 | 88 | 0.0034023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
93 | LV_3295-3_1_3_line_93 | NAYY 4x150 SE | 86 | 89 | 0.0018302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3295-3_1_3_line_94 | NAYY 4x150 SE | 87 | 90 | 0.0080149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
95 | LV_3295-3_1_3_line_95 | NAYY 4x150 SE | 88 | 91 | 0.0073817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_3295-3_1_3_line_96 | NAYY 4x150 SE | 90 | 92 | 0.0081245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
97 | LV_3295-3_1_3_line_97 | NAYY 4x150 SE | 91 | 117 | 0.0013729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_3295-3_1_3_line_98 | NAYY 4x150 SE | 92 | 109 | 0.014209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
99 | LV_3295-3_1_3_line_99 | NAYY 4x150 SE | 93 | 160 | 0.014202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3295-3_1_3_line_100 | NAYY 4x150 SE | 94 | 95 | 0.0014621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3295-3_1_3_line_101 | NAYY 4x150 SE | 94 | 96 | 0.010154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3295-3_1_3_line_102 | NAYY 4x150 SE | 95 | 97 | 0.0271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3295-3_1_3_line_103 | NAYY 4x150 SE | 96 | 98 | 0.0049342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3295-3_1_3_line_104 | NAYY 4x150 SE | 97 | 99 | 0.001577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3295-3_1_3_line_105 | NAYY 4x150 SE | 98 | 100 | 0.030192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3295-3_1_3_line_106 | NAYY 4x150 SE | 99 | 101 | 0.010748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3295-3_1_3_line_107 | NAYY 4x150 SE | 101 | 102 | 0.01485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3295-3_1_3_line_108 | NAYY 4x150 SE | 102 | 126 | 0.0061331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3295-3_1_3_line_109 | NAYY 4x150 SE | 103 | 104 | 0.0060573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
110 | LV_3295-3_1_3_line_110 | NAYY 4x150 SE | 103 | 105 | 0.0084271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
111 | LV_3295-3_1_3_line_111 | NAYY 4x150 SE | 104 | 106 | 0.0017043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
112 | LV_3295-3_1_3_line_112 | NAYY 4x150 SE | 105 | 107 | 0.0087334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
113 | LV_3295-3_1_3_line_113 | NAYY 4x150 SE | 106 | 108 | 0.0060786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
114 | LV_3295-3_1_3_line_114 | NAYY 4x150 SE | 107 | 109 | 0.0085029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
115 | LV_3295-3_1_3_line_115 | NAYY 4x150 SE | 108 | 110 | 0.0086789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
116 | LV_3295-3_1_3_line_116 | NAYY 4x150 SE | 110 | 111 | 0.01099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3295-3_1_3_line_117 | NAYY 4x150 SE | 110 | 112 | 0.010034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
118 | LV_3295-3_1_3_line_118 | NAYY 4x150 SE | 111 | 185 | 0.012199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3295-3_1_3_line_119 | NAYY 4x150 SE | 112 | 182 | 0.016162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
120 | LV_3295-3_1_3_line_120 | NAYY 4x150 SE | 113 | 114 | 0.015349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3295-3_1_3_line_121 | NAYY 4x150 SE | 114 | 115 | 0.023336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3295-3_1_3_line_122 | NAYY 4x150 SE | 115 | 127 | 0.039893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
123 | LV_3295-3_1_3_line_123 | NAYY 4x150 SE | 117 | 178 | 0.0069869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
124 | LV_3295-3_1_3_line_124 | NAYY 4x150 SE | 118 | 119 | 0.0040418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3295-3_1_3_line_125 | NAYY 4x150 SE | 119 | 120 | 0.011383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3295-3_1_3_line_126 | NAYY 4x150 SE | 120 | 121 | 0.005891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3295-3_1_3_line_127 | NAYY 4x150 SE | 121 | 122 | 0.015472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3295-3_1_3_line_128 | NAYY 4x150 SE | 122 | 123 | 0.0059959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3295-3_1_3_line_129 | NAYY 4x150 SE | 123 | 125 | 0.0099633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3295-3_1_3_line_130 | NAYY 4x150 SE | 124 | 125 | 0.012053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3295-3_1_3_line_131 | NAYY 4x150 SE | 124 | 126 | 0.0026696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3295-3_1_3_line_132 | NAYY 4x150 SE | 127 | 128 | 0.028766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
133 | LV_3295-3_1_3_line_133 | NAYY 4x150 SE | 128 | 129 | 0.017304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
134 | LV_3295-3_1_3_line_134 | NAYY 4x150 SE | 129 | 130 | 0.0051418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
135 | LV_3295-3_1_3_line_135 | NAYY 4x150 SE | 130 | 131 | 0.013368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3295-3_1_3_line_136 | NAYY 4x150 SE | 130 | 132 | 0.035459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
137 | LV_3295-3_1_3_line_137 | NAYY 4x150 SE | 132 | 133 | 0.010182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3295-3_1_3_line_138 | NAYY 4x150 SE | 132 | 134 | 0.00058942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
139 | LV_3295-3_1_3_line_139 | NAYY 4x150 SE | 133 | 135 | 0.012528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3295-3_1_3_line_140 | NAYY 4x150 SE | 134 | 136 | 0.027841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
141 | LV_3295-3_1_3_line_141 | NAYY 4x150 SE | 135 | 153 | 0.012264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3295-3_1_3_line_142 | NAYY 4x150 SE | 135 | 151 | 0.021933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3295-3_1_3_line_143 | NAYY 4x150 SE | 136 | 184 | 0.016044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
144 | LV_3295-3_1_3_line_144 | NAYY 4x150 SE | 137 | 138 | 0.025201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3295-3_1_3_line_145 | NAYY 4x150 SE | 137 | 139 | 0.00052213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3295-3_1_3_line_146 | NAYY 4x150 SE | 138 | 140 | 0.020612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3295-3_1_3_line_147 | NAYY 4x150 SE | 140 | 141 | 0.031133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3295-3_1_3_line_148 | NAYY 4x150 SE | 140 | 142 | 0.016901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3295-3_1_3_line_149 | NAYY 4x150 SE | 142 | 143 | 0.022357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
150 | LV_3295-3_1_3_line_150 | NAYY 4x150 SE | 142 | 144 | 0.037048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
151 | LV_3295-3_1_3_line_151 | NAYY 4x150 SE | 143 | 145 | 0.015022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_3295-3_1_3_line_152 | NAYY 4x150 SE | 143 | 146 | 0.0075785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
153 | LV_3295-3_1_3_line_153 | NAYY 4x150 SE | 144 | 147 | 0.011243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
154 | LV_3295-3_1_3_line_154 | NAYY 4x150 SE | 145 | 186 | 0.024521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_3295-3_1_3_line_155 | NAYY 4x150 SE | 146 | 168 | 0.034237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
156 | LV_3295-3_1_3_line_156 | NAYY 4x150 SE | 147 | 176 | 0.011015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
157 | LV_3295-3_1_3_line_157 | NAYY 4x150 SE | 148 | 149 | 0.019082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_3295-3_1_3_line_158 | NAYY 4x150 SE | 148 | 150 | 0.038767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_3295-3_1_3_line_159 | NAYY 4x150 SE | 149 | 151 | 0.003979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_3295-3_1_3_line_160 | NAYY 4x150 SE | 150 | 152 | 0.017382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_3295-3_1_3_line_161 | NAYY 4x150 SE | 153 | 157 | 0.012355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_3295-3_1_3_line_162 | NAYY 4x150 SE | 154 | 155 | 0.0178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_3295-3_1_3_line_163 | NAYY 4x150 SE | 154 | 156 | 0.0078751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_3295-3_1_3_line_164 | NAYY 4x150 SE | 155 | 158 | 0.0069732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_3295-3_1_3_line_165 | NAYY 4x150 SE | 156 | 159 | 0.0011862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_3295-3_1_3_line_166 | NAYY 4x150 SE | 158 | 195 | 0.0095789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_3295-3_1_3_line_167 | NAYY 4x150 SE | 158 | 196 | 0.011838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_3295-3_1_3_line_168 | NAYY 4x150 SE | 159 | 197 | 0.015961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_3295-3_1_3_line_169 | NAYY 4x150 SE | 160 | 161 | 0.003568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
170 | LV_3295-3_1_3_line_170 | NAYY 4x150 SE | 161 | 177 | 0.016058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
171 | LV_3295-3_1_3_line_171 | NAYY 4x150 SE | 162 | 163 | 0.0020634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
172 | LV_3295-3_1_3_line_172 | NAYY 4x150 SE | 162 | 164 | 0.010838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
173 | LV_3295-3_1_3_line_173 | NAYY 4x150 SE | 163 | 165 | 0.017377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
174 | LV_3295-3_1_3_line_174 | NAYY 4x150 SE | 164 | 166 | 0.0054158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
175 | LV_3295-3_1_3_line_175 | NAYY 4x150 SE | 165 | 167 | 0.0084946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
176 | LV_3295-3_1_3_line_176 | NAYY 4x150 SE | 167 | 173 | 0.020486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
177 | LV_3295-3_1_3_line_177 | NAYY 4x150 SE | 168 | 169 | 0.01097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
178 | LV_3295-3_1_3_line_178 | NAYY 4x150 SE | 169 | 172 | 0.015283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
179 | LV_3295-3_1_3_line_179 | NAYY 4x150 SE | 170 | 171 | 0.010889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
180 | LV_3295-3_1_3_line_180 | NAYY 4x150 SE | 170 | 172 | 0.0063121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
181 | LV_3295-3_1_3_line_181 | NAYY 4x150 SE | 171 | 174 | 0.0051404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
182 | LV_3295-3_1_3_line_182 | NAYY 4x150 SE | 173 | 175 | 0.0092086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
183 | LV_3295-3_1_3_line_183 | NAYY 4x150 SE | 173 | 174 | 0.0060423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
184 | LV_3295-3_1_3_line_184 | NAYY 4x150 SE | 175 | 179 | 0.0043558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
185 | LV_3295-3_1_3_line_185 | NAYY 4x150 SE | 176 | 177 | 0.0034903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
186 | LV_3295-3_1_3_line_186 | NAYY 4x150 SE | 178 | 179 | 0.0075296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
187 | LV_3295-3_1_3_line_187 | NAYY 4x150 SE | 180 | 181 | 0.010818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
188 | LV_3295-3_1_3_line_188 | NAYY 4x150 SE | 180 | 182 | 0.015876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
189 | LV_3295-3_1_3_line_189 | NAYY 4x150 SE | 181 | 183 | 0.0063583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
190 | LV_3295-3_1_3_line_190 | NAYY 4x150 SE | 183 | 184 | 0.0091347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
191 | LV_3295-3_1_3_line_191 | NAYY 4x150 SE | 185 | 203 | 0.0014969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
192 | LV_3295-3_1_3_line_192 | NAYY 4x150 SE | 186 | 187 | 0.010649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
193 | LV_3295-3_1_3_line_193 | NAYY 4x150 SE | 187 | 193 | 0.030543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
194 | LV_3295-3_1_3_line_194 | NAYY 4x150 SE | 187 | 190 | 0.002457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
195 | LV_3295-3_1_3_line_195 | NAYY 4x150 SE | 188 | 189 | 0.025013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
196 | LV_3295-3_1_3_line_196 | NAYY 4x150 SE | 189 | 190 | 0.019824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
197 | LV_3295-3_1_3_line_197 | NAYY 4x150 SE | 190 | 191 | 0.044129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
198 | LV_3295-3_1_3_line_198 | NAYY 4x150 SE | 191 | 192 | 0.04726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
199 | LV_3295-3_1_3_line_199 | NAYY 4x150 SE | 193 | 194 | 0.0087416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
200 | LV_3295-3_1_3_line_200 | NAYY 4x150 SE | 194 | 200 | 0.007135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
201 | LV_3295-3_1_3_line_201 | NAYY 4x150 SE | 195 | 198 | 0.0045194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
202 | LV_3295-3_1_3_line_202 | NAYY 4x150 SE | 197 | 199 | 0.0018925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
203 | LV_3295-3_1_3_line_203 | NAYY 4x150 SE | 198 | 205 | 0.014388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
204 | LV_3295-3_1_3_line_204 | NAYY 4x150 SE | 199 | 206 | 0.05335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
205 | LV_3295-3_1_3_line_205 | NAYY 4x150 SE | 200 | 201 | 0.0008352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
206 | LV_3295-3_1_3_line_206 | NAYY 4x150 SE | 202 | 208 | 0.0035574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
207 | LV_3295-3_1_3_line_207 | NAYY 4x150 SE | 203 | 204 | 0.012834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3295-3_1_3_trafo_183 | 0.25 MVA 20/0.4 kV | 209 | 161 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29
0 | 2738221.8083 | 1218203.2145 | 2738226.5398 | 1218204.8356
1 | 2738260.5685 | 1218224.9874 | 2738251.131 | 1218217.4177 | 2738241.8626 | 1218210.0854 | 2738226.5398 | 1218204.8356
2 | 2738221.8083 | 1218203.2145 | 2738217.102 | 1218198.8906 | 2738211.5905 | 1218193.9253 | 2738204.2916 | 1218192.0042
3 | 2738260.5685 | 1218224.9874 | 2738304.4392 | 1218184.6384 | 2738333.5674 | 1218157.8589
4 | 2738163.8425 | 1218137.6487 | 2738175.0384 | 1218144.3917 | 2738184.4046 | 1218154.0615 | 2738191.5692 | 1218168.6175 | 2738195.1026 | 1218187.1594 | 2738201.9525 | 1218191.3885 | 2738204.2916 | 1218192.0042
5 | 2738333.5674 | 1218157.8589 | 2738335.6549 | 1218163.4453 | 2738335.1537 | 1218168.3489 | 2738330.8601 | 1218175.2542
6 | 2738333.5674 | 1218157.8589 | 2738339.6582 | 1218146.7132 | 2738347.8552 | 1218094.2707 | 2738349.5867 | 1218090.0185
7 | 2738163.8425 | 1218137.6487 | 2738166.2896 | 1218129.71 | 2738167.0355 | 1218128.9303
8 | 2738329.7746 | 1218177.0001 | 2738330.8601 | 1218175.2542
9 | 2738349.5867 | 1218090.0185 | 2738352.8204 | 1218083.5326 | 2738357.7668 | 1218078.7492
10 | 2738349.5867 | 1218090.0185 | 2738344.09 | 1218088.99 | 2738340.1984 | 1218090.4565 | 2738338.9135 | 1218091.3096
11 | 2738223.5455 | 1218114.6474 | 2738221.0418 | 1218119.46 | 2738214.7019 | 1218123.0271 | 2738199.4853 | 1218125.276 | 2738191.1645 | 1218124.8716 | 2738182.9653 | 1218122.5017 | 2738176.1305 | 1218122.1985 | 2738170.7022 | 1218125.0973 | 2738167.0355 | 1218128.9303
12 | 2738315.5636 | 1218203.4565 | 2738315.1964 | 1218200.4458 | 2738329.7746 | 1218177.0001
13 | 2738376.2738 | 1218065.4569 | 2738364.7912 | 1218071.9564 | 2738357.7668 | 1218078.7492
14 | 2738330.0742 | 1218099.39 | 2738333.4344 | 1218094.9476 | 2738338.9135 | 1218091.3096
15 | 2738223.5455 | 1218114.6474 | 2738235.2535 | 1218111.7611 | 2738237.9005 | 1218111.5667 | 2738245.1343 | 1218113.0024 | 2738252.4892 | 1218115.4306 | 2738255.1407 | 1218116.6821
16 | 2738223.5455 | 1218114.6474 | 2738224.8653 | 1218105.2257 | 2738224.5784 | 1218100.2482 | 2738222.2777 | 1218096.3138 | 2738222.6758 | 1218087.6714 | 2738223.201 | 1218078.1312 | 2738218.3848 | 1218074.939 | 2738213.3069 | 1218072.9546
17 | 2738167.656 | 1217876.5494 | 2738164.4333 | 1217879.1911 | 2738149.6436 | 1217888.5449 | 2738124.4747 | 1217897.1798 | 2738105.3814 | 1217896.6257 | 2738064.6727 | 1217899.4848 | 2738047.9935 | 1217900.9329 | 2738029.9151 | 1217898.8568 | 2738006.8914 | 1217902.749 | 2737997.2324 | 1217904.3712 | 2737994.9419 | 1217899.3361 | 2738000.0511 | 1217894.4837 | 2738008.7901 | 1217884.7224 | 2738014.2336 | 1217865.121 | 2738023.2256 | 1217860.1696 | 2738038.3057 | 1217856.9018
18 | 2738171.564 | 1217873.346 | 2738167.656 | 1217876.5494
19 | 2738171.564 | 1217873.346 | 2738177.7713 | 1217868.2579 | 2738186.3624 | 1217864.8532
20 | 2738186.3624 | 1217864.8532 | 2738193.1461 | 1217862.1649 | 2738199.0483 | 1217863.0692
21 | 2738202.6509 | 1217866.0669 | 2738199.0483 | 1217863.0692 | 2738199.0483 | 1217863.0692
22 | 2738202.6509 | 1217866.0669 | 2738204.2037 | 1217867.359 | 2738205.4315 | 1217870.815
23 | 2738216.7075 | 1217713.2345 | 2738238.6521 | 1217718.7562 | 2738268.0908 | 1217717.9273 | 2738277.7402 | 1217712.1575 | 2738301.4257 | 1217687.3356
24 | 2738216.7075 | 1217713.2345 | 2738213.0425 | 1217712.3123 | 2738171.6401 | 1217704.757 | 2738126.8606 | 1217705.2861 | 2738098.957 | 1217711.9805
25 | 2738301.4257 | 1217687.3356 | 2738312.3927 | 1217675.8425 | 2738321.6523 | 1217671.8207 | 2738330.7275 | 1217673.1213 | 2738336.9113 | 1217679.2366 | 2738338.6933 | 1217688.8304 | 2738335.4099 | 1217699.4075 | 2738323.871 | 1217709.8738
26 | 2738028.8342 | 1217713.8775 | 2738046.0208 | 1217720.381 | 2738064.6454 | 1217720.2124 | 2738098.957 | 1217711.9805
27 | 2738312.278 | 1217748.1056 | 2738309.569 | 1217742.1545 | 2738309.6731 | 1217733.0938 | 2738311.1824 | 1217724.6774 | 2738317.8855 | 1217715.3029 | 2738323.871 | 1217709.8738
28 | 2737993.6258 | 1217655.6469 | 2738013.2801 | 1217695.5909 | 2738028.8342 | 1217713.8775
29 | 2738315.5237 | 1217755.2355 | 2738312.278 | 1217748.1056
30 | 2737993.6258 | 1217655.6469 | 2737989.3685 | 1217646.9967 | 2737981.8763 | 1217637.026 | 2737970.2931 | 1217630.886 | 2737867.3768 | 1217615.118
31 | 2738340.9268 | 1217811.0399 | 2738315.5237 | 1217755.2355
32 | 2737725.6264 | 1217560.5125 | 2737729.1635 | 1217570.1133 | 2737738.0017 | 1217580.0258 | 2737803.1303 | 1217605.2747 | 2737867.3768 | 1217615.118
33 | 2738340.9268 | 1217811.0399 | 2738347.4208 | 1217825.3693 | 2738349.7503 | 1217838.5233 | 2738347.2619 | 1217852.1435 | 2738346.3393 | 1217853.0421
34 | 2738340.9268 | 1217811.0399 | 2738349.9793 | 1217752.1898 | 2738354.5893 | 1217744.0011 | 2738355.6959 | 1217743.333
35 | 2737725.6264 | 1217560.5125 | 2737721.1594 | 1217563.534 | 2737706.4138 | 1217596.921 | 2737703.5406 | 1217604.9168 | 2737699.68 | 1217607.0861
36 | 2737731.5309 | 1217433.2875 | 2737719.0527 | 1217456.9522 | 2737716.6259 | 1217468.628 | 2737723.8472 | 1217555.6784 | 2737725.6264 | 1217560.5125
37 | 2738376.5667 | 1217733.5227 | 2738393.574 | 1217727.5145
38 | 2738376.5667 | 1217733.5227 | 2738365.4262 | 1217737.4583 | 2738355.6959 | 1217743.333
39 | 2738417.5854 | 1217719.032 | 2738393.574 | 1217727.5145
40 | 2738417.5854 | 1217719.032 | 2738455.4222 | 1217733.6783
41 | 2738417.5854 | 1217719.032 | 2738423.6314 | 1217717.3057
42 | 2738457.7159 | 1217734.5661 | 2738455.4222 | 1217733.6783
43 | 2738442.4614 | 1217711.9294 | 2738423.6314 | 1217717.3057
44 | 2738341.024 | 1217858.2189 | 2738346.3393 | 1217853.0421
45 | 2738457.7159 | 1217734.5661 | 2738450.9959 | 1217744.9854 | 2738441.5039 | 1217748.4834
46 | 2738457.7159 | 1217734.5661 | 2738473.6224 | 1217737.3537
47 | 2738481.8928 | 1217700.6711 | 2738442.4614 | 1217711.9294
48 | 2738336.1434 | 1217862.9722 | 2738341.024 | 1217858.2189
49 | 2738424.3589 | 1217750.082 | 2738438.6485 | 1217749.5357 | 2738441.5039 | 1217748.4834
50 | 2738473.6224 | 1217737.3537 | 2738479.7285 | 1217738.4238
51 | 2738481.8928 | 1217700.6711 | 2738488.5165 | 1217698.7799
52 | 2738336.1434 | 1217862.9722 | 2738336.1434 | 1217862.9722 | 2738329.2795 | 1217865.6346
53 | 2738650.1219 | 1218059.934 | 2738652.0706 | 1218148.4546
54 | 2738604.8321 | 1217891.9843 | 2738620.0697 | 1217933.5513 | 2738613.7819 | 1217984.7701 | 2738617.9531 | 1218024.467 | 2738626.5895 | 1218047.1981 | 2738636.1315 | 1218048.6435 | 2738643.1293 | 1218062.8182 | 2738650.1219 | 1218059.934
55 | 2738604.8321 | 1217891.9843 | 2738602.3923 | 1217875.1135 | 2738603.3044 | 1217864.637 | 2738607.2444 | 1217859.1463 | 2738608.1336 | 1217852.9173 | 2738613.468 | 1217848.2041 | 2738616.6958 | 1217834.8125 | 2738619.9442 | 1217829.6726 | 2738622.8467 | 1217826.9934 | 2738635.9198 | 1217820.3031 | 2738638.0589 | 1217821.3871 | 2738643.9465 | 1217815.4191 | 2738645.9502 | 1217809.5941 | 2738646.1405 | 1217804.6834 | 2738649.2445 | 1217799.5513 | 2738653.5538 | 1217784.0719 | 2738660.396 | 1217773.9671 | 2738665.7566 | 1217765.1956 | 2738667.8873 | 1217757.183 | 2738673.6219 | 1217746.374 | 2738675.6372 | 1217738.4254 | 2738683.6298 | 1217727.8359 | 2738685.9414 | 1217715.6461 | 2738700.2215 | 1217700.1878 | 2738705.6677 | 1217694.9212
56 | 2738604.8321 | 1217891.9843 | 2738599.5513 | 1217894.3969 | 2738596.5459 | 1217898.5638 | 2738593.4212 | 1217901.3268 | 2738578.9668 | 1217896.898 | 2738574.8697 | 1217893.1552 | 2738574.5568 | 1217890.6124 | 2738565.5869 | 1217891.0042 | 2738551.0586 | 1217891.0553 | 2738547.6397 | 1217892.4325 | 2738546.2612 | 1217897.1711 | 2738542.8503 | 1217899.1824 | 2738540.9691 | 1217903.0085 | 2738540.4364 | 1217909.913 | 2738535.2039 | 1217913.5166 | 2738533.3006 | 1217915.0292 | 2738530.4462 | 1217918.9105 | 2738526.4503 | 1217920.6079 | 2738523.9369 | 1217924.6897
57 | 2738705.6677 | 1217694.9212 | 2738721.2585 | 1217681.2282 | 2738725.8551 | 1217683.0923 | 2738723.7323 | 1217692.3952 | 2738727.3042 | 1217710.8604 | 2738724.6592 | 1217719.4282 | 2738754.9717 | 1217751.5052
58 | 2738705.6677 | 1217694.9212 | 2738695.5952 | 1217692.7516 | 2738685.6831 | 1217692.4985 | 2738674.0805 | 1217701.9031 | 2738666.4589 | 1217704.0608 | 2738660.0333 | 1217700.1859 | 2738656.8481 | 1217697.0647 | 2738647.1118 | 1217682.4148 | 2738640.0531 | 1217679.3147 | 2738632.2669 | 1217676.7981 | 2738624.42 | 1217677.2159 | 2738612.4527 | 1217670.6432 | 2738604.7282 | 1217668.7397 | 2738600.6859 | 1217657.414 | 2738602.7896 | 1217644.6856 | 2738598.3429 | 1217628.224 | 2738597.9229 | 1217618.8619 | 2738592.7346 | 1217607.176 | 2738585.8964 | 1217609.9303 | 2738580.9623 | 1217608.8591 | 2738570.2885 | 1217621.099 | 2738570.2774 | 1217626.4699 | 2738551.7637 | 1217639.4836 | 2738537.0178 | 1217655.3874 | 2738533.6872 | 1217657.534 | 2738529.7159 | 1217660.7777 | 2738521.6156 | 1217670.4531 | 2738516.2135 | 1217679.0569 | 2738506.6541 | 1217682.9046 | 2738504.4717 | 1217684.3329
59 | 2738504.4717 | 1217684.3329 | 2738503.4503 | 1217682.8635 | 2738490.0139 | 1217679.8791
60 | 2738504.4717 | 1217684.3329 | 2738507.9622 | 1217689.3515 | 2738500.4558 | 1217695.371 | 2738488.5165 | 1217698.7799
61 | 2738465.1522 | 1217674.9244 | 2738468.6665 | 1217675.1376 | 2738490.0139 | 1217679.8791
62 | 2738378.9163 | 1217669.6934 | 2738377.4146 | 1217669.6023 | 2738365.5762 | 1217665.9688 | 2738364.0339 | 1217660.117 | 2738366.3956 | 1217655.5458 | 2738383.7169 | 1217651.4966
63 | 2738378.9163 | 1217669.6934 | 2738397.9531 | 1217670.8481
64 | 2738392.7462 | 1217649.3858 | 2738383.7169 | 1217651.4966
65 | 2738417.4907 | 1217672.0333 | 2738397.9531 | 1217670.8481
66 | 2738392.7462 | 1217649.3858 | 2738425.9643 | 1217641.6103
67 | 2738392.7462 | 1217649.3858 | 2738392.5011 | 1217634.3145
68 | 2738417.4907 | 1217672.0333 | 2738421.6856 | 1217672.2877
69 | 2738425.9643 | 1217641.6103 | 2738434.1473 | 1217639.6949 | 2738468.779 | 1217631.1206
70 | 2738392.5011 | 1217634.3145 | 2738392.4992 | 1217634.2008
71 | 2738439.5783 | 1217673.3731 | 2738421.6856 | 1217672.2877
72 | 2738488.2354 | 1217626.3035 | 2738468.779 | 1217631.1206
73 | 2738439.5783 | 1217673.3731 | 2738442.2689 | 1217673.5363
74 | 2738509.6764 | 1217622.6643 | 2738498.1171 | 1217623.8569 | 2738488.2354 | 1217626.3035
75 | 2738461.6013 | 1217674.709 | 2738442.2689 | 1217673.5363
76 | 2737787.3149 | 1217449.0627 | 2737798.1731 | 1217448.663 | 2737805.6114 | 1217447.1467
77 | 2737731.5309 | 1217433.2875 | 2737739.0223 | 1217434.128 | 2737752.3043 | 1217440.3958 | 2737764.7635 | 1217447.1005 | 2737778.1372 | 1217449.4004 | 2737787.3149 | 1217449.0627
78 | 2737805.6114 | 1217447.1467 | 2737893.5874 | 1217505.4479
79 | 2737731.5309 | 1217433.2875 | 2737729.618 | 1217424.3803 | 2737722.8721 | 1217416.9182 | 2737714.833 | 1217413.4851 | 2737703.0034 | 1217416.6589 | 2737667.5349 | 1217443.3312
80 | 2737893.8131 | 1217508.2042 | 2737893.5874 | 1217505.4479
81 | 2737684.8361 | 1217615.4268 | 2737699.68 | 1217607.0861
82 | 2738352.2611 | 1217276.1343 | 2738358.8482 | 1217262.2979 | 2738366.8181 | 1217252.686 | 2738378.7213 | 1217248.3365
83 | 2738402.3335 | 1217545.6663 | 2738352.2611 | 1217276.1343
84 | 2738402.3335 | 1217545.6663 | 2738402.8476 | 1217556.8765 | 2738410.505 | 1217568.8644 | 2738420.3222 | 1217574.8418 | 2738438.7208 | 1217583.4319 | 2738463.8559 | 1217599.1957 | 2738489.691 | 1217596.605 | 2738522.0375 | 1217600.4155 | 2738532.1081 | 1217601.6951 | 2738537.3293 | 1217605.4418 | 2738539.3844 | 1217610.138 | 2738537.9093 | 1217616.7425 | 2738531.6274 | 1217620.3995 | 2738509.6764 | 1217622.6643
85 | 2738214.6895 | 1218003.3609 | 2738213.0395 | 1218004.5795
86 | 2738236.1761 | 1217995.3311 | 2738230.8302 | 1217993.8488 | 2738226.3981 | 1217994.7134 | 2738214.6895 | 1218003.3609
87 | 2738205.6688 | 1218010.0232 | 2738213.0395 | 1218004.5795
88 | 2738236.1761 | 1217995.3311 | 2738237.2209 | 1217995.6208 | 2738243.7028 | 1217998.0324
89 | 2738205.6688 | 1218010.0232 | 2738196.878 | 1217996.1901
90 | 2738205.6688 | 1218010.0232 | 2738200.7135 | 1218014.4564 | 2738199.3441 | 1218018.8172
91 | 2738252.8731 | 1218001.4443 | 2738243.7028 | 1217998.0324
92 | 2738196.878 | 1217996.1901 | 2738195.0532 | 1217993.3186
93 | 2738200.0172 | 1218020.5191 | 2738199.3441 | 1218018.8172
94 | 2738252.8731 | 1218001.4443 | 2738260.7633 | 1218002.8527
95 | 2738196.5404 | 1217986.0882 | 2738195.0532 | 1217993.3186 | 2738195.0532 | 1217993.3186
96 | 2738268.7614 | 1218004.2804 | 2738260.7633 | 1218002.8527
97 | 2738196.5404 | 1217986.0882 | 2738196.817 | 1217984.7435
98 | 2738268.7614 | 1218004.2804 | 2738276.6492 | 1218005.6884 | 2738282.8347 | 1218005.3175
99 | 2738329.2795 | 1217865.6346 | 2738316.0391 | 1217870.7702
100 | 2738289.4793 | 1218109.8083 | 2738288.0662 | 1218109.4329
101 | 2738289.4793 | 1218109.8083 | 2738296.445 | 1218111.6586 | 2738299.3914 | 1218111.6367
102 | 2738288.0662 | 1218109.4329 | 2738280.7095 | 1218107.4788 | 2738270.0781 | 1218097.357 | 2738268.0436 | 1218092.9992
103 | 2738304.3255 | 1218111.6 | 2738299.3914 | 1218111.6367
104 | 2738268.0436 | 1218092.9992 | 2738267.3765 | 1218091.5702
105 | 2738330.0742 | 1218099.39 | 2738325.6393 | 1218105.2531 | 2738313.488 | 1218111.5318 | 2738304.3255 | 1218111.6
106 | 2738262.8298 | 1218081.8314 | 2738267.3765 | 1218091.5702
107 | 2738262.8298 | 1218081.8314 | 2738262.8298 | 1218081.8314 | 2738263.3537 | 1218066.9908
108 | 2738263.3537 | 1218066.9908 | 2738263.4068 | 1218065.4867 | 2738266.3605 | 1218061.9237
109 | 2738314.3491 | 1218002.1982 | 2738308.3939 | 1218003.3055
110 | 2738300.0401 | 1218004.2858 | 2738304.5875 | 1218004.0132 | 2738308.3939 | 1218003.3055
111 | 2738314.3491 | 1218002.1982 | 2738316.0247 | 1218001.8867
112 | 2738300.0401 | 1218004.2858 | 2738291.3224 | 1218004.8086
113 | 2738322.0008 | 1218000.7756 | 2738316.0247 | 1218001.8867
114 | 2738282.8347 | 1218005.3175 | 2738291.3224 | 1218004.8086
115 | 2738330.5335 | 1217999.1892 | 2738322.0008 | 1218000.7756
116 | 2738330.5335 | 1217999.1892 | 2738338.6927 | 1218006.5514
117 | 2738330.5335 | 1217999.1892 | 2738339.8431 | 1217995.4459
118 | 2738350.7946 | 1218008.0905 | 2738338.6927 | 1218006.5514 | 2738338.6927 | 1218006.5514
119 | 2738339.8431 | 1217995.4459 | 2738354.8385 | 1217989.4165
120 | 2738389.6318 | 1218057.8959 | 2738376.2738 | 1218065.4569
121 | 2738389.6318 | 1218057.8959 | 2738409.9401 | 1218046.4007
122 | 2738444.6572 | 1218026.7497 | 2738409.9401 | 1218046.4007
123 | 2738196.817 | 1217984.7435 | 2738198.2246 | 1217977.8998
124 | 2738330.449 | 1218052.2073 | 2738326.4195 | 1218051.8932
125 | 2738326.4195 | 1218051.8932 | 2738315.071 | 1218051.0087
126 | 2738309.1856 | 1218051.0387 | 2738313.8179 | 1218050.911 | 2738315.071 | 1218051.0087
127 | 2738309.1856 | 1218051.0387 | 2738293.7193 | 1218051.4649
128 | 2738293.7193 | 1218051.4649 | 2738287.7257 | 1218051.6301
129 | 2738278.1359 | 1218054.1563 | 2738286.2277 | 1218051.6713 | 2738287.7257 | 1218051.6301
130 | 2738268.0642 | 1218059.8685 | 2738270.9771 | 1218056.3547 | 2738278.1359 | 1218054.1563
131 | 2738268.0642 | 1218059.8685 | 2738266.3605 | 1218061.9237
132 | 2738444.6572 | 1218026.7497 | 2738456.0147 | 1218020.321 | 2738467.9912 | 1218010.1463
133 | 2738469.9535 | 1217993.4333 | 2738471.2106 | 1217997.7552 | 2738467.9912 | 1218010.1463 | 2738467.9912 | 1218010.1463
134 | 2738468.5175 | 1217988.496 | 2738469.9535 | 1217993.4333
135 | 2738468.5175 | 1217988.496 | 2738476.8268 | 1217983.8519 | 2738479.3974 | 1217980.9879
136 | 2738468.5175 | 1217988.496 | 2738459.1367 | 1217981.0941 | 2738436.3372 | 1217975.0148
137 | 2738436.3372 | 1217975.0148 | 2738438.3567 | 1217965.0353
138 | 2738435.7677 | 1217974.863 | 2738436.3372 | 1217975.0148
139 | 2738440.8415 | 1217952.7564 | 2738438.3567 | 1217965.0353
140 | 2738408.8661 | 1217967.6928 | 2738435.7677 | 1217974.863
141 | 2738440.8415 | 1217952.7564 | 2738453.0475 | 1217953.9488
142 | 2738440.8415 | 1217952.7564 | 2738436.0097 | 1217931.3622
143 | 2738408.8661 | 1217967.6928 | 2738393.9803 | 1217973.6782
144 | 2738218.8911 | 1217892.1499 | 2738215 | 1217889.0497 | 2738208.4022 | 1217879.1773 | 2738205.6063 | 1217871.307
145 | 2738205.4315 | 1217870.815 | 2738205.6063 | 1217871.307
146 | 2738235.0117 | 1217904.9939 | 2738218.8911 | 1217892.1499
147 | 2738252.6253 | 1217879.3366 | 2738241.6839 | 1217893.995 | 2738235.0117 | 1217904.9939
148 | 2738249.818 | 1217911.6095 | 2738245.2097 | 1217911.2356 | 2738242.5869 | 1217911.0302 | 2738238.9634 | 1217908.1437 | 2738235.0117 | 1217904.9939
149 | 2738249.818 | 1217911.6095 | 2738252.9227 | 1217920.1665 | 2738263.0977 | 1217928.6986
150 | 2738249.818 | 1217911.6095 | 2738251.7896 | 1217901.5913 | 2738261.3762 | 1217891.9724 | 2738273.736 | 1217887.1784
151 | 2738263.0977 | 1217928.6986 | 2738266.6071 | 1217929.6363 | 2738277.6937 | 1217932.2441
152 | 2738263.0977 | 1217928.6986 | 2738255.5551 | 1217929.4353
153 | 2738284.2177 | 1217883.1128 | 2738273.736 | 1217887.1784
154 | 2738301.5634 | 1217937.8586 | 2738277.6937 | 1217932.2441
155 | 2738229.5656 | 1217928.932 | 2738239.5555 | 1217935.6248 | 2738241.7921 | 1217927.6034 | 2738255.5551 | 1217929.4353
156 | 2738284.2177 | 1217883.1128 | 2738294.4875 | 1217879.1294
157 | 2738423.6042 | 1217912.0914 | 2738423.7168 | 1217912.9365 | 2738434.0492 | 1217927.9551
158 | 2738437.8255 | 1217889.5678 | 2738435.4681 | 1217894.8165 | 2738421.1436 | 1217893.6161 | 2738423.6042 | 1217912.0914
159 | 2738436.0097 | 1217931.3622 | 2738435.8223 | 1217930.5324 | 2738434.0492 | 1217927.9551
160 | 2738437.8255 | 1217889.5678 | 2738444.9472 | 1217873.7118
161 | 2738465.3442 | 1217955.15 | 2738453.0475 | 1217953.9488
162 | 2738447.428 | 1217794.8997 | 2738442.3235 | 1217797.8948 | 2738431.232 | 1217802.1569
163 | 2738447.428 | 1217794.8997 | 2738452.9448 | 1217789.28
164 | 2738424.7228 | 1217804.6582 | 2738431.232 | 1217802.1569
165 | 2738453.7758 | 1217788.4335 | 2738452.9448 | 1217789.28
166 | 2738424.7228 | 1217804.6582 | 2738419.1611 | 1217796.8594
167 | 2738424.7228 | 1217804.6582 | 2738413.6716 | 1217808.9009
168 | 2738453.7758 | 1217788.4335 | 2738464.4624 | 1217777.5477 | 2738464.9081 | 1217777
169 | 2738312.7126 | 1217872.0604 | 2738316.0391 | 1217870.7702
170 | 2738312.7126 | 1217872.0604 | 2738297.7416 | 1217877.8673
171 | 2738191.334 | 1217922.6002 | 2738192.1359 | 1217920.699
172 | 2738196.3478 | 1217910.713 | 2738192.1359 | 1217920.699
173 | 2738191.334 | 1217922.6002 | 2738188.7859 | 1217928.6415 | 2738186.3672 | 1217939.1885
174 | 2738196.3478 | 1217910.713 | 2738191.0478 | 1217909.5985
175 | 2738184.4685 | 1217947.4682 | 2738186.3672 | 1217939.1885
176 | 2738202.4744 | 1217957.2383 | 2738184.4685 | 1217947.4682
177 | 2738229.5656 | 1217928.932 | 2738223.6624 | 1217938.1787
178 | 2738212.7094 | 1217939.0428 | 2738220.1564 | 1217943.6705 | 2738223.6624 | 1217938.1787
179 | 2738207.3481 | 1217935.7112 | 2738204.9437 | 1217946.3317
180 | 2738207.3481 | 1217935.7112 | 2738212.7094 | 1217939.0428
181 | 2738204.9437 | 1217946.3317 | 2738203.8086 | 1217951.3452
182 | 2738202.4744 | 1217957.2383 | 2738200.6192 | 1217966.2581
183 | 2738202.4744 | 1217957.2383 | 2738203.8086 | 1217951.3452
184 | 2738200.6192 | 1217966.2581 | 2738199.7416 | 1217970.5246
185 | 2738297.7416 | 1217877.8673 | 2738294.4875 | 1217879.1294
186 | 2738199.7416 | 1217970.5246 | 2738198.2246 | 1217977.8998
187 | 2738379.6057 | 1217979.458 | 2738369.5685 | 1217983.4938
188 | 2738354.8385 | 1217989.4165 | 2738369.5685 | 1217983.4938
189 | 2738385.5051 | 1217977.0859 | 2738379.6057 | 1217979.458
190 | 2738385.5051 | 1217977.0859 | 2738393.9803 | 1217973.6782
191 | 2738350.7946 | 1218008.0905 | 2738352.2795 | 1218008.2794
192 | 2738311.93 | 1217940.297 | 2738301.5634 | 1217937.8586
193 | 2738311.93 | 1217940.297 | 2738302.4917 | 1217943.8587 | 2738289.5075 | 1217946.7487 | 2738285.9612 | 1217952.9605 | 2738285.9612 | 1217952.9605
194 | 2738311.93 | 1217940.297 | 2738314.3491 | 1217940.7647
195 | 2738328.5039 | 1217929.5168 | 2738353.1673 | 1217925.3506
196 | 2738314.3491 | 1217940.7647 | 2738320.3421 | 1217930.8955 | 2738328.5039 | 1217929.5168
197 | 2738314.3491 | 1217940.7647 | 2738357.0365 | 1217952.4209
198 | 2738403.1467 | 1217947.8212 | 2738397.6383 | 1217950.8847 | 2738364.053 | 1217949.815 | 2738357.0365 | 1217952.4209
199 | 2738285.9612 | 1217952.9605 | 2738277.2201 | 1217953.0599
200 | 2738277.2201 | 1217953.0599 | 2738270.0856 | 1217953.1411
201 | 2738416.537 | 1217793.1798 | 2738419.1611 | 1217796.8594
202 | 2738466.1027 | 1217775.5321 | 2738464.9081 | 1217777
203 | 2738408.1831 | 1217781.4658 | 2738416.537 | 1217793.1798
204 | 2738466.1027 | 1217775.5321 | 2738490.1583 | 1217745.974 | 2738488.6648 | 1217739.9898 | 2738479.7285 | 1217738.4238
205 | 2738269.2504 | 1217953.1506 | 2738270.0856 | 1217953.1411
206 | 2738461.6013 | 1217674.709 | 2738465.1522 | 1217674.9244
207 | 2738365.0108 | 1218009.8985 | 2738352.2795 | 1218008.2794

## bus_geodata
| x | y | coords
0 | 2738226.5398 | 1218204.8356
1 | 2738221.8083 | 1218203.2145
2 | 2738260.5685 | 1218224.9874
3 | 2738204.2916 | 1218192.0042
4 | 2738333.5674 | 1218157.8589
5 | 2738163.8425 | 1218137.6487
6 | 2738330.8601 | 1218175.2542
7 | 2738349.5867 | 1218090.0185
8 | 2738167.0355 | 1218128.9303
9 | 2738329.7746 | 1218177.0001
10 | 2738357.7668 | 1218078.7492
11 | 2738338.9135 | 1218091.3096
12 | 2738223.5455 | 1218114.6474
13 | 2738213.3069 | 1218072.9546
14 | 2738255.1407 | 1218116.6821
15 | 2738038.3057 | 1217856.9018
16 | 2738167.656 | 1217876.5494
17 | 2738171.564 | 1217873.346
18 | 2738186.3624 | 1217864.8532
19 | 2738199.0483 | 1217863.0692
20 | 2738202.6509 | 1217866.0669
21 | 2738216.7075 | 1217713.2345
22 | 2738301.4257 | 1217687.3356
23 | 2738098.957 | 1217711.9805
24 | 2738323.871 | 1217709.8738
25 | 2738028.8342 | 1217713.8775
26 | 2738312.278 | 1217748.1056
27 | 2737993.6258 | 1217655.6469
28 | 2738315.5237 | 1217755.2355
29 | 2737867.3768 | 1217615.118
30 | 2738340.9268 | 1217811.0399
31 | 2737725.6264 | 1217560.5125
32 | 2738376.5667 | 1217733.5227
33 | 2738393.574 | 1217727.5145
34 | 2738355.6959 | 1217743.333
35 | 2738417.5854 | 1217719.032
36 | 2738455.4222 | 1217733.6783
37 | 2738423.6314 | 1217717.3057
38 | 2738346.3393 | 1217853.0421
39 | 2738457.7159 | 1217734.5661
40 | 2738442.4614 | 1217711.9294
41 | 2738341.024 | 1217858.2189
42 | 2738441.5039 | 1217748.4834
43 | 2738473.6224 | 1217737.3537
44 | 2738481.8928 | 1217700.6711
45 | 2738336.1434 | 1217862.9722
46 | 2738652.0706 | 1218148.4546
47 | 2738650.1219 | 1218059.934
48 | 2738604.8321 | 1217891.9843
49 | 2738705.6677 | 1217694.9212
50 | 2738523.9369 | 1217924.6897
51 | 2738754.9717 | 1217751.5052
52 | 2738504.4717 | 1217684.3329
53 | 2738490.0139 | 1217679.8791
54 | 2738488.5165 | 1217698.7799
55 | 2738378.9163 | 1217669.6934
56 | 2738383.7169 | 1217651.4966
57 | 2738397.9531 | 1217670.8481
58 | 2738392.7462 | 1217649.3858
59 | 2738417.4907 | 1217672.0333
60 | 2738425.9643 | 1217641.6103
61 | 2738392.5011 | 1217634.3145
62 | 2738421.6856 | 1217672.2877
63 | 2738468.779 | 1217631.1206
64 | 2738392.4992 | 1217634.2008
65 | 2738439.5783 | 1217673.3731
66 | 2738488.2354 | 1217626.3035
67 | 2738442.2689 | 1217673.5363
68 | 2737787.3149 | 1217449.0627
69 | 2737805.6114 | 1217447.1467
70 | 2737731.5309 | 1217433.2875
71 | 2737893.5874 | 1217505.4479
72 | 2737667.5349 | 1217443.3312
73 | 2737893.8131 | 1217508.2042
74 | 2737699.68 | 1217607.0861
75 | 2737684.8361 | 1217615.4268
76 | 2738352.2611 | 1217276.1343
77 | 2738378.7213 | 1217248.3365
78 | 2738402.3335 | 1217545.6663
79 | 2738509.6764 | 1217622.6643
80 | 2738214.6895 | 1218003.3609
81 | 2738213.0395 | 1218004.5795
82 | 2738236.1761 | 1217995.3311
83 | 2738205.6688 | 1218010.0232
84 | 2738243.7028 | 1217998.0324
85 | 2738196.878 | 1217996.1901
86 | 2738199.3441 | 1218018.8172
87 | 2738252.8731 | 1218001.4443
88 | 2738195.0532 | 1217993.3186
89 | 2738200.0172 | 1218020.5191
90 | 2738260.7633 | 1218002.8527
91 | 2738196.5404 | 1217986.0882
92 | 2738268.7614 | 1218004.2804
93 | 2738329.2795 | 1217865.6346
94 | 2738289.4793 | 1218109.8083
95 | 2738288.0662 | 1218109.4329
96 | 2738299.3914 | 1218111.6367
97 | 2738268.0436 | 1218092.9992
98 | 2738304.3255 | 1218111.6
99 | 2738267.3765 | 1218091.5702
100 | 2738330.0742 | 1218099.39
101 | 2738262.8298 | 1218081.8314
102 | 2738263.3537 | 1218066.9908
103 | 2738308.3939 | 1218003.3055
104 | 2738314.3491 | 1218002.1982
105 | 2738300.0401 | 1218004.2858
106 | 2738316.0247 | 1218001.8867
107 | 2738291.3224 | 1218004.8086
108 | 2738322.0008 | 1218000.7756
109 | 2738282.8347 | 1218005.3175
110 | 2738330.5335 | 1217999.1892
111 | 2738338.6928 | 1218006.5514
112 | 2738339.8431 | 1217995.4459
113 | 2738376.2738 | 1218065.4569
114 | 2738389.6318 | 1218057.8959
115 | 2738409.9401 | 1218046.4007
116 | 2738315.5636 | 1218203.4565
117 | 2738196.817 | 1217984.7435
118 | 2738330.449 | 1218052.2073
119 | 2738326.4195 | 1218051.8932
120 | 2738315.071 | 1218051.0087
121 | 2738309.1856 | 1218051.0387
122 | 2738293.7193 | 1218051.4649
123 | 2738287.7257 | 1218051.6301
124 | 2738268.0642 | 1218059.8685
125 | 2738278.1359 | 1218054.1563
126 | 2738266.3605 | 1218061.9237
127 | 2738444.6572 | 1218026.7497
128 | 2738467.9912 | 1218010.1463
129 | 2738469.9535 | 1217993.4333
130 | 2738468.5175 | 1217988.496
131 | 2738479.3974 | 1217980.9879
132 | 2738436.3372 | 1217975.0148
133 | 2738438.3567 | 1217965.0353
134 | 2738435.7677 | 1217974.863
135 | 2738440.8415 | 1217952.7564
136 | 2738408.8661 | 1217967.6928
137 | 2738205.6063 | 1217871.307
138 | 2738218.8911 | 1217892.1499
139 | 2738205.4315 | 1217870.815
140 | 2738235.0117 | 1217904.9939
141 | 2738252.6253 | 1217879.3366
142 | 2738249.818 | 1217911.6095
143 | 2738263.0977 | 1217928.6986
144 | 2738273.736 | 1217887.1784
145 | 2738277.6937 | 1217932.2441
146 | 2738255.5551 | 1217929.4353
147 | 2738284.2177 | 1217883.1128
148 | 2738423.6042 | 1217912.0914
149 | 2738434.0492 | 1217927.9551
150 | 2738437.8255 | 1217889.5678
151 | 2738436.0097 | 1217931.3622
152 | 2738444.9472 | 1217873.7118
153 | 2738453.0475 | 1217953.9488
154 | 2738447.428 | 1217794.8997
155 | 2738431.232 | 1217802.1569
156 | 2738452.9448 | 1217789.28
157 | 2738465.3442 | 1217955.15
158 | 2738424.7228 | 1217804.6582
159 | 2738453.7758 | 1217788.4335
160 | 2738316.0391 | 1217870.7702
161 | 2738312.7126 | 1217872.0604
162 | 2738192.1359 | 1217920.699
163 | 2738191.334 | 1217922.6002
164 | 2738196.3478 | 1217910.713
165 | 2738186.3672 | 1217939.1885
166 | 2738191.0478 | 1217909.5985
167 | 2738184.4685 | 1217947.4682
168 | 2738229.5656 | 1217928.932
169 | 2738223.6624 | 1217938.1787
170 | 2738207.3481 | 1217935.7112
171 | 2738204.9437 | 1217946.3317
172 | 2738212.7094 | 1217939.0428
173 | 2738202.4744 | 1217957.2383
174 | 2738203.8086 | 1217951.3452
175 | 2738200.6192 | 1217966.2581
176 | 2738294.4875 | 1217879.1295
177 | 2738297.7416 | 1217877.8673
178 | 2738198.2246 | 1217977.8998
179 | 2738199.7416 | 1217970.5246
180 | 2738369.5685 | 1217983.4938
181 | 2738379.6057 | 1217979.458
182 | 2738354.8385 | 1217989.4165
183 | 2738385.5051 | 1217977.0859
184 | 2738393.9803 | 1217973.6782
185 | 2738350.7946 | 1218008.0905
186 | 2738301.5634 | 1217937.8586
187 | 2738311.93 | 1217940.297
188 | 2738353.1673 | 1217925.3506
189 | 2738328.5039 | 1217929.5168
190 | 2738314.3491 | 1217940.7647
191 | 2738357.0365 | 1217952.4209
192 | 2738403.1467 | 1217947.8212
193 | 2738285.9612 | 1217952.9605
194 | 2738277.2201 | 1217953.0599
195 | 2738419.1611 | 1217796.8594
196 | 2738413.6716 | 1217808.9009
197 | 2738464.9081 | 1217777
198 | 2738416.537 | 1217793.1798
199 | 2738466.1027 | 1217775.5321
200 | 2738270.0856 | 1217953.1411
201 | 2738269.2504 | 1217953.1506
202 | 2738465.1522 | 1217674.9244
203 | 2738352.2795 | 1218008.2794
204 | 2738365.0108 | 1218009.8985
205 | 2738408.1831 | 1217781.4658
206 | 2738479.7285 | 1217738.4238
207 | 2738424.3589 | 1217750.082
208 | 2738461.6013 | 1217674.709
209 | 2738312.7126 | 1217872.0604

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1