## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3295-6_1_2_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_3295-6_1_2_node_37 | 0.4 | n |  | TRUE
2 | bus_LV_3295-6_1_2_node_137 | 0.4 | n |  | TRUE
3 | bus_LV_3295-6_1_2_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_3295-6_1_2_node_34 | 0.4 | n |  | TRUE
5 | bus_LV_3295-6_1_2_node_156 | 0.4 | n |  | TRUE
6 | bus_LV_3295-6_1_2_node_157 | 0.4 | n |  | TRUE
7 | bus_LV_3295-6_1_2_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_3295-6_1_2_node_136 | 0.4 | n |  | TRUE
9 | bus_LV_3295-6_1_2_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_3295-6_1_2_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_3295-6_1_2_node_154 | 0.4 | n |  | TRUE
12 | bus_LV_3295-6_1_2_node_212 | 0.4 | n |  | TRUE
13 | bus_LV_3295-6_1_2_node_213 | 0.4 | n |  | TRUE
14 | bus_LV_3295-6_1_2_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_3295-6_1_2_node_102 | 0.4 | n |  | TRUE
16 | bus_LV_3295-6_1_2_node_44 | 0.4 | n |  | TRUE
17 | bus_LV_3295-6_1_2_node_251 | 0.4 | n |  | TRUE
18 | bus_LV_3295-6_1_2_node_54 | 0.4 | n |  | TRUE
19 | bus_LV_3295-6_1_2_node_55 | 0.4 | n |  | TRUE
20 | bus_LV_3295-6_1_2_node_56 | 0.4 | n |  | TRUE
21 | bus_LV_3295-6_1_2_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_3295-6_1_2_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_3295-6_1_2_node_167 | 0.4 | n |  | TRUE
24 | bus_LV_3295-6_1_2_node_165 | 0.4 | n |  | TRUE
25 | bus_LV_3295-6_1_2_node_240 | 0.4 | n |  | TRUE
26 | bus_LV_3295-6_1_2_node_246 | 0.4 | n |  | TRUE
27 | bus_LV_3295-6_1_2_node_60 | 0.4 | n |  | TRUE
28 | bus_LV_3295-6_1_2_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_3295-6_1_2_node_218 | 0.4 | n |  | TRUE
30 | bus_LV_3295-6_1_2_node_166 | 0.4 | n |  | TRUE
31 | bus_LV_3295-6_1_2_node_241 | 0.4 | n |  | TRUE
32 | bus_LV_3295-6_1_2_node_62 | 0.4 | n |  | TRUE
33 | bus_LV_3295-6_1_2_node_63 | 0.4 | n |  | TRUE
34 | bus_LV_3295-6_1_2_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_3295-6_1_2_node_65 | 0.4 | n |  | TRUE
36 | bus_LV_3295-6_1_2_node_78 | 0.4 | n |  | TRUE
37 | bus_LV_3295-6_1_2_node_79 | 0.4 | n |  | TRUE
38 | bus_LV_3295-6_1_2_node_66 | 0.4 | n |  | TRUE
39 | bus_LV_3295-6_1_2_node_67 | 0.4 | n |  | TRUE
40 | bus_LV_3295-6_1_2_node_68 | 0.4 | n |  | TRUE
41 | bus_LV_3295-6_1_2_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_3295-6_1_2_node_70 | 0.4 | n |  | TRUE
43 | bus_LV_3295-6_1_2_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_3295-6_1_2_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_3295-6_1_2_node_77 | 0.4 | n |  | TRUE
46 | bus_LV_3295-6_1_2_node_73 | 0.4 | n |  | TRUE
47 | bus_LV_3295-6_1_2_node_169 | 0.4 | n |  | TRUE
48 | bus_LV_3295-6_1_2_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_3295-6_1_2_node_72 | 0.4 | n |  | TRUE
50 | bus_LV_3295-6_1_2_node_74 | 0.4 | n |  | TRUE
51 | bus_LV_3295-6_1_2_node_115 | 0.4 | n |  | TRUE
52 | bus_LV_3295-6_1_2_node_80 | 0.4 | n |  | TRUE
53 | bus_LV_3295-6_1_2_node_81 | 0.4 | n |  | TRUE
54 | bus_LV_3295-6_1_2_node_82 | 0.4 | n |  | TRUE
55 | bus_LV_3295-6_1_2_node_126 | 0.4 | n |  | TRUE
56 | bus_LV_3295-6_1_2_node_122 | 0.4 | n |  | TRUE
57 | bus_LV_3295-6_1_2_node_83 | 0.4 | n |  | TRUE
58 | bus_LV_3295-6_1_2_node_161 | 0.4 | n |  | TRUE
59 | bus_LV_3295-6_1_2_node_123 | 0.4 | n |  | TRUE
60 | bus_LV_3295-6_1_2_node_84 | 0.4 | n |  | TRUE
61 | bus_LV_3295-6_1_2_node_85 | 0.4 | n |  | TRUE
62 | bus_LV_3295-6_1_2_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_3295-6_1_2_node_87 | 0.4 | n |  | TRUE
64 | bus_LV_3295-6_1_2_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_3295-6_1_2_node_89 | 0.4 | n |  | TRUE
66 | bus_LV_3295-6_1_2_node_90 | 0.4 | n |  | TRUE
67 | bus_LV_3295-6_1_2_node_91 | 0.4 | n |  | TRUE
68 | bus_LV_3295-6_1_2_node_92 | 0.4 | n |  | TRUE
69 | bus_LV_3295-6_1_2_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_3295-6_1_2_node_97 | 0.4 | n |  | TRUE
71 | bus_LV_3295-6_1_2_node_93 | 0.4 | n |  | TRUE
72 | bus_LV_3295-6_1_2_node_158 | 0.4 | n |  | TRUE
73 | bus_LV_3295-6_1_2_node_145 | 0.4 | n |  | TRUE
74 | bus_LV_3295-6_1_2_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_3295-6_1_2_node_94 | 0.4 | n |  | TRUE
76 | bus_LV_3295-6_1_2_node_159 | 0.4 | n |  | TRUE
77 | bus_LV_3295-6_1_2_node_95 | 0.4 | n |  | TRUE
78 | bus_LV_3295-6_1_2_node_96 | 0.4 | n |  | TRUE
79 | bus_LV_3295-6_1_2_node_130 | 0.4 | n |  | TRUE
80 | bus_LV_3295-6_1_2_node_127 | 0.4 | n |  | TRUE
81 | bus_LV_3295-6_1_2_node_106 | 0.4 | n |  | TRUE
82 | bus_LV_3295-6_1_2_node_140 | 0.4 | n |  | TRUE
83 | bus_LV_3295-6_1_2_node_128 | 0.4 | n |  | TRUE
84 | bus_LV_3295-6_1_2_node_105 | 0.4 | n |  | TRUE
85 | bus_LV_3295-6_1_2_node_99 | 0.4 | n |  | TRUE
86 | bus_LV_3295-6_1_2_node_101 | 0.4 | n |  | TRUE
87 | bus_LV_3295-6_1_2_node_162 | 0.4 | n |  | TRUE
88 | bus_LV_3295-6_1_2_node_143 | 0.4 | n |  | TRUE
89 | bus_LV_3295-6_1_2_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_3295-6_1_2_node_103 | 0.4 | n |  | TRUE
91 | bus_LV_3295-6_1_2_node_104 | 0.4 | n |  | TRUE
92 | bus_LV_3295-6_1_2_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_3295-6_1_2_node_172 | 0.4 | n |  | TRUE
94 | bus_LV_3295-6_1_2_node_108 | 0.4 | n |  | TRUE
95 | bus_LV_3295-6_1_2_node_109 | 0.4 | n |  | TRUE
96 | bus_LV_3295-6_1_2_node_110 | 0.4 | n |  | TRUE
97 | bus_LV_3295-6_1_2_node_111 | 0.4 | n |  | TRUE
98 | bus_LV_3295-6_1_2_node_116 | 0.4 | n |  | TRUE
99 | bus_LV_3295-6_1_2_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_3295-6_1_2_node_113 | 0.4 | n |  | TRUE
101 | bus_LV_3295-6_1_2_node_114 | 0.4 | n |  | TRUE
102 | bus_LV_3295-6_1_2_node_120 | 0.4 | n |  | TRUE
103 | bus_LV_3295-6_1_2_node_168 | 0.4 | n |  | TRUE
104 | bus_LV_3295-6_1_2_node_118 | 0.4 | n |  | TRUE
105 | bus_LV_3295-6_1_2_node_173 | 0.4 | n |  | TRUE
106 | bus_LV_3295-6_1_2_node_125 | 0.4 | n |  | TRUE
107 | bus_LV_3295-6_1_2_node_119 | 0.4 | n |  | TRUE
108 | bus_LV_3295-6_1_2_node_121 | 0.4 | n |  | TRUE
109 | bus_LV_3295-6_1_2_node_142 | 0.4 | n |  | TRUE
110 | bus_LV_3295-6_1_2_node_124 | 0.4 | n |  | TRUE
111 | bus_LV_3295-6_1_2_node_171 | 0.4 | n |  | TRUE
112 | bus_LV_3295-6_1_2_node_170 | 0.4 | n |  | TRUE
113 | bus_LV_3295-6_1_2_node_153 | 0.4 | n |  | TRUE
114 | bus_LV_3295-6_1_2_node_244 | 0.4 | n |  | TRUE
115 | bus_LV_3295-6_1_2_node_151 | 0.4 | n |  | TRUE
116 | bus_LV_3295-6_1_2_node_152 | 0.4 | n |  | TRUE
117 | bus_LV_3295-6_1_2_node_129 | 0.4 | n |  | TRUE
118 | bus_LV_3295-6_1_2_node_138 | 0.4 | n |  | TRUE
119 | bus_LV_3295-6_1_2_node_131 | 0.4 | n |  | TRUE
120 | bus_LV_3295-6_1_2_node_132 | 0.4 | n |  | TRUE
121 | bus_LV_3295-6_1_2_node_133 | 0.4 | n |  | TRUE
122 | bus_LV_3295-6_1_2_node_134 | 0.4 | n |  | TRUE
123 | bus_LV_3295-6_1_2_node_135 | 0.4 | n |  | TRUE
124 | bus_LV_3295-6_1_2_node_160 | 0.4 | n |  | TRUE
125 | bus_LV_3295-6_1_2_node_139 | 0.4 | n |  | TRUE
126 | bus_LV_3295-6_1_2_node_141 | 0.4 | n |  | TRUE
127 | bus_LV_3295-6_1_2_node_144 | 0.4 | n |  | TRUE
128 | bus_LV_3295-6_1_2_node_146 | 0.4 | n |  | TRUE
129 | bus_LV_3295-6_1_2_node_155 | 0.4 | n |  | TRUE
130 | bus_LV_3295-6_1_2_node_147 | 0.4 | n |  | TRUE
131 | bus_LV_3295-6_1_2_node_148 | 0.4 | n |  | TRUE
132 | bus_LV_3295-6_1_2_node_149 | 0.4 | n |  | TRUE
133 | bus_LV_3295-6_1_2_node_150 | 0.4 | n |  | TRUE
134 | bus_LV_3295-6_1_2_node_163 | 0.4 | n |  | TRUE
135 | bus_LV_3295-6_1_2_node_245 | 0.4 | n |  | TRUE
136 | bus_LV_3295-6_1_2_node_164 | 0.4 | n |  | TRUE
137 | bus_LV_3295-6_1_2_node_217 | 0.4 | n |  | TRUE
138 | bus_LV_3295-6_1_2_node_174 | 0.4 | n |  | TRUE
139 | bus_LV_3295-6_1_2_node_214 | 0.4 | n |  | TRUE
140 | bus_MV_152_0_node_139 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3295-6_1_2_load_37 | 1 | 0.0011312 | 0.00028349 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3295-6_1_2_load_157 | 6 | 0.0020073 | 0.00050308 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3295-6_1_2_load_35 | 7 | 0.0013091 | 0.00032808 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3295-6_1_2_load_136 | 8 | 0.00065996 | 0.0001654 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3295-6_1_2_load_32 | 10 | 0.0029361 | 0.00073586 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3295-6_1_2_load_154 | 11 | 0.00071116 | 0.00017823 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3295-6_1_2_load_212 | 12 | 0.00037875 | 9.4923e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3295-6_1_2_load_33 | 14 | 0.0017977 | 0.00045056 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3295-6_1_2_load_102 | 15 | 0.0010533 | 0.00026398 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3295-6_1_2_load_251 | 17 | 0.00038235 | 9.5827e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3295-6_1_2_load_55 | 19 | 0.00088672 | 0.00022223 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3295-6_1_2_load_53 | 21 | 0.00029844 | 7.4795e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3295-6_1_2_load_165 | 24 | 0.00024945 | 6.2518e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3295-6_1_2_load_240 | 25 | 0.00095025 | 0.00023816 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3295-6_1_2_load_246 | 26 | 0.00029529 | 7.4007e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3295-6_1_2_load_61 | 28 | 0.0016008 | 0.00040119 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3295-6_1_2_load_218 | 29 | 0.0028823 | 0.00072238 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3295-6_1_2_load_241 | 31 | 0.00066291 | 0.00016614 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3295-6_1_2_load_62 | 32 | 0.00028783 | 7.2137e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3295-6_1_2_load_64 | 34 | 0.00029161 | 7.3084e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3295-6_1_2_load_78 | 36 | 0.00016835 | 4.2193e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3295-6_1_2_load_66 | 38 | 0.0010514 | 0.0002635 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3295-6_1_2_load_67 | 39 | 0.00032354 | 8.1086e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3295-6_1_2_load_68 | 40 | 0.00027137 | 6.8012e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3295-6_1_2_load_69 | 41 | 0.00034172 | 8.5643e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3295-6_1_2_load_75 | 43 | 0.00014883 | 3.7299e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3295-6_1_2_load_76 | 44 | 0.00033975 | 8.5149e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3295-6_1_2_load_77 | 45 | 0.00044552 | 0.00011166 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3295-6_1_2_load_169 | 47 | 0.00081629 | 0.00020458 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3295-6_1_2_load_71 | 48 | 0.00015681 | 3.9301e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3295-6_1_2_load_72 | 49 | 0.00022803 | 5.7148e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3295-6_1_2_load_74 | 50 | 0.00027721 | 6.9475e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3295-6_1_2_load_80 | 52 | 0.0003664 | 9.1828e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3295-6_1_2_load_82 | 54 | 0.0010115 | 0.00025351 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3295-6_1_2_load_126 | 55 | 0.00029877 | 7.4878e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3295-6_1_2_load_122 | 56 | 0.00013761 | 3.4489e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3295-6_1_2_load_83 | 57 | 0.00028051 | 7.0303e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3295-6_1_2_load_161 | 58 | 0.00037823 | 9.4794e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3295-6_1_2_load_84 | 60 | 0.00047803 | 0.0001198 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3295-6_1_2_load_85 | 61 | 0.00044815 | 0.00011232 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3295-6_1_2_load_86 | 62 | 0.0014031 | 0.00035165 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3295-6_1_2_load_87 | 63 | 0.0016689 | 0.00041826 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3295-6_1_2_load_88 | 64 | 0.0011121 | 0.00027872 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3295-6_1_2_load_91 | 67 | 0.0018623 | 0.00046675 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3295-6_1_2_load_92 | 68 | 0.0012004 | 0.00030086 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3295-6_1_2_load_100 | 69 | 0.00045729 | 0.00011461 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3295-6_1_2_load_97 | 70 | 0.00054509 | 0.00013661 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3295-6_1_2_load_93 | 71 | 0.0016908 | 0.00042376 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3295-6_1_2_load_158 | 72 | 0.0018183 | 0.00045572 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3295-6_1_2_load_145 | 73 | 0.00082669 | 0.00020719 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3295-6_1_2_load_98 | 74 | 0.0012225 | 0.00030638 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3295-6_1_2_load_159 | 76 | 0.0010137 | 0.00025406 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3295-6_1_2_load_96 | 78 | 0.001475 | 0.00036967 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3295-6_1_2_load_130 | 79 | 0.00035594 | 8.9206e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3295-6_1_2_load_127 | 80 | 0.0019442 | 0.00048727 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3295-6_1_2_load_106 | 81 | 0.0015646 | 0.00039213 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3295-6_1_2_load_128 | 83 | 0.00025906 | 6.4926e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3295-6_1_2_load_99 | 85 | 0.0013446 | 0.00033698 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3295-6_1_2_load_101 | 86 | 0.0013784 | 0.00034547 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3295-6_1_2_load_162 | 87 | 0.0021051 | 0.00052759 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3295-6_1_2_load_143 | 88 | 0.00093535 | 0.00023442 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3295-6_1_2_load_117 | 89 | 0.001123 | 0.00028146 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3295-6_1_2_load_103 | 90 | 0.00075275 | 0.00018866 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3295-6_1_2_load_104 | 91 | 0.0035658 | 0.00089368 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3295-6_1_2_load_107 | 92 | 0.002045 | 0.00051253 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3295-6_1_2_load_172 | 93 | 0.0016315 | 0.0004089 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3295-6_1_2_load_108 | 94 | 0.00026659 | 6.6813e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3295-6_1_2_load_110 | 96 | 0.00024625 | 6.1715e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3295-6_1_2_load_111 | 97 | 0.00038643 | 9.6848e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3295-6_1_2_load_116 | 98 | 0.00069333 | 0.00017377 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3295-6_1_2_load_112 | 99 | 0.00010135 | 2.54e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3295-6_1_2_load_114 | 101 | 0.00076354 | 0.00019136 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3295-6_1_2_load_120 | 102 | 0.0002631 | 6.5939e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3295-6_1_2_load_118 | 104 | 0.00012547 | 3.1445e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3295-6_1_2_load_173 | 105 | 0.00017701 | 4.4363e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3295-6_1_2_load_119 | 107 | 0.00016633 | 4.1687e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3295-6_1_2_load_142 | 109 | 0.0002403 | 6.0224e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3295-6_1_2_load_170 | 112 | 0.00014018 | 3.5132e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3295-6_1_2_load_153 | 113 | 0.00011622 | 2.9127e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3295-6_1_2_load_244 | 114 | 0.0002337 | 5.8571e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3295-6_1_2_load_152 | 116 | 0.00013163 | 3.299e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3295-6_1_2_load_129 | 117 | 0.00047008 | 0.00011781 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3295-6_1_2_load_138 | 118 | 0.0002974 | 7.4537e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3295-6_1_2_load_131 | 119 | 0.00072969 | 0.00018288 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3295-6_1_2_load_132 | 120 | 0.00072954 | 0.00018284 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3295-6_1_2_load_133 | 121 | 0.00059686 | 0.00014959 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3295-6_1_2_load_134 | 122 | 0.00033531 | 8.4035e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3295-6_1_2_load_135 | 123 | 0.0007348 | 0.00018416 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3295-6_1_2_load_160 | 124 | 0.0012062 | 0.0003023 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3295-6_1_2_load_139 | 125 | 0.00022805 | 5.7156e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3295-6_1_2_load_141 | 126 | 0.00086934 | 0.00021788 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3295-6_1_2_load_144 | 127 | 0.0027273 | 0.00068353 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3295-6_1_2_load_146 | 128 | 0.00094249 | 0.00023621 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3295-6_1_2_load_155 | 129 | 0.00096073 | 0.00024078 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3295-6_1_2_load_147 | 130 | 0.00030318 | 7.5983e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3295-6_1_2_load_148 | 131 | 0.00011048 | 2.7689e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3295-6_1_2_load_150 | 133 | 0.00022712 | 5.6922e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3295-6_1_2_load_163 | 134 | 0.00022049 | 5.5259e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3295-6_1_2_load_245 | 135 | 0.00028847 | 7.2297e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3295-6_1_2_load_164 | 136 | 0.00010806 | 2.7083e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3295-6_1_2_load_217 | 137 | 0.00057704 | 0.00014462 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3295-6_1_2_load_174 | 138 | 0.00017812 | 4.4641e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 91 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3295-6_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.045041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3295-6_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.42026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3295-6_1_2_line_2 | NAYY 4x150 SE | 1 | 7 | 0.0040584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3295-6_1_2_line_3 | NAYY 4x150 SE | 2 | 8 | 0.050514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3295-6_1_2_line_4 | NAYY 4x150 SE | 3 | 4 | 0.3838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3295-6_1_2_line_5 | NAYY 4x150 SE | 3 | 5 | 0.1287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3295-6_1_2_line_6 | NAYY 4x150 SE | 3 | 6 | 0.053201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3295-6_1_2_line_7 | NAYY 4x150 SE | 4 | 9 | 0.1693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3295-6_1_2_line_8 | NAYY 4x150 SE | 4 | 10 | 0.11986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3295-6_1_2_line_9 | NAYY 4x150 SE | 5 | 11 | 0.12859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3295-6_1_2_line_10 | NAYY 4x150 SE | 7 | 14 | 0.0067387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3295-6_1_2_line_11 | NAYY 4x150 SE | 9 | 15 | 0.041286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3295-6_1_2_line_12 | NAYY 4x150 SE | 10 | 14 | 0.010584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3295-6_1_2_line_13 | NAYY 4x150 SE | 11 | 129 | 0.06336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3295-6_1_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.0076606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3295-6_1_2_line_15 | NAYY 4x150 SE | 13 | 139 | 0.082858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3295-6_1_2_line_16 | NAYY 4x150 SE | 16 | 17 | 0.066549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3295-6_1_2_line_17 | NAYY 4x150 SE | 16 | 18 | 0.066999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3295-6_1_2_line_18 | NAYY 4x150 SE | 18 | 19 | 0.019862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3295-6_1_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.2504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3295-6_1_2_line_20 | NAYY 4x150 SE | 18 | 21 | 0.36602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3295-6_1_2_line_21 | NAYY 4x150 SE | 19 | 27 | 0.018912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3295-6_1_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.10649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3295-6_1_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.037339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3295-6_1_2_line_24 | NAYY 4x150 SE | 20 | 24 | 0.087436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3295-6_1_2_line_25 | NAYY 4x150 SE | 21 | 26 | 0.25252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3295-6_1_2_line_26 | NAYY 4x150 SE | 22 | 25 | 0.035054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3295-6_1_2_line_27 | NAYY 4x150 SE | 23 | 29 | 0.21184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3295-6_1_2_line_28 | NAYY 4x150 SE | 24 | 30 | 0.020116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3295-6_1_2_line_29 | NAYY 4x150 SE | 25 | 31 | 0.0064215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3295-6_1_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.012607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3295-6_1_2_line_31 | NAYY 4x150 SE | 29 | 137 | 0.026851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3295-6_1_2_line_32 | NAYY 4x150 SE | 30 | 109 | 0.20317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_3295-6_1_2_line_33 | NAYY 4x150 SE | 30 | 108 | 0.085499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_3295-6_1_2_line_34 | NAYY 4x150 SE | 32 | 33 | 0.051228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3295-6_1_2_line_35 | NAYY 4x150 SE | 32 | 34 | 0.024453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3295-6_1_2_line_36 | NAYY 4x150 SE | 33 | 35 | 0.24465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3295-6_1_2_line_37 | NAYY 4x150 SE | 35 | 36 | 0.1285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3295-6_1_2_line_38 | NAYY 4x150 SE | 36 | 37 | 0.03157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3295-6_1_2_line_39 | NAYY 4x150 SE | 37 | 52 | 0.088052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3295-6_1_2_line_40 | NAYY 4x150 SE | 37 | 53 | 0.51338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3295-6_1_2_line_41 | NAYY 4x150 SE | 38 | 39 | 0.02451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3295-6_1_2_line_42 | NAYY 4x150 SE | 38 | 40 | 0.098288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3295-6_1_2_line_43 | NAYY 4x150 SE | 39 | 41 | 0.017515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3295-6_1_2_line_44 | NAYY 4x150 SE | 40 | 42 | 0.033801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3295-6_1_2_line_45 | NAYY 4x150 SE | 41 | 43 | 0.040405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3295-6_1_2_line_46 | NAYY 4x150 SE | 42 | 44 | 0.045979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3295-6_1_2_line_47 | NAYY 4x150 SE | 42 | 45 | 0.045999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3295-6_1_2_line_48 | NAYY 4x150 SE | 43 | 46 | 0.07857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3295-6_1_2_line_49 | NAYY 4x150 SE | 45 | 47 | 0.23814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3295-6_1_2_line_50 | NAYY 4x150 SE | 46 | 48 | 0.054133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3295-6_1_2_line_51 | NAYY 4x150 SE | 47 | 51 | 0.27198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3295-6_1_2_line_52 | NAYY 4x150 SE | 48 | 49 | 0.068177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3295-6_1_2_line_53 | NAYY 4x150 SE | 49 | 50 | 0.080996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3295-6_1_2_line_54 | NAYY 4x150 SE | 51 | 103 | 0.39874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_3295-6_1_2_line_55 | NAYY 4x150 SE | 51 | 100 | 0.19678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_3295-6_1_2_line_56 | NAYY 4x150 SE | 52 | 54 | 0.14331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3295-6_1_2_line_57 | NAYY 4x150 SE | 53 | 55 | 0.061297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3295-6_1_2_line_58 | NAYY 4x150 SE | 53 | 56 | 0.13605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_3295-6_1_2_line_59 | NAYY 4x150 SE | 54 | 57 | 0.054065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3295-6_1_2_line_60 | NAYY 4x150 SE | 55 | 58 | 0.017099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3295-6_1_2_line_61 | NAYY 4x150 SE | 56 | 59 | 0.16401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_3295-6_1_2_line_62 | NAYY 4x150 SE | 57 | 60 | 0.055513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3295-6_1_2_line_63 | NAYY 4x150 SE | 59 | 110 | 0.16631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3295-6_1_2_line_64 | NAYY 4x150 SE | 59 | 106 | 0.073989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
65 | LV_3295-6_1_2_line_65 | NAYY 4x150 SE | 60 | 61 | 0.024802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3295-6_1_2_line_66 | NAYY 4x150 SE | 61 | 62 | 0.032338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3295-6_1_2_line_67 | NAYY 4x150 SE | 63 | 64 | 0.020872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3295-6_1_2_line_68 | NAYY 4x150 SE | 63 | 65 | 0.016887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3295-6_1_2_line_69 | NAYY 4x150 SE | 64 | 66 | 0.035724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3295-6_1_2_line_70 | NAYY 4x150 SE | 65 | 67 | 0.0044811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3295-6_1_2_line_71 | NAYY 4x150 SE | 65 | 68 | 0.016693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3295-6_1_2_line_72 | NAYY 4x150 SE | 66 | 69 | 0.0072252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3295-6_1_2_line_73 | NAYY 4x150 SE | 66 | 70 | 0.008528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3295-6_1_2_line_74 | NAYY 4x150 SE | 67 | 71 | 0.027321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3295-6_1_2_line_75 | NAYY 4x150 SE | 68 | 72 | 0.018359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3295-6_1_2_line_76 | NAYY 4x150 SE | 69 | 73 | 0.012399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3295-6_1_2_line_77 | NAYY 4x150 SE | 70 | 74 | 0.0078207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3295-6_1_2_line_78 | NAYY 4x150 SE | 71 | 75 | 0.0026349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3295-6_1_2_line_79 | NAYY 4x150 SE | 72 | 76 | 0.02361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3295-6_1_2_line_80 | NAYY 4x150 SE | 73 | 88 | 0.0041774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3295-6_1_2_line_81 | NAYY 4x150 SE | 74 | 85 | 0.0059057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3295-6_1_2_line_82 | NAYY 4x150 SE | 75 | 77 | 0.04323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
83 | LV_3295-6_1_2_line_83 | NAYY 4x150 SE | 75 | 78 | 0.014717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_3295-6_1_2_line_84 | NAYY 4x150 SE | 76 | 124 | 0.012035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3295-6_1_2_line_85 | NAYY 4x150 SE | 77 | 79 | 0.12148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_3295-6_1_2_line_86 | NAYY 4x150 SE | 77 | 80 | 0.026978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3295-6_1_2_line_87 | NAYY 4x150 SE | 78 | 81 | 0.0098887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_3295-6_1_2_line_88 | NAYY 4x150 SE | 79 | 82 | 0.0070864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_3295-6_1_2_line_89 | NAYY 4x150 SE | 80 | 83 | 0.01315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3295-6_1_2_line_90 | NAYY 4x150 SE | 81 | 84 | 0.01463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_3295-6_1_2_line_91 | NAYY 4x150 SE | 82 | 109 | 0.073803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_3295-6_1_2_line_92 | NAYY 4x150 SE | 82 | 118 | 0.020011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3295-6_1_2_line_93 | NAYY 4x150 SE | 83 | 117 | 0.064326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3295-6_1_2_line_94 | NAYY 4x150 SE | 84 | 92 | 0.013881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_3295-6_1_2_line_95 | NAYY 4x150 SE | 84 | 90 | 0.03825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_3295-6_1_2_line_96 | NAYY 4x150 SE | 85 | 86 | 0.019146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3295-6_1_2_line_97 | NAYY 4x150 SE | 86 | 87 | 0.006556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3295-6_1_2_line_98 | NAYY 4x150 SE | 87 | 89 | 0.0214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3295-6_1_2_line_99 | NAYY 4x150 SE | 88 | 127 | 0.024402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3295-6_1_2_line_100 | NAYY 4x150 SE | 89 | 98 | 0.026104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3295-6_1_2_line_101 | NAYY 4x150 SE | 90 | 91 | 0.0048849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
102 | LV_3295-6_1_2_line_102 | NAYY 4x150 SE | 92 | 93 | 0.017575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3295-6_1_2_line_103 | NAYY 4x150 SE | 94 | 95 | 0.024781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3295-6_1_2_line_104 | NAYY 4x150 SE | 95 | 96 | 0.079174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3295-6_1_2_line_105 | NAYY 4x150 SE | 95 | 97 | 0.31839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3295-6_1_2_line_106 | NAYY 4x150 SE | 97 | 98 | 0.34451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3295-6_1_2_line_107 | NAYY 4x150 SE | 99 | 100 | 0.11476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3295-6_1_2_line_108 | NAYY 4x150 SE | 100 | 101 | 0.05808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
109 | LV_3295-6_1_2_line_109 | NAYY 4x150 SE | 101 | 102 | 0.029836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
110 | LV_3295-6_1_2_line_110 | NAYY 4x150 SE | 102 | 104 | 0.00048233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
111 | LV_3295-6_1_2_line_111 | NAYY 4x150 SE | 103 | 105 | 0.29375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3295-6_1_2_line_112 | NAYY 4x150 SE | 103 | 106 | 0.44922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
113 | LV_3295-6_1_2_line_113 | NAYY 4x150 SE | 104 | 107 | 0.22343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
114 | LV_3295-6_1_2_line_114 | NAYY 4x150 SE | 105 | 138 | 0.00070431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3295-6_1_2_line_115 | NAYY 4x150 SE | 106 | 113 | 0.061208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3295-6_1_2_line_116 | NAYY 4x150 SE | 107 | 108 | 0.0071119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
117 | LV_3295-6_1_2_line_117 | NAYY 4x150 SE | 110 | 111 | 0.1219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3295-6_1_2_line_118 | NAYY 4x150 SE | 110 | 112 | 0.082273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3295-6_1_2_line_119 | NAYY 4x150 SE | 111 | 114 | 0.20019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3295-6_1_2_line_120 | NAYY 4x150 SE | 111 | 115 | 0.29299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3295-6_1_2_line_121 | NAYY 4x150 SE | 113 | 116 | 0.01693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3295-6_1_2_line_122 | NAYY 4x150 SE | 115 | 135 | 0.12828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3295-6_1_2_line_123 | NAYY 4x150 SE | 115 | 132 | 0.36266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3295-6_1_2_line_124 | NAYY 4x150 SE | 118 | 125 | 0.017377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3295-6_1_2_line_125 | NAYY 4x150 SE | 119 | 120 | 0.020095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3295-6_1_2_line_126 | NAYY 4x150 SE | 119 | 121 | 0.019791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3295-6_1_2_line_127 | NAYY 4x150 SE | 120 | 122 | 0.038747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3295-6_1_2_line_128 | NAYY 4x150 SE | 121 | 123 | 0.00057888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3295-6_1_2_line_129 | NAYY 4x150 SE | 122 | 124 | 0.020404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3295-6_1_2_line_130 | NAYY 4x150 SE | 125 | 126 | 0.10032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3295-6_1_2_line_131 | NAYY 4x150 SE | 127 | 128 | 0.053696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3295-6_1_2_line_132 | NAYY 4x150 SE | 128 | 129 | 0.013908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3295-6_1_2_line_133 | NAYY 4x150 SE | 130 | 131 | 0.037255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3295-6_1_2_line_134 | NAYY 4x150 SE | 130 | 132 | 0.090889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3295-6_1_2_line_135 | NAYY 4x150 SE | 131 | 133 | 0.0036115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3295-6_1_2_line_136 | NAYY 4x150 SE | 133 | 134 | 0.071092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3295-6_1_2_line_137 | NAYY 4x150 SE | 134 | 136 | 0.0023861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3295-6_1_2_line_138 | NAYY 4x150 SE | 137 | 139 | 0.01826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3295-6_1_2_trafo_104 | 0.25 MVA 20/0.4 kV | 140 | 91 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48
0 | 2735219.8971 | 1219485.9413 | 2735223.9616 | 1219479.4615 | 2735225.7553 | 1219473.0191 | 2735224.9603 | 1219463.9047 | 2735220.2105 | 1219449.7518 | 2735217.9725 | 1219443.5148
1 | 2735219.8971 | 1219485.9413 | 2735226.1738 | 1219484.338 | 2735231.9764 | 1219476.8746 | 2735233.6356 | 1219469.0058 | 2735236.6377 | 1219460.8339 | 2735240.6123 | 1219456.6428 | 2735245.8184 | 1219453.3805 | 2735251.759 | 1219450.8689 | 2735258.0806 | 1219448.2992 | 2735264.7785 | 1219446.5387 | 2735272.3326 | 1219442.8516 | 2735290.4571 | 1219434.7008 | 2735323.4702 | 1219419.1489 | 2735350.1157 | 1219409.5351 | 2735377.0014 | 1219402.3845 | 2735396.2843 | 1219397.7188 | 2735422.539 | 1219390.2761 | 2735444.2477 | 1219387.1114 | 2735464.3732 | 1219384.4557 | 2735485.4425 | 1219383.3672 | 2735521.2072 | 1219381.379 | 2735541.5974 | 1219380.1085 | 2735559.5301 | 1219381.0729 | 2735583.8614 | 1219379.4252 | 2735606.1188 | 1219377.8415 | 2735609.2822 | 1219377.6134
2 | 2735217.9725 | 1219443.5148 | 2735216.6018 | 1219439.6949
3 | 2735609.2822 | 1219377.6134 | 2735616.3444 | 1219380.1985 | 2735642.9505 | 1219389.334 | 2735657.4198 | 1219392.732
4 | 2735064.9421 | 1219399.6883 | 2735055.0157 | 1219399.8634 | 2735037.9565 | 1219399.8879 | 2735025.1371 | 1219397.0728 | 2735009.1204 | 1219390.2931 | 2735005.8863 | 1219397.6592 | 2735033.7935 | 1219409.7127 | 2735050.4517 | 1219415.9844 | 2735062.1896 | 1219419.2866 | 2735076.4829 | 1219422.0462 | 2735092.9589 | 1219422.6314 | 2735110.4802 | 1219422.3174 | 2735140.3392 | 1219416.601 | 2735170.5628 | 1219407.8683 | 2735210.1896 | 1219397.6035 | 2735250.2856 | 1219388.4171 | 2735262.1734 | 1219386.1184 | 2735314.7495 | 1219377.6387
5 | 2735000.2423 | 1219302.0635 | 2735002.3498 | 1219305.8811 | 2735031.104 | 1219321.7792 | 2735039.4025 | 1219336.4794 | 2735048.5058 | 1219348.4957 | 2735053.5855 | 1219363.8568 | 2735052.7061 | 1219375.5132 | 2735051.1346 | 1219390.2342 | 2735058.3305 | 1219393.967 | 2735064.9421 | 1219399.6883
6 | 2735064.9421 | 1219399.6883 | 2735079.4202 | 1219398.9938 | 2735100.255 | 1219392.5053 | 2735115.9954 | 1219386.3963
7 | 2735314.7495 | 1219377.6387 | 2735315.0347 | 1219373.1081 | 2735318.2028 | 1219366.9972 | 2735325.1059 | 1219362.5614 | 2735346.1993 | 1219354.7341 | 2735363.5228 | 1219354.1161 | 2735375.4674 | 1219352.6641 | 2735396.4004 | 1219349.893 | 2735433.0492 | 1219341.0854 | 2735470.6272 | 1219329.1521
8 | 2735314.7495 | 1219377.6387 | 2735314.1908 | 1219385.855 | 2735310.4554 | 1219389.8735 | 2735297.0398 | 1219393.2494 | 2735265.099 | 1219399.3625 | 2735230.248 | 1219406.2548 | 2735222.6036 | 1219409.9065 | 2735217.6674 | 1219413.9867 | 2735214.3397 | 1219422.1179 | 2735214.3252 | 1219422.7095
9 | 2735000.2423 | 1219302.0635 | 2734979.2162 | 1219298.2284 | 2734965.5791 | 1219297.6523 | 2734961.8854 | 1219296.1562 | 2734959.5197 | 1219293.0112 | 2734959.1109 | 1219289.2766 | 2734960.0905 | 1219285.9182 | 2734962.4825 | 1219283.2146 | 2734966.2321 | 1219281.9096 | 2734973.7104 | 1219282.5685 | 2734983.1572 | 1219286.141 | 2734990.9254 | 1219288.0742 | 2734999.2285 | 1219288.5182 | 2735026.2225 | 1219287.9739 | 2735036.0291 | 1219286.7145
10 | 2735214.7797 | 1219433.2212 | 2735215.584 | 1219436.8584 | 2735216.6018 | 1219439.6949
11 | 2735470.6272 | 1219329.1521 | 2735478.3983 | 1219328.6173 | 2735509.8279 | 1219317.0332
12 | 2735214.3252 | 1219422.7095 | 2735214.1382 | 1219430.3202 | 2735214.7797 | 1219433.2212
13 | 2735036.0291 | 1219286.7145 | 2735039.6157 | 1219286.2539 | 2735047.5119 | 1219284.5537 | 2735054.9479 | 1219282.3871 | 2735062.0248 | 1219278.9892 | 2735069.0332 | 1219274.2552 | 2735073.5401 | 1219268.0189 | 2735078.114 | 1219261.8398 | 2735087.2255 | 1219253.6793
14 | 2734849.7513 | 1219150.1189 | 2734854.9939 | 1219155.7045
15 | 2734849.7513 | 1219150.1189 | 2734850.2681 | 1219133.6725 | 2734846.333 | 1219113.3334 | 2734830.7091 | 1219082.799 | 2734820.3966 | 1219077.8727
16 | 2734611.8299 | 1218693.5292 | 2734606.2944 | 1218688.5112 | 2734597.5648 | 1218678.35 | 2734596.2169 | 1218673.827 | 2734596.6363 | 1218670.7228 | 2734599.1506 | 1218666.6429 | 2734605.2679 | 1218661.3768 | 2734611.3337 | 1218653.3516 | 2734611.8747 | 1218649.5719 | 2734610.4682 | 1218645.6257 | 2734607.7274 | 1218639.2363
17 | 2734611.8299 | 1218693.5292 | 2734614.3562 | 1218692.2742 | 2734617.7778 | 1218691.0505 | 2734622.3509 | 1218689.9418 | 2734628.1206 | 1218689.6385 | 2734633.7651 | 1218689.8329 | 2734645.4155 | 1218691.0305 | 2734646.5355 | 1218685.151 | 2734652.6587 | 1218659.1457
18 | 2734652.6587 | 1218659.1457 | 2734672.388 | 1218661.4376
19 | 2734652.6587 | 1218659.1457 | 2734646.5355 | 1218685.151 | 2734645.4155 | 1218691.0305 | 2734649.9205 | 1218722.1357 | 2734662.4712 | 1218724.1432 | 2734678.9872 | 1218723.3825 | 2734708.0594 | 1218732.1025 | 2734731.2068 | 1218763.0736 | 2734743.0935 | 1218792.0663 | 2734775.8336 | 1218805.0953 | 2734796.9143 | 1218801.2356
20 | 2734652.6587 | 1218659.1457 | 2734653.7342 | 1218654.5663 | 2734657.1819 | 1218616.2682 | 2734654.6097 | 1218598.0618 | 2734638.9331 | 1218564.3798 | 2734637.8321 | 1218544.572 | 2734643.6498 | 1218511.2649 | 2734643.5817 | 1218489.7679 | 2734640.9822 | 1218479.1449 | 2734633.7696 | 1218463.3356 | 2734626.8738 | 1218450.636 | 2734617.9824 | 1218434.8554 | 2734615.3402 | 1218424.7763 | 2734618.1607 | 1218412.53 | 2734626.4585 | 1218397.8165 | 2734650.185 | 1218367.6722 | 2734652.5837 | 1218357.2957 | 2734651.8138 | 1218349.3718 | 2734648.7389 | 1218342.3076 | 2734630.0082 | 1218323.2119
21 | 2734691.1739 | 1218663.6199 | 2734672.388 | 1218661.4376
22 | 2734796.9143 | 1218801.2356 | 2734789.2853 | 1218817.5987 | 2734785.4701 | 1218828.8328 | 2734779.4343 | 1218842.5742 | 2734775.6469 | 1218849.561 | 2734756.2075 | 1218881.8813 | 2734749.3825 | 1218896.2832
23 | 2734796.9143 | 1218801.2356 | 2734797.908 | 1218808.9867 | 2734792.5131 | 1218838.0108
24 | 2734796.9143 | 1218801.2356 | 2734799.1972 | 1218796.9838 | 2734801.1282 | 1218794.5254 | 2734803.891 | 1218792.553 | 2734807.0689 | 1218791.0236 | 2734810.9286 | 1218789.5653 | 2734814.9228 | 1218788.5326 | 2734818.044 | 1218788.1696 | 2734821.7918 | 1218788.299 | 2734825.8444 | 1218789.0468 | 2734829.2192 | 1218790.2242 | 2734832.1613 | 1218791.7364 | 2734833.9885 | 1218793.1901 | 2734850.8835 | 1218811.5542 | 2734859.0175 | 1218821.5021 | 2734861.9766 | 1218824.605 | 2734863.5992 | 1218825.7556
25 | 2734630.0082 | 1218323.2119 | 2734697.9989 | 1218080.0164
26 | 2734749.3825 | 1218896.2832 | 2734748.1702 | 1218889.4613 | 2734747.4752 | 1218879.5819 | 2734747.5152 | 1218863.3917 | 2734747.6936 | 1218861.3689
27 | 2734792.5131 | 1218838.0108 | 2734787.4032 | 1218865.5179 | 2734773.3441 | 1218941.2178 | 2734771.9441 | 1218973.5461 | 2734788.096 | 1219036.7858 | 2734794.9231 | 1219043.0135
28 | 2734882.3002 | 1218833.0498 | 2734867.7564 | 1218827.8718 | 2734864.3902 | 1218826.3166 | 2734863.5992 | 1218825.7556
29 | 2734747.12 | 1218855.0203 | 2734747.8726 | 1218859.3409 | 2734747.6936 | 1218861.3689
30 | 2734692.1719 | 1218651.0544 | 2734691.1739 | 1218663.6199
31 | 2734814.7606 | 1219061.1093 | 2734794.9231 | 1219043.0135
32 | 2734882.3002 | 1218833.0498 | 2734885.9687 | 1218835.3347 | 2734889.2007 | 1218838.1213 | 2734892.8194 | 1218842.6069 | 2734896.4865 | 1218848.6393 | 2734902.9716 | 1218860.9852 | 2734925.8121 | 1218906.7735 | 2734930.0387 | 1218915.5876 | 2734934.406 | 1218922.8814 | 2734937.7669 | 1218927.6837 | 2734943.1137 | 1218933.6319 | 2734949.269 | 1218939.4206 | 2734954.3654 | 1218943.0167 | 2734963.3071 | 1218948.4682 | 2734981.1175 | 1218959.5697 | 2734985.3987 | 1218962.9584 | 2734988.7442 | 1218966.426 | 2734991.1889 | 1218969.773 | 2735003.1213 | 1218990.5227
33 | 2734884.596 | 1218748.8101 | 2734883.7005 | 1218765.8817 | 2734887.8103 | 1218819.3966 | 2734882.3002 | 1218833.0498
34 | 2735899.2438 | 1218712.4917 | 2735873.7951 | 1218737.3541 | 2735874.9374 | 1218752.9631
35 | 2735884.6985 | 1218772.5986 | 2735885.7622 | 1218765.5838 | 2735882.9943 | 1218758.7817 | 2735874.9526 | 1218753.1714 | 2735874.9374 | 1218752.9631
36 | 2735851.082 | 1218572.4665 | 2735853.8729 | 1218577.601 | 2735852.9582 | 1218594.394 | 2735842.4153 | 1218614.8706 | 2735837.6024 | 1218629.473 | 2735826.4464 | 1218654.1947 | 2735820.6306 | 1218663.5031 | 2735822.0309 | 1218669.0174 | 2735829.3364 | 1218670.2961 | 2735843.7887 | 1218666.1555 | 2735869.218 | 1218662.7769 | 2735885.5659 | 1218660.4144 | 2735895.0745 | 1218660.309 | 2735906.4502 | 1218662.2256 | 2735910.6291 | 1218670.083 | 2735911.2183 | 1218680.8609 | 2735909.5676 | 1218689.308 | 2735902.2596 | 1218700.7842 | 2735899.1207 | 1218706.5729 | 2735899.2438 | 1218712.4917
37 | 2735851.082 | 1218572.4665 | 2735847.7867 | 1218571.1347 | 2735842.2708 | 1218571.954 | 2735832.7471 | 1218578.7092 | 2735815.0772 | 1218590.0825 | 2735797.5162 | 1218596.6877 | 2735790.7461 | 1218603.2277 | 2735783.9189 | 1218603.2832 | 2735774.2571 | 1218594.1222 | 2735770.2374 | 1218591.5951 | 2735758.1025 | 1218592.3304 | 2735744.3387 | 1218593.2398 | 2735736.9238 | 1218595.1797
38 | 2735705.798 | 1218599.8785 | 2735726.5107 | 1218597.9042 | 2735736.9238 | 1218595.1797
39 | 2735705.798 | 1218599.8785 | 2735692.5539 | 1218599.9769 | 2735682.5127 | 1218602.795 | 2735667.3192 | 1218612.8018 | 2735654.9393 | 1218619.6256 | 2735627.8391 | 1218629.3611 | 2735624.6275 | 1218629.883
40 | 2735597.3618 | 1218438.3318 | 2735605.9045 | 1218439.972 | 2735608.8031 | 1218439.7267 | 2735611.9536 | 1218437.4187 | 2735615.837 | 1218433.2703 | 2735621.6227 | 1218430.9445 | 2735633.5487 | 1218421.397 | 2735636.6234 | 1218414.4168 | 2735643.9453 | 1218396.3241 | 2735646.6902 | 1218391.1601 | 2735650.732 | 1218388.3942 | 2735655.5119 | 1218388.8923 | 2735664.2932 | 1218392.7288 | 2735670.5499 | 1218393.0604 | 2735677.0071 | 1218390.2607 | 2735683.1909 | 1218384.4633 | 2735686.8494 | 1218381.8556 | 2735692.1237 | 1218380.6525 | 2735703.4069 | 1218383.6564 | 2735709.0831 | 1218391.8035 | 2735718.0352 | 1218398.8021 | 2735724.1416 | 1218401.0652 | 2735726.1341 | 1218405.2585 | 2735723.2625 | 1218410.6531 | 2735716.641 | 1218415.3284 | 2735713.6063 | 1218418.8845 | 2735711.4957 | 1218426.5316 | 2735711.1484 | 1218442.1032 | 2735708.662 | 1218446.9172 | 2735705.4376 | 1218448.4673 | 2735701.5437 | 1218446.7439 | 2735698.2611 | 1218442.1876 | 2735694.1116 | 1218434.3533 | 2735688.7817 | 1218431.3405 | 2735684.4131 | 1218430.785 | 2735677.9738 | 1218431.8059 | 2735673.2361 | 1218434.1222 | 2735668.2175 | 1218440.1017 | 2735656.3449 | 1218460.6373 | 2735652.4735 | 1218469.5899 | 2735643.7127 | 1218478.52 | 2735633.7482 | 1218495.9632 | 2735627.5869 | 1218496.7791 | 2735645.2361 | 1218563.625 | 2735632.8235 | 1218581.2126 | 2735650.0092 | 1218595.4044 | 2735672.9554 | 1218598.3737 | 2735687.9023 | 1218594.8556 | 2735705.798 | 1218599.8785
41 | 2735850.48 | 1218968.9124 | 2735851.0579 | 1218968.8051 | 2735868.3588 | 1218963.9066 | 2735872.5663 | 1218963.5134 | 2735874.2769 | 1218963.6459
42 | 2735850.48 | 1218968.9124 | 2735844.1804 | 1218970.0827 | 2735837.6731 | 1218970.4457 | 2735830.4461 | 1218970.4031 | 2735819.8239 | 1218969.0932 | 2735777.8697 | 1218961.3862 | 2735763.0047 | 1218958.0224 | 2735756.4833 | 1218956.0055 | 2735753.9474 | 1218955.049
43 | 2735874.2769 | 1218963.6459 | 2735876.4316 | 1218963.8129 | 2735880.9345 | 1218964.783 | 2735887.705 | 1218967.195 | 2735890.9912 | 1218968.5643
44 | 2735722.4319 | 1218943.9976 | 2735727.9437 | 1218944.3456 | 2735733.1187 | 1218945.4756 | 2735738.1968 | 1218947.1927 | 2735751.086 | 1218953.9697 | 2735753.9474 | 1218955.049
45 | 2735928.2878 | 1218984.105 | 2735890.9912 | 1218968.5643
46 | 2735722.4319 | 1218943.9976 | 2735718.4712 | 1218946.5539 | 2735715.4524 | 1218948.0864 | 2735694.9391 | 1218955.0249 | 2735690.2461 | 1218958.065 | 2735687.628 | 1218961.0078 | 2735684.202 | 1218966.7583
47 | 2735722.4319 | 1218943.9976 | 2735715.6769 | 1218944.2328 | 2735677.0247 | 1218951.0012
48 | 2736004.4413 | 1218983.65 | 2735986.1929 | 1218987.8147 | 2735970.1479 | 1218991.5739 | 2735964.5256 | 1218992.4129 | 2735958.4908 | 1218992.6977 | 2735952.8195 | 1218992.3569 | 2735947.3008 | 1218991.319 | 2735939.0646 | 1218988.5955 | 2735928.2878 | 1218984.105
49 | 2735447.9251 | 1218967.0598 | 2735471.6279 | 1218975.5824 | 2735500.585 | 1218984.9264 | 2735508.4564 | 1218986.0063 | 2735521.1937 | 1218986.1183 | 2735535.7733 | 1218986.0166 | 2735543.455 | 1218985.0906 | 2735554.8268 | 1218982.4916 | 2735564.1914 | 1218979.0129 | 2735584.811 | 1218969.7299 | 2735611.083 | 1218960.6203 | 2735635.6993 | 1218952.5406 | 2735641.4757 | 1218951.6047 | 2735648.0091 | 1218951.4311 | 2735661.1982 | 1218952.3766 | 2735666.6864 | 1218952.4238 | 2735672.8597 | 1218951.7305 | 2735677.0247 | 1218951.0012
50 | 2736004.4413 | 1218983.65 | 2736001.4454 | 1218981.1907 | 2735998.163 | 1218979.6367 | 2735992.7298 | 1218978.5118 | 2735971.9532 | 1218976.358 | 2735965.8906 | 1218975.1965 | 2735961.0211 | 1218972.9946 | 2735956.7596 | 1218970.095 | 2735954.0887 | 1218967.8061
51 | 2735196.2568 | 1218872.1755 | 2735204.1778 | 1218875.091 | 2735211.5974 | 1218877.0165 | 2735221.5716 | 1218879.1224 | 2735236.9395 | 1218881.4286 | 2735244.099 | 1218882.77 | 2735248.3069 | 1218884.0332 | 2735251.5693 | 1218885.4751 | 2735256.3709 | 1218888.0085 | 2735266.3412 | 1218894.6292 | 2735283.1848 | 1218907.1664 | 2735295.8115 | 1218915.1597 | 2735323.0973 | 1218930.581 | 2735340.2893 | 1218937.7997 | 2735351.5833 | 1218940.9588 | 2735440.526 | 1218964.3994 | 2735447.9251 | 1218967.0598
52 | 2735954.0887 | 1218967.8061 | 2735952.3736 | 1218966.3362 | 2735946.1348 | 1218957.5978 | 2735943.0402 | 1218954.469 | 2735939.6345 | 1218952.0004 | 2735907.6377 | 1218938.8039 | 2735906.0166 | 1218937.9774 | 2735904.6683 | 1218936.5121 | 2735904.1802 | 1218934.2769 | 2735904.9499 | 1218931.1585 | 2735906.7483 | 1218929.209 | 2735906.7483 | 1218929.209
53 | 2735957.5992 | 1218891.3821 | 2735963.3416 | 1218897.3182 | 2735965.2878 | 1218900.1984 | 2735965.2795 | 1218902.8893 | 2735964.1279 | 1218904.7757 | 2735961.4293 | 1218906.5823 | 2735950.7096 | 1218909.5401 | 2735944.6146 | 1218911.7918 | 2735941.0395 | 1218913.7452 | 2735937.1459 | 1218916.681 | 2735929.1726 | 1218924.0496 | 2735926.3852 | 1218926.0877 | 2735922.8198 | 1218927.6188 | 2735919.0126 | 1218928.099 | 2735911.1747 | 1218927.8756 | 2735908.7138 | 1218928.2531 | 2735906.7483 | 1218929.209
54 | 2735196.2568 | 1218872.1755 | 2735195.1333 | 1218868.825 | 2735180.0751 | 1218854.8829 | 2735170.2975 | 1218835.4228 | 2735148.4568 | 1218789.812 | 2735144.0635 | 1218768.2834 | 2735134.3429 | 1218738.9388 | 2735132.2906 | 1218716.963 | 2735127.1721 | 1218704.9703 | 2735112.0533 | 1218688.9921 | 2735105.6636 | 1218678.8055 | 2735100.9133 | 1218663.9633 | 2735089.4913 | 1218591.8004 | 2735087.8423 | 1218562.7501 | 2735084.9972 | 1218548.2626 | 2735072.5773 | 1218501.9873
55 | 2735083.6891 | 1218853.1955 | 2735085.168 | 1218850.5936 | 2735082.679 | 1218843.8427 | 2735069.565 | 1218829.5336 | 2735064.489 | 1218819.677 | 2735064.011 | 1218813.9726 | 2735066.9579 | 1218809.5802 | 2735071.6494 | 1218809.2752 | 2735084.1724 | 1218813.8295 | 2735157.0878 | 1218858.1086 | 2735170.6445 | 1218862.2751 | 2735184.1119 | 1218868.697 | 2735192.23 | 1218871.2945 | 2735196.2568 | 1218872.1755
56 | 2735499.8089 | 1218674.3928 | 2735503.7382 | 1218672.9291 | 2735508.4759 | 1218665.9311 | 2735547.7946 | 1218652.1029 | 2735557.035 | 1218644.0954 | 2735565.626 | 1218629.2675 | 2735578.3088 | 1218626.8096 | 2735615.7751 | 1218631.3215 | 2735624.6275 | 1218629.883
57 | 2735597.3618 | 1218438.3318 | 2735591.0183 | 1218439.8109 | 2735586.3034 | 1218441.127 | 2735584.5979 | 1218444.3352 | 2735582.5067 | 1218455.8082 | 2735580.9655 | 1218460.7995 | 2735577.2175 | 1218464.673 | 2735558.5537 | 1218479.7273
58 | 2735597.3618 | 1218438.3318 | 2735592.944 | 1218435.6068 | 2735588.4945 | 1218434.2711 | 2735577.9785 | 1218439.9254 | 2735566.5058 | 1218442.9113 | 2735522.2913 | 1218443.9286 | 2735492.5107 | 1218436.9567 | 2735468.1275 | 1218434.3779 | 2735465.051 | 1218434.694
59 | 2735499.8089 | 1218674.3928 | 2735493.4693 | 1218676.7543 | 2735475.046 | 1218676.235 | 2735465.0413 | 1218682.4682 | 2735460.4908 | 1218691.2498 | 2735460.6917 | 1218698.4381 | 2735460.6917 | 1218698.4381
60 | 2735545.276 | 1218490.4993 | 2735545.8829 | 1218489.9477 | 2735558.5537 | 1218479.7273
61 | 2735309.1421 | 1218477.6012 | 2735328.9999 | 1218462.473 | 2735369.1445 | 1218452.4322 | 2735430.2765 | 1218442.0461 | 2735452.0002 | 1218436.0349 | 2735465.051 | 1218434.694
62 | 2735509.0937 | 1218723.8486 | 2735509.0937 | 1218723.8486 | 2735503.8009 | 1218719.2132 | 2735472.191 | 1218707.9407 | 2735460.6917 | 1218698.4381
63 | 2735309.1421 | 1218477.6012 | 2735304.8393 | 1218473.489 | 2735291.6204 | 1218471.1313 | 2735276.5524 | 1218465.9405 | 2735268.1525 | 1218463.0252 | 2735259.7354 | 1218455.5168 | 2735254.8227 | 1218449.5003 | 2735251.2611 | 1218441.8354 | 2735238.8362 | 1218411.8731 | 2735234.0274 | 1218403.2902 | 2735227.749 | 1218394.218 | 2735225.3481 | 1218385.9234 | 2735221.0001 | 1218361.727 | 2735218.7657 | 1218353.7919
64 | 2735309.1421 | 1218477.6012 | 2735305.5408 | 1218482.0453 | 2735299.0277 | 1218484.9776 | 2735265.545 | 1218503.2658 | 2735256.8868 | 1218506.7055 | 2735243.3345 | 1218503.9845
65 | 2735509.0937 | 1218723.8486 | 2735510.6767 | 1218739.364 | 2735516.9389 | 1218746.112 | 2735516.9389 | 1218746.112
66 | 2735549.15 | 1218748.9693 | 2735524.0555 | 1218746.6744 | 2735516.9389 | 1218746.112
67 | 2735162.1453 | 1219199.1811 | 2735178.1218 | 1219212.6128
68 | 2735149.2192 | 1219188.3138 | 2735162.1453 | 1219199.1811
69 | 2735200.3791 | 1219239.5836 | 2735197.1654 | 1219231.3261 | 2735191.8916 | 1219224.1894 | 2735178.1218 | 1219212.6128
70 | 2735149.2192 | 1219188.3138 | 2735144.7546 | 1219187.9288
71 | 2735149.2192 | 1219188.3138 | 2735152.852 | 1219186.8061 | 2735165.5208 | 1219185.2888
72 | 2735200.3791 | 1219239.5836 | 2735193.5024 | 1219241.8006
73 | 2735200.3791 | 1219239.5836 | 2735208.6614 | 1219237.5512
74 | 2735117.5347 | 1219185.5818 | 2735144.7546 | 1219187.9288
75 | 2735183.8706 | 1219185.2496 | 2735166.7453 | 1219185.1421 | 2735165.5208 | 1219185.2888
76 | 2735193.5024 | 1219241.8006 | 2735191.1633 | 1219242.5547 | 2735181.3863 | 1219244.3542
77 | 2735208.6614 | 1219237.5512 | 2735216.2568 | 1219235.6874
78 | 2735114.9096 | 1219185.3554 | 2735117.5347 | 1219185.5818
79 | 2735207.4804 | 1219185.3977 | 2735183.8706 | 1219185.2496
80 | 2735181.3863 | 1219244.3542 | 2735177.2779 | 1219245.1103
81 | 2735221.9462 | 1219234.1043 | 2735216.4727 | 1219235.6344 | 2735216.2568 | 1219235.6874
82 | 2735073.7552 | 1219175.225 | 2735083.8173 | 1219181.803 | 2735093.1174 | 1219183.4819 | 2735114.9096 | 1219185.3554
83 | 2735114.9096 | 1219185.3554 | 2735118.0148 | 1219170.9695
84 | 2735219.5156 | 1219185.4733 | 2735207.4804 | 1219185.3977
85 | 2735073.7552 | 1219175.225 | 2735059.6398 | 1219161.5826 | 2735057.2148 | 1219153.0206 | 2735052.2029 | 1219110.5719 | 2735042.0921 | 1219062.959 | 2735041.6785 | 1219061.4808
86 | 2735073.7552 | 1219175.225 | 2735061.1079 | 1219179.5307 | 2735047.8753 | 1219176.316
87 | 2735118.0148 | 1219170.9695 | 2735124.5491 | 1219163.5472
88 | 2735039.316 | 1219054.8116 | 2735040.9053 | 1219058.7175 | 2735041.6785 | 1219061.4808
89 | 2735047.8753 | 1219176.316 | 2735041.2653 | 1219174.7103 | 2735035.0282 | 1219175.8921
90 | 2735134.2164 | 1219152.5662 | 2735124.5491 | 1219163.5472
91 | 2735039.316 | 1219054.8116 | 2735036.0002 | 1219047.6972 | 2735003.1213 | 1218990.5227
92 | 2735039.316 | 1219054.8116 | 2735043.3904 | 1219054.9262 | 2735046.4058 | 1219055.8731 | 2735056.3833 | 1219063.8498
93 | 2734992.2546 | 1219203.3454 | 2734994.9137 | 1219202.594 | 2735000.3783 | 1219204.3414 | 2735007.2846 | 1219209.4688 | 2735012.2425 | 1219210.7934 | 2735015.7579 | 1219208.4378 | 2735031.3468 | 1219180.8794 | 2735035.0282 | 1219175.8921 | 2735035.0282 | 1219175.8921
94 | 2735134.2164 | 1219152.5662 | 2735138.3256 | 1219146.4655 | 2735136.1267 | 1219140.3216
95 | 2735134.2164 | 1219152.5662 | 2735157.9411 | 1219152.5933 | 2735168.517 | 1219148.5743 | 2735169.6751 | 1219145.5793
96 | 2735221.9462 | 1219234.1043 | 2735240.3853 | 1219228.9497
97 | 2735246.6992 | 1219227.1847 | 2735240.3853 | 1219228.9497
98 | 2735246.6992 | 1219227.1847 | 2735256.4631 | 1219224.4552 | 2735267.3092 | 1219221.4245
99 | 2735153.0365 | 1219243.0504 | 2735175.4048 | 1219245.4551 | 2735177.2779 | 1219245.1103
100 | 2735292.4501 | 1219214.3995 | 2735267.3092 | 1219221.4245
101 | 2735171.4368 | 1219141.0232 | 2735169.6751 | 1219145.5793
102 | 2735120.3117 | 1219132.6566 | 2735136.1267 | 1219140.3216
103 | 2735893.6373 | 1219127.3853 | 2735895.8012 | 1219127.3791 | 2735909.5462 | 1219135.5549 | 2735916.0068 | 1219137.0164
104 | 2735893.6373 | 1219127.3853 | 2735892.7804 | 1219124.0185 | 2735890.3804 | 1219121.3949 | 2735886.5334 | 1219120.9624 | 2735882.9825 | 1219122.8607 | 2735878.1618 | 1219129.1671 | 2735874.4729 | 1219136.7782 | 2735871.783 | 1219142.1991 | 2735869.1335 | 1219145.5192 | 2735865.3342 | 1219147.9902 | 2735861.12 | 1219148.0163 | 2735854.5027 | 1219145.8859 | 2735834.2286 | 1219137.3721
105 | 2735893.6373 | 1219127.3853 | 2735887.5177 | 1219127.4013 | 2735881.3662 | 1219138.459 | 2735879.8601 | 1219157.5405 | 2735878.012 | 1219164.3373 | 2735873.5462 | 1219170.0624 | 2735861.3121 | 1219176.8557 | 2735832.2838 | 1219186.6686 | 2735800.8909 | 1219186.9866 | 2735773.7786 | 1219184.0329 | 2735758.6321 | 1219181.0519 | 2735744.1382 | 1219175.0834 | 2735733.1542 | 1219167.6826 | 2735714.9614 | 1219148.4633 | 2735704.3431 | 1219143.6619 | 2735692.1669 | 1219142.9284 | 2735624.1357 | 1219147.5975
106 | 2735292.4501 | 1219214.3995 | 2735292.4576 | 1219214.3975 | 2735323.7814 | 1219210.0942 | 2735327.5587 | 1219209.5796 | 2735351.0737 | 1219209.4692 | 2735373.8352 | 1219206.773 | 2735391.35 | 1219201.0996 | 2735409.0774 | 1219188.7479 | 2735431.2918 | 1219175.0637 | 2735441.9698 | 1219171.5702 | 2735453.5334 | 1219169.1978 | 2735505.0401 | 1219152.7666 | 2735519.7657 | 1219149.8991 | 2735606.5305 | 1219148.8057 | 2735624.1357 | 1219147.5975
107 | 2735083.6891 | 1218853.1955 | 2735121.5207 | 1218876.3502 | 2735129.6876 | 1218882.8186 | 2735134.7801 | 1218887.9272 | 2735138.2524 | 1218893.4994 | 2735142.1037 | 1218896.0889 | 2735180.4934 | 1218912.0285
108 | 2735083.6891 | 1218853.1955 | 2735066.7221 | 1218844.4036 | 2735049.6096 | 1218843.6929 | 2735039.076 | 1218841.8082 | 2735030.4451 | 1218845.7491 | 2735028.908 | 1218846.3602
109 | 2735000.8509 | 1218846.7079 | 2735001.6023 | 1218846.0402 | 2735017.7959 | 1218850.7777 | 2735028.908 | 1218846.3602
110 | 2735000.8509 | 1218846.7079 | 2735000.4903 | 1218847.0282
111 | 2735072.5773 | 1218501.9873 | 2735085.4416 | 1218515.6235 | 2735104.8383 | 1218531.4875 | 2735119.2805 | 1218545.1818 | 2735124.3354 | 1218551.624 | 2735130.7568 | 1218562.0893 | 2735140.3977 | 1218570.8708 | 2735149.0405 | 1218575.1259 | 2735153.8058 | 1218578.9371 | 2735168.8469 | 1218600.3515 | 2735176.5386 | 1218607.6988 | 2735183.7265 | 1218612.1544 | 2735188.5126 | 1218613.3751 | 2735194.2488 | 1218613.8834 | 2735204.4205 | 1218611.6569 | 2735209.7704 | 1218611.7895 | 2735216.746 | 1218614.2276 | 2735221.9132 | 1218618.3927 | 2735225.2545 | 1218623.3838 | 2735234.0965 | 1218646.6036 | 2735235.186 | 1218656.8034 | 2735237.1415 | 1218659.9615 | 2735246.9733 | 1218666.6791 | 2735261.7261 | 1218671.6848 | 2735273.416 | 1218676.8211 | 2735281.4662 | 1218682.6957
112 | 2735072.5773 | 1218501.9873 | 2735069.4664 | 1218492.5201 | 2735056.3858 | 1218449.5882 | 2735046.278 | 1218414.8416 | 2735046.1592 | 1218408.7005 | 2735045.48 | 1218399.8111 | 2735044.3725 | 1218393.7366 | 2735041.3572 | 1218384.7386 | 2735036.8271 | 1218379.9209 | 2735022.6402 | 1218370.0134 | 2735014.0928 | 1218361.535 | 2735012.2826 | 1218355.9783 | 2735013.8932 | 1218352.5898 | 2735018.4573 | 1218351.8926 | 2735029.0898 | 1218355.481 | 2735048.5103 | 1218356.9334 | 2735057.3532 | 1218360.0808 | 2735084.2788 | 1218373.7803 | 2735097.816 | 1218383.206 | 2735124.2185 | 1218408.9037 | 2735141.223 | 1218426.8041 | 2735181.2967 | 1218451.3111 | 2735209.1651 | 1218484.315 | 2735243.3345 | 1218503.9845
113 | 2735000.4903 | 1218847.0282 | 2734996.8059 | 1218850.3017 | 2735001.0152 | 1218858.2036 | 2735011.9943 | 1218871.5745 | 2735009.6949 | 1218876.2151 | 2734998.4183 | 1218875.9594 | 2734940.7623 | 1218847.7857 | 2734914.9834 | 1218809.7038 | 2734895.7269 | 1218760.5273 | 2734891.2279 | 1218748.525
114 | 2735282.0351 | 1218683.1108 | 2735281.4662 | 1218682.6957
115 | 2735243.3345 | 1218503.9845 | 2735246.6102 | 1218509.8637 | 2735252.9878 | 1218517.2368 | 2735263.2951 | 1218522.7531 | 2735273.107 | 1218526.679 | 2735281.1426 | 1218530.9205 | 2735284.5755 | 1218535.2243 | 2735290.2912 | 1218540.6474
116 | 2734884.596 | 1218748.8101 | 2734891.0015 | 1218747.921 | 2734891.2279 | 1218748.525
117 | 2735218.7657 | 1218353.7919 | 2735198.8984 | 1218312.8296 | 2735194.8283 | 1218302.4731 | 2735191.5169 | 1218276.421 | 2735192.6968 | 1218267.9296 | 2735195.29 | 1218256.7237 | 2735196.3782 | 1218248.9308 | 2735195.497 | 1218237.9129
118 | 2735218.7657 | 1218353.7919 | 2735233.4591 | 1218368.4708 | 2735261.7837 | 1218394.4351 | 2735268.7133 | 1218398.9072 | 2735282.9389 | 1218403.106
119 | 2735195.497 | 1218237.9129 | 2735198.4761 | 1218240.1379 | 2735200.6229 | 1218244.2455 | 2735205.2913 | 1218263.0336 | 2735208.9238 | 1218273.2689 | 2735214.0646 | 1218280.2802 | 2735228.694 | 1218290.7653 | 2735250.7917 | 1218304.0667 | 2735285.6402 | 1218321.2942 | 2735306.8685 | 1218328.0707 | 2735318.0163 | 1218330.359 | 2735328.3984 | 1218330.595 | 2735344.0886 | 1218330.1399 | 2735354.9173 | 1218328.7625
120 | 2735195.497 | 1218237.9129 | 2735193.8457 | 1218218.0034 | 2735194.2951 | 1218206.2373 | 2735192.8043 | 1218201.3327 | 2735186.9295 | 1218194.2047 | 2735177.5261 | 1218179.2791 | 2735174.5845 | 1218170.3828 | 2735174.4143 | 1218163.4955 | 2735172.4362 | 1218157.9794 | 2735165.3619 | 1218146.8208 | 2735159.7113 | 1218133.4928 | 2735158.4255 | 1218126.9138 | 2735159.1026 | 1218121.1688 | 2735166.4783 | 1218104.667 | 2735168.1335 | 1218099.3224 | 2735168.1875 | 1218096.2766 | 2735166.4196 | 1218091.199 | 2735163.6344 | 1218085.7758 | 2735162.3201 | 1218080.1191 | 2735161.5647 | 1218068.5703 | 2735160.2764 | 1218062.436 | 2735165.7842 | 1218062.9947 | 2735169.0747 | 1218065.8939 | 2735172.594 | 1218074.4364 | 2735175.0003 | 1218077.4824 | 2735178.6596 | 1218079.8562 | 2735185.1616 | 1218081.772 | 2735198.0385 | 1218090.8716 | 2735202.5217 | 1218096.0887 | 2735205.6017 | 1218100.5623 | 2735208.7176 | 1218103.4576 | 2735221.6583 | 1218109.7453 | 2735237.0012 | 1218119.2569 | 2735242.786 | 1218121.3232
121 | 2735306.4254 | 1218544.2951 | 2735300.6343 | 1218544.5855 | 2735296.4123 | 1218543.5999 | 2735290.2912 | 1218540.6474
122 | 2735242.786 | 1218121.3232 | 2735257.1328 | 1218154.2871 | 2735275.1853 | 1218185.5671 | 2735286.8967 | 1218196.8201 | 2735309.2438 | 1218214.8646 | 2735313.4102 | 1218217.3056 | 2735319.975 | 1218217.4548
123 | 2735242.786 | 1218121.3232 | 2735253.3961 | 1218121.5642 | 2735267.7659 | 1218119.422 | 2735282.0092 | 1218115.164 | 2735288.0243 | 1218114.778 | 2735302.8616 | 1218115.4599 | 2735322.9174 | 1218112.0459 | 2735332.0101 | 1218108.8942 | 2735342.9152 | 1218103.5041 | 2735354.4899 | 1218100.0642 | 2735374.0987 | 1218092.9371 | 2735391.8991 | 1218087.8706 | 2735405.3026 | 1218081.481 | 2735414.5005 | 1218079.0436 | 2735423.3854 | 1218081.3585 | 2735472.1872 | 1218086.0939 | 2735481.6237 | 1218083.1838 | 2735496.7499 | 1218073.5087 | 2735509.3394 | 1218069.525 | 2735592.9471 | 1218056.7052
124 | 2735056.3833 | 1219063.8498 | 2735060.5069 | 1219067.1465 | 2735072.3763 | 1219069.4868
125 | 2735298.5966 | 1219181.3789 | 2735278.5619 | 1219182.9337
126 | 2735318.3279 | 1219179.8476 | 2735298.5966 | 1219181.3789
127 | 2735239.9194 | 1219185.6013 | 2735243.8695 | 1219185.6261 | 2735278.5619 | 1219182.9337
128 | 2735318.905 | 1219179.8028 | 2735318.3279 | 1219179.8476
129 | 2735219.5156 | 1219185.4733 | 2735239.9194 | 1219185.6013
130 | 2735072.3763 | 1219069.4868 | 2735091.927 | 1219073.3418 | 2735127.0744 | 1219094.9455 | 2735135.7207 | 1219090.9828 | 2735139.1464 | 1219083.5544 | 2735134.0708 | 1219073.6978 | 2735125.5505 | 1219067.8107
131 | 2735153.0365 | 1219243.0504 | 2735142.0966 | 1219241.8743 | 2735108.087 | 1219246.7847 | 2735100.0385 | 1219248.9351
132 | 2735087.2255 | 1219253.6793 | 2735089.3274 | 1219251.7968 | 2735100.0385 | 1219248.9351
133 | 2735533.1156 | 1218124.8558 | 2735518.2903 | 1218137.9962 | 2735509.1759 | 1218152.8703
134 | 2735592.9471 | 1218056.7052 | 2735558.8631 | 1218093.2487 | 2735547.6609 | 1218106.6717 | 2735540.3317 | 1218113.7441 | 2735533.1156 | 1218124.8558
135 | 2735507.2889 | 1218155.9497 | 2735507.2889 | 1218155.9497 | 2735509.1759 | 1218152.8703
136 | 2735471.576 | 1218208.9448 | 2735466.3599 | 1218198.3652 | 2735490.126 | 1218178.389 | 2735507.2889 | 1218155.9497
137 | 2735472.6311 | 1218211.0849 | 2735471.576 | 1218208.9448
138 | 2734820.3966 | 1219077.8727 | 2734817.4857 | 1219063.5951 | 2734814.7606 | 1219061.1093

## bus_geodata
| x | y | coords
0 | 2735219.8971 | 1219485.9413
1 | 2735217.9725 | 1219443.5148
2 | 2735609.2822 | 1219377.6134
3 | 2735064.9421 | 1219399.6883
4 | 2735314.7495 | 1219377.6387
5 | 2735000.2423 | 1219302.0635
6 | 2735115.9954 | 1219386.3963
7 | 2735216.6018 | 1219439.6949
8 | 2735657.4198 | 1219392.732
9 | 2735470.6272 | 1219329.1521
10 | 2735214.3252 | 1219422.7095
11 | 2735036.0291 | 1219286.7145
12 | 2734854.9939 | 1219155.7045
13 | 2734849.7513 | 1219150.1189
14 | 2735214.7797 | 1219433.2212
15 | 2735509.8279 | 1219317.0332
16 | 2734611.8299 | 1218693.5292
17 | 2734607.7274 | 1218639.2363
18 | 2734652.6587 | 1218659.1457
19 | 2734672.388 | 1218661.4376
20 | 2734796.9143 | 1218801.2356
21 | 2734630.0082 | 1218323.2119
22 | 2734749.3825 | 1218896.2832
23 | 2734792.5131 | 1218838.0108
24 | 2734863.5992 | 1218825.7556
25 | 2734747.6936 | 1218861.3689
26 | 2734697.9989 | 1218080.0164
27 | 2734691.1739 | 1218663.6199
28 | 2734692.1719 | 1218651.0544
29 | 2734794.9231 | 1219043.0135
30 | 2734882.3002 | 1218833.0498
31 | 2734747.12 | 1218855.0203
32 | 2735874.9374 | 1218752.9631
33 | 2735899.2438 | 1218712.4917
34 | 2735884.6985 | 1218772.5986
35 | 2735851.082 | 1218572.4665
36 | 2735736.9238 | 1218595.1797
37 | 2735705.798 | 1218599.8785
38 | 2735850.48 | 1218968.9124
39 | 2735874.2769 | 1218963.6459
40 | 2735753.9474 | 1218955.049
41 | 2735890.9912 | 1218968.5643
42 | 2735722.4319 | 1218943.9976
43 | 2735928.2878 | 1218984.105
44 | 2735684.202 | 1218966.7583
45 | 2735677.0247 | 1218951.0012
46 | 2736004.4413 | 1218983.65
47 | 2735447.9251 | 1218967.0598
48 | 2735954.0887 | 1218967.8061
49 | 2735906.7483 | 1218929.209
50 | 2735957.5992 | 1218891.3821
51 | 2735196.2568 | 1218872.1755
52 | 2735624.6275 | 1218629.883
53 | 2735597.3618 | 1218438.3318
54 | 2735499.8089 | 1218674.3928
55 | 2735558.5537 | 1218479.7273
56 | 2735465.051 | 1218434.694
57 | 2735460.6917 | 1218698.4381
58 | 2735545.276 | 1218490.4993
59 | 2735309.1421 | 1218477.6012
60 | 2735509.0937 | 1218723.8486
61 | 2735516.9389 | 1218746.112
62 | 2735549.15 | 1218748.9693
63 | 2735162.1453 | 1219199.1811
64 | 2735178.1218 | 1219212.6128
65 | 2735149.2192 | 1219188.3138
66 | 2735200.3791 | 1219239.5836
67 | 2735144.7546 | 1219187.9288
68 | 2735165.5208 | 1219185.2888
69 | 2735193.5024 | 1219241.8006
70 | 2735208.6614 | 1219237.5512
71 | 2735117.5347 | 1219185.5818
72 | 2735183.8706 | 1219185.2496
73 | 2735181.3863 | 1219244.3542
74 | 2735216.2568 | 1219235.6874
75 | 2735114.9096 | 1219185.3554
76 | 2735207.4804 | 1219185.3977
77 | 2735073.7552 | 1219175.225
78 | 2735118.0148 | 1219170.9695
79 | 2735041.6785 | 1219061.4808
80 | 2735047.8753 | 1219176.316
81 | 2735124.5491 | 1219163.5472
82 | 2735039.316 | 1219054.8116
83 | 2735035.0282 | 1219175.8921
84 | 2735134.2164 | 1219152.5662
85 | 2735221.9462 | 1219234.1043
86 | 2735240.3853 | 1219228.9497
87 | 2735246.6992 | 1219227.1847
88 | 2735177.2779 | 1219245.1103
89 | 2735267.3092 | 1219221.4245
90 | 2735169.6751 | 1219145.5793
91 | 2735171.4368 | 1219141.0232
92 | 2735136.1267 | 1219140.3216
93 | 2735120.3117 | 1219132.6566
94 | 2735916.0068 | 1219137.0164
95 | 2735893.6373 | 1219127.3853
96 | 2735834.2286 | 1219137.3721
97 | 2735624.1357 | 1219147.5975
98 | 2735292.4501 | 1219214.3995
99 | 2735180.4934 | 1218912.0285
100 | 2735083.6891 | 1218853.1955
101 | 2735028.908 | 1218846.3602
102 | 2735000.8509 | 1218846.7079
103 | 2735072.5773 | 1218501.9873
104 | 2735000.4903 | 1218847.0282
105 | 2735281.4662 | 1218682.6957
106 | 2735243.3345 | 1218503.9845
107 | 2734891.2279 | 1218748.525
108 | 2734884.596 | 1218748.8101
109 | 2735003.1213 | 1218990.5227
110 | 2735218.7658 | 1218353.7919
111 | 2735195.4969 | 1218237.9129
112 | 2735282.9389 | 1218403.106
113 | 2735290.2912 | 1218540.6474
114 | 2735354.9173 | 1218328.7625
115 | 2735242.786 | 1218121.3232
116 | 2735306.4254 | 1218544.2951
117 | 2734992.2546 | 1219203.3454
118 | 2735056.3833 | 1219063.8498
119 | 2735298.5966 | 1219181.3789
120 | 2735278.5619 | 1219182.9337
121 | 2735318.3279 | 1219179.8476
122 | 2735239.9194 | 1219185.6013
123 | 2735318.905 | 1219179.8028
124 | 2735219.5156 | 1219185.4733
125 | 2735072.3763 | 1219069.4868
126 | 2735125.5505 | 1219067.8107
127 | 2735153.0365 | 1219243.0504
128 | 2735100.0385 | 1219248.9351
129 | 2735087.2255 | 1219253.6793
130 | 2735533.1156 | 1218124.8558
131 | 2735509.1759 | 1218152.8703
132 | 2735592.9471 | 1218056.7052
133 | 2735507.2889 | 1218155.9497
134 | 2735471.576 | 1218208.9448
135 | 2735319.975 | 1218217.4548
136 | 2735472.6311 | 1218211.0849
137 | 2734814.7606 | 1219061.1093
138 | 2735282.0351 | 1218683.1108
139 | 2734820.3966 | 1219077.8727
140 | 2735134.2164 | 1219152.5662

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1