## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3341-20_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3341-20_0_4_node_5 | 0.4 | n |  | TRUE
2 | bus_LV_3341-20_0_4_node_63 | 0.4 | n |  | TRUE
3 | bus_LV_3341-20_0_4_node_62 | 0.4 | n |  | TRUE
4 | bus_LV_3341-20_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_3341-20_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_3341-20_0_4_node_66 | 0.4 | n |  | TRUE
7 | bus_LV_3341-20_0_4_node_65 | 0.4 | n |  | TRUE
8 | bus_LV_3341-20_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_3341-20_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_3341-20_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_3341-20_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_3341-20_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_3341-20_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_3341-20_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_3341-20_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_3341-20_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_3341-20_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_3341-20_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_3341-20_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_3341-20_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_3341-20_0_4_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_3341-20_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_3341-20_0_4_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_3341-20_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_3341-20_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_3341-20_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_3341-20_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_3341-20_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_3341-20_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_3341-20_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_3341-20_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_3341-20_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_3341-20_0_4_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_3341-20_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_3341-20_0_4_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_3341-20_0_4_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_3341-20_0_4_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_3341-20_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_3341-20_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_3341-20_0_4_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_3341-20_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_3341-20_0_4_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_3341-20_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_3341-20_0_4_node_81 | 0.4 | n |  | TRUE
45 | bus_LV_3341-20_0_4_node_82 | 0.4 | n |  | TRUE
46 | bus_LV_3341-20_0_4_node_84 | 0.4 | n |  | TRUE
47 | bus_LV_3341-20_0_4_node_83 | 0.4 | n |  | TRUE
48 | bus_LV_3341-20_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_3341-20_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_3341-20_0_4_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_3341-20_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_3341-20_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_3341-20_0_4_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_3341-20_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_3341-20_0_4_node_78 | 0.4 | n |  | TRUE
56 | bus_LV_3341-20_0_4_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_3341-20_0_4_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_3341-20_0_4_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_3341-20_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_3341-20_0_4_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_3341-20_0_4_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_3341-20_0_4_node_70 | 0.4 | n |  | TRUE
63 | bus_LV_3341-20_0_4_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_3341-20_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_3341-20_0_4_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_3341-20_0_4_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_3341-20_0_4_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_3341-20_0_4_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_3341-20_0_4_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_3341-20_0_4_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_3341-20_0_4_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_3341-20_0_4_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_3341-20_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_3341-20_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_3341-20_0_4_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_3341-20_0_4_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_3341-20_0_4_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_3341-20_0_4_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_3341-20_0_4_node_73 | 0.4 | n |  | TRUE
80 | bus_LV_3341-20_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_3341-20_0_4_node_80 | 0.4 | n |  | TRUE
82 | bus_MV_10_1_node_145 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3341-20_0_4_load_0 | 0 | 0.0019477 | 0.00048814 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3341-20_0_4_load_5 | 1 | 0.0014141 | 0.00035441 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3341-20_0_4_load_63 | 2 | 0.0081368 | 0.0020393 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3341-20_0_4_load_62 | 3 | 0.0043987 | 0.0011024 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3341-20_0_4_load_2 | 4 | 0.0032961 | 0.00082608 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3341-20_0_4_load_3 | 5 | 0.0026344 | 0.00066025 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3341-20_0_4_load_66 | 6 | 0.0040937 | 0.001026 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3341-20_0_4_load_65 | 7 | 0.0033207 | 0.00083225 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3341-20_0_4_load_6 | 8 | 0.0023633 | 0.0005923 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3341-20_0_4_load_9 | 10 | 0.0032412 | 0.00081231 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3341-20_0_4_load_12 | 11 | 0.00074405 | 0.00018648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3341-20_0_4_load_18 | 12 | 0.001486 | 0.00037244 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3341-20_0_4_load_10 | 13 | 0.0025564 | 0.00064068 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3341-20_0_4_load_11 | 14 | 0.002554 | 0.0006401 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3341-20_0_4_load_13 | 15 | 0.0028973 | 0.00072612 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3341-20_0_4_load_14 | 16 | 0.0029144 | 0.00073042 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3341-20_0_4_load_16 | 17 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3341-20_0_4_load_17 | 19 | 0.0026615 | 0.00066704 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3341-20_0_4_load_26 | 22 | 0.002438 | 0.00061101 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3341-20_0_4_load_28 | 23 | 0.0026068 | 0.00065334 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3341-20_0_4_load_25 | 25 | 0.0015558 | 0.00038992 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3341-20_0_4_load_20 | 26 | 0.0024456 | 0.00061292 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3341-20_0_4_load_21 | 27 | 0.0023448 | 0.00058767 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3341-20_0_4_load_22 | 28 | 0.0041528 | 0.0010408 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3341-20_0_4_load_23 | 29 | 0.0021829 | 0.0005471 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3341-20_0_4_load_24 | 30 | 0.0021859 | 0.00054783 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3341-20_0_4_load_30 | 31 | 0.0042665 | 0.0010693 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3341-20_0_4_load_43 | 32 | 0.0041412 | 0.0010379 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3341-20_0_4_load_39 | 33 | 0.0019917 | 0.00049916 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3341-20_0_4_load_31 | 34 | 0.0037651 | 0.00094361 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3341-20_0_4_load_46 | 35 | 0.0066324 | 0.0016622 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3341-20_0_4_load_40 | 36 | 0.0024144 | 0.0006051 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3341-20_0_4_load_32 | 37 | 0.0054276 | 0.0013603 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3341-20_0_4_load_33 | 38 | 0.0061096 | 0.0015312 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3341-20_0_4_load_34 | 39 | 0.002222 | 0.00055689 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3341-20_0_4_load_36 | 40 | 0.0033538 | 0.00084054 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3341-20_0_4_load_37 | 41 | 0.0023534 | 0.00058983 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3341-20_0_4_load_38 | 42 | 0.0011046 | 0.00027684 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3341-20_0_4_load_35 | 43 | 0.0021703 | 0.00054393 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3341-20_0_4_load_81 | 44 | 0.0033183 | 0.00083164 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3341-20_0_4_load_82 | 45 | 0.002112 | 0.00052932 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3341-20_0_4_load_84 | 46 | 0.0050164 | 0.0012572 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3341-20_0_4_load_41 | 48 | 0.0033884 | 0.00084921 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3341-20_0_4_load_42 | 49 | 0.0023858 | 0.00059795 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3341-20_0_4_load_44 | 50 | 0.0033075 | 0.00082895 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3341-20_0_4_load_45 | 51 | 0.0024166 | 0.00060566 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3341-20_0_4_load_47 | 52 | 0.0015434 | 0.00038681 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3341-20_0_4_load_77 | 53 | 0.0023414 | 0.0005868 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3341-20_0_4_load_48 | 54 | 0.0027317 | 0.00068462 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3341-20_0_4_load_50 | 57 | 0.0055643 | 0.0013946 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3341-20_0_4_load_51 | 58 | 0.0019976 | 0.00050063 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3341-20_0_4_load_52 | 59 | 0.0029228 | 0.00073252 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3341-20_0_4_load_53 | 60 | 0.0017466 | 0.00043773 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3341-20_0_4_load_55 | 63 | 0.0023052 | 0.00057774 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3341-20_0_4_load_56 | 64 | 0.0030579 | 0.00076638 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3341-20_0_4_load_72 | 65 | 0.006857 | 0.0017185 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3341-20_0_4_load_57 | 66 | 0.0040521 | 0.0010155 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3341-20_0_4_load_59 | 68 | 0.0023383 | 0.00058603 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3341-20_0_4_load_67 | 69 | 0.0034512 | 0.00086494 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3341-20_0_4_load_68 | 70 | 0.002195 | 0.00055011 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3341-20_0_4_load_69 | 72 | 0.0039019 | 0.0009779 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3341-20_0_4_load_64 | 73 | 0.0029213 | 0.00073216 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3341-20_0_4_load_61 | 74 | 0.007361 | 0.0018448 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3341-20_0_4_load_71 | 75 | 0.0043386 | 0.0010874 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3341-20_0_4_load_74 | 76 | 0.0046465 | 0.0011645 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3341-20_0_4_load_75 | 77 | 0.0036389 | 0.00091199 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3341-20_0_4_load_76 | 78 | 0.0043284 | 0.0010848 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3341-20_0_4_load_73 | 79 | 0.0039731 | 0.00099575 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3341-20_0_4_load_79 | 80 | 0.0028174 | 0.0007061 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3341-20_0_4_load_80 | 81 | 0.0028328 | 0.00070997 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3341-20_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.088143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3341-20_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.10276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3341-20_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.045706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3341-20_0_4_line_3 | NAYY 4x150 SE | 3 | 74 | 0.01802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3341-20_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.027084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3341-20_0_4_line_5 | NAYY 4x150 SE | 5 | 6 | 0.011041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3341-20_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.017713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3341-20_0_4_line_7 | NAYY 4x150 SE | 7 | 73 | 0.010087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3341-20_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.017803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3341-20_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.045903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3341-20_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.0090568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3341-20_0_4_line_11 | NAYY 4x150 SE | 11 | 12 | 0.00010791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3341-20_0_4_line_12 | NAYY 4x150 SE | 12 | 17 | 0.0075165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3341-20_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.012161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3341-20_0_4_line_14 | NAYY 4x150 SE | 14 | 15 | 0.010981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3341-20_0_4_line_15 | NAYY 4x150 SE | 15 | 16 | 0.021388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3341-20_0_4_line_16 | NAYY 4x150 SE | 16 | 18 | 0.027265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3341-20_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.0063852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3341-20_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.018407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3341-20_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.016337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3341-20_0_4_line_20 | NAYY 4x150 SE | 20 | 21 | 0.031172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3341-20_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.016981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3341-20_0_4_line_22 | NAYY 4x150 SE | 21 | 23 | 0.019297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3341-20_0_4_line_23 | NAYY 4x150 SE | 21 | 24 | 0.012172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3341-20_0_4_line_24 | NAYY 4x150 SE | 22 | 25 | 0.024053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3341-20_0_4_line_25 | NAYY 4x150 SE | 23 | 31 | 0.0018828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3341-20_0_4_line_26 | NAYY 4x150 SE | 24 | 32 | 0.027102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3341-20_0_4_line_27 | NAYY 4x150 SE | 24 | 33 | 0.011733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3341-20_0_4_line_28 | NAYY 4x150 SE | 25 | 30 | 0.0072753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3341-20_0_4_line_29 | NAYY 4x150 SE | 26 | 27 | 0.022884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3341-20_0_4_line_30 | NAYY 4x150 SE | 26 | 28 | 0.040216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3341-20_0_4_line_31 | NAYY 4x150 SE | 27 | 29 | 0.013546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3341-20_0_4_line_32 | NAYY 4x150 SE | 29 | 30 | 0.0087355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3341-20_0_4_line_33 | NAYY 4x150 SE | 31 | 34 | 0.026877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3341-20_0_4_line_34 | NAYY 4x150 SE | 32 | 35 | 0.034554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3341-20_0_4_line_35 | NAYY 4x150 SE | 33 | 36 | 0.030185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_3341-20_0_4_line_36 | NAYY 4x150 SE | 34 | 37 | 0.021846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3341-20_0_4_line_37 | NAYY 4x150 SE | 35 | 53 | 0.0051746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3341-20_0_4_line_38 | NAYY 4x150 SE | 36 | 48 | 0.016434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_3341-20_0_4_line_39 | NAYY 4x150 SE | 36 | 49 | 0.025663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3341-20_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.014293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3341-20_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.017017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3341-20_0_4_line_42 | NAYY 4x150 SE | 39 | 43 | 0.012148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3341-20_0_4_line_43 | NAYY 4x150 SE | 40 | 41 | 0.0014737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3341-20_0_4_line_44 | NAYY 4x150 SE | 40 | 42 | 0.063913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3341-20_0_4_line_45 | NAYY 4x150 SE | 42 | 46 | 0.07173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3341-20_0_4_line_46 | NAYY 4x150 SE | 43 | 44 | 0.010252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3341-20_0_4_line_47 | NAYY 4x150 SE | 44 | 45 | 0.01093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3341-20_0_4_line_48 | NAYY 4x150 SE | 46 | 47 | 0.005685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3341-20_0_4_line_49 | NAYY 4x150 SE | 47 | 81 | 0.015821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3341-20_0_4_line_50 | NAYY 4x150 SE | 48 | 50 | 0.0091227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_3341-20_0_4_line_51 | NAYY 4x150 SE | 49 | 51 | 0.006329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3341-20_0_4_line_52 | NAYY 4x150 SE | 50 | 52 | 0.016053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_3341-20_0_4_line_53 | NAYY 4x150 SE | 52 | 54 | 0.01034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3341-20_0_4_line_54 | NAYY 4x150 SE | 53 | 55 | 0.012866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3341-20_0_4_line_55 | NAYY 4x150 SE | 54 | 56 | 0.013846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3341-20_0_4_line_56 | NAYY 4x150 SE | 55 | 80 | 0.039896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3341-20_0_4_line_57 | NAYY 4x150 SE | 56 | 57 | 0.0063338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3341-20_0_4_line_58 | NAYY 4x150 SE | 56 | 58 | 0.015117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3341-20_0_4_line_59 | NAYY 4x150 SE | 57 | 59 | 0.024835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3341-20_0_4_line_60 | NAYY 4x150 SE | 58 | 60 | 0.004539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3341-20_0_4_line_61 | NAYY 4x150 SE | 59 | 61 | 0.0071056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3341-20_0_4_line_62 | NAYY 4x150 SE | 60 | 62 | 0.0035412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3341-20_0_4_line_63 | NAYY 4x150 SE | 61 | 63 | 0.0089986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3341-20_0_4_line_64 | NAYY 4x150 SE | 61 | 64 | 0.014856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3341-20_0_4_line_65 | NAYY 4x150 SE | 62 | 65 | 0.020094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3341-20_0_4_line_66 | NAYY 4x150 SE | 63 | 66 | 0.02811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3341-20_0_4_line_67 | NAYY 4x150 SE | 64 | 67 | 0.010622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3341-20_0_4_line_68 | NAYY 4x150 SE | 65 | 75 | 0.013825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3341-20_0_4_line_69 | NAYY 4x150 SE | 66 | 68 | 0.0066965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3341-20_0_4_line_70 | NAYY 4x150 SE | 67 | 69 | 0.017168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3341-20_0_4_line_71 | NAYY 4x150 SE | 67 | 70 | 0.012726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3341-20_0_4_line_72 | NAYY 4x150 SE | 68 | 71 | 0.0095158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3341-20_0_4_line_73 | NAYY 4x150 SE | 69 | 72 | 0.026059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3341-20_0_4_line_74 | NAYY 4x150 SE | 71 | 73 | 0.0077082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3341-20_0_4_line_75 | NAYY 4x150 SE | 71 | 74 | 0.034745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3341-20_0_4_line_76 | NAYY 4x150 SE | 75 | 76 | 0.032145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3341-20_0_4_line_77 | NAYY 4x150 SE | 76 | 77 | 0.031047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3341-20_0_4_line_78 | NAYY 4x150 SE | 76 | 79 | 0.022225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3341-20_0_4_line_79 | NAYY 4x150 SE | 77 | 78 | 0.011136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3341-20_0_4_line_80 | NAYY 4x150 SE | 80 | 81 | 0.018841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3341-20_0_4_trafo_44 | 0.25 MVA 20/0.4 kV | 82 | 50 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2720306.2984 | 1233052.745 | 2720387.2383 | 1233017.8471
1 | 2720478.3638 | 1233065.3513 | 2720387.2383 | 1233017.8471
2 | 2720478.3638 | 1233065.3513 | 2720484.2773 | 1233069.152 | 2720488.5679 | 1233067.8379 | 2720491.7905 | 1233064.2893 | 2720504.1092 | 1233048.7821 | 2720509.7712 | 1233041.0414
3 | 2720522.5486 | 1233028.7398 | 2720522.5486 | 1233028.7398 | 2720518.7175 | 1233030.9194 | 2720514.9212 | 1233034.0005 | 2720509.7712 | 1233041.0414
4 | 2720521.7046 | 1233084.3662 | 2720504.9531 | 1233105.6488
5 | 2720521.7046 | 1233084.3662 | 2720528.5333 | 1233075.6904
6 | 2720539.4886 | 1233061.7717 | 2720528.5333 | 1233075.6904
7 | 2720539.4886 | 1233061.7717 | 2720545.7273 | 1233053.8455
8 | 2720561.8756 | 1232783.7289 | 2720553.0122 | 1232787.9303 | 2720545.1209 | 1232786.6532
9 | 2720561.8756 | 1232783.7289 | 2720573.2527 | 1232784.7939 | 2720570.2284 | 1232789.0137 | 2720575.441 | 1232790.4205 | 2720581.4633 | 1232796.3364 | 2720586.2095 | 1232800.5694 | 2720590.6918 | 1232808.4704
10 | 2720595.6826 | 1232815.9351 | 2720594.0848 | 1232814.4514 | 2720590.6918 | 1232808.4704
11 | 2720595.6826 | 1232815.9351 | 2720595.7617 | 1232816.0085
12 | 2720595.7617 | 1232816.0085 | 2720601.2698 | 1232821.123
13 | 2720644.8789 | 1232780.5604 | 2720647.4559 | 1232778.0051 | 2720652.8577 | 1232771.4016
14 | 2720644.8789 | 1232780.5604 | 2720637.0816 | 1232788.2919
15 | 2720637.0816 | 1232788.2919 | 2720621.8942 | 1232803.3512
16 | 2720605.949 | 1232825.4677 | 2720621.8942 | 1232803.3512 | 2720621.8942 | 1232803.3512
17 | 2720605.949 | 1232825.4677 | 2720601.2698 | 1232821.123
18 | 2720605.949 | 1232825.4677 | 2720618.8392 | 1232838.6078
19 | 2720630.2799 | 1232850.2702 | 2720618.8392 | 1232838.6078
20 | 2720630.2799 | 1232850.2702 | 2720654.6807 | 1232869.7589
21 | 2720630.2799 | 1232850.2702 | 2720618.3412 | 1232862.3455
22 | 2720654.6807 | 1232869.7589 | 2720666.7495 | 1232854.7015
23 | 2720658.1342 | 1232881.3272 | 2720657.1012 | 1232875.1346 | 2720654.6807 | 1232869.7589
24 | 2720601.4305 | 1232879.4497 | 2720618.3412 | 1232862.3455
25 | 2720667.927 | 1232853.2323 | 2720666.7495 | 1232854.7015
26 | 2720658.1342 | 1232881.3272 | 2720666.6215 | 1232885.5696 | 2720676.5423 | 1232893.811 | 2720680.0948 | 1232896.9125
27 | 2720658.1342 | 1232881.3272 | 2720657.7449 | 1232887.0684 | 2720655.0373 | 1232892.3988
28 | 2720601.4305 | 1232879.4497 | 2720596.3154 | 1232884.6233
29 | 2720580.6496 | 1232900.4683 | 2720564.5606 | 1232916.7413
30 | 2720541.8934 | 1232949.5349 | 2720545.0885 | 1232943.2391 | 2720554.3925 | 1232927.0258 | 2720564.5606 | 1232916.7413
31 | 2720580.6496 | 1232900.4683 | 2720590.1737 | 1232890.8353
32 | 2720590.1737 | 1232890.8353 | 2720596.3154 | 1232884.6233
33 | 2720667.927 | 1232853.2323 | 2720684.7364 | 1232832.2601
34 | 2720707.7947 | 1232917.2471 | 2720707.0656 | 1232916.8715 | 2720695.9206 | 1232910.7292 | 2720680.0948 | 1232896.9125
35 | 2720640.8348 | 1232919.0287 | 2720649.3586 | 1232903.5781 | 2720655.0373 | 1232892.3988
36 | 2720684.7364 | 1232832.2601 | 2720698.3994 | 1232815.2137
37 | 2720712.3949 | 1232919.6166 | 2720707.7947 | 1232917.2471
38 | 2720640.8348 | 1232919.0287 | 2720631.9074 | 1232932.8267
39 | 2720640.8348 | 1232919.0287 | 2720664.8998 | 1232924.833 | 2720665.6094 | 1232924.2673
40 | 2720698.3994 | 1232815.2137 | 2720698.3994 | 1232815.2137 | 2720709.3066 | 1232824.4508
41 | 2720709.3066 | 1232824.4508 | 2720722.2927 | 1232835.4485 | 2720722.2927 | 1232835.4485
42 | 2720722.2927 | 1232835.4485 | 2720714.7207 | 1232844.9473
43 | 2720750.5315 | 1232731.7051 | 2720751.9033 | 1232732.2436
44 | 2720751.9033 | 1232732.2436 | 2720778.8196 | 1232790.2129
45 | 2720761.9439 | 1232859.9292 | 2720778.8196 | 1232790.2129
46 | 2720708.3306 | 1232852.9636 | 2720714.7207 | 1232844.9473
47 | 2720708.3306 | 1232852.9636 | 2720701.5173 | 1232861.5106
48 | 2720765.9438 | 1232863.9804 | 2720761.9439 | 1232859.9292
49 | 2720765.9438 | 1232863.9804 | 2720757.008 | 1232877.0362
50 | 2720626.9519 | 1232940.4861 | 2720631.9074 | 1232932.8267
51 | 2720670.5582 | 1232920.322 | 2720665.6094 | 1232924.2673
52 | 2720626.9519 | 1232940.4861 | 2720618.2315 | 1232953.9642
53 | 2720612.6147 | 1232962.6455 | 2720618.2315 | 1232953.9642
54 | 2720723.8325 | 1232925.5079 | 2720712.3949 | 1232919.6166
55 | 2720605.0935 | 1232974.2701 | 2720612.6147 | 1232962.6455
56 | 2720723.8325 | 1232925.5079 | 2720746.3662 | 1232892.5846
57 | 2720605.0935 | 1232974.2701 | 2720601.6534 | 1232979.5882
58 | 2720605.0935 | 1232974.2701 | 2720618.4638 | 1232981.3246
59 | 2720601.6534 | 1232979.5882 | 2720600.23 | 1232981.7886 | 2720586.8613 | 1232999.5302
60 | 2720618.4638 | 1232981.3246 | 2720622.4783 | 1232983.4427
61 | 2720582.5851 | 1233005.2051 | 2720586.8613 | 1232999.5302
62 | 2720625.6104 | 1232985.0952 | 2720622.4783 | 1232983.4427
63 | 2720582.5851 | 1233005.2051 | 2720577.1695 | 1233012.3916
64 | 2720582.5851 | 1233005.2051 | 2720595.3346 | 1233012.8316
65 | 2720625.6104 | 1232985.0952 | 2720636.7078 | 1232990.9585 | 2720643.2667 | 1232994.6835
66 | 2720577.1695 | 1233012.3916 | 2720560.2518 | 1233034.841
67 | 2720604.5674 | 1233018.0837 | 2720595.882 | 1233013.159 | 2720595.3346 | 1233012.8316
68 | 2720642.5321 | 1233007.8729 | 2720642.9729 | 1233006.9096 | 2720644.3355 | 1233001.7219 | 2720644.6538 | 1232997.2359 | 2720643.2667 | 1232994.6835 | 2720643.2667 | 1232994.6835
69 | 2720560.2518 | 1233034.841 | 2720556.2217 | 1233040.1889
70 | 2720604.5674 | 1233018.0837 | 2720606.1785 | 1233020.0513 | 2720605.0255 | 1233025.7324 | 2720604.8878 | 1233030.2778 | 2720606.0851 | 1233033.2266 | 2720607.0053 | 1233033.8245
71 | 2720604.5674 | 1233018.0837 | 2720610.4287 | 1233015.8786 | 2720613.838 | 1233012.0892 | 2720614.6073 | 1233010.9606
72 | 2720550.4948 | 1233047.7885 | 2720556.2217 | 1233040.1889
73 | 2720607.0053 | 1233033.8245 | 2720608.2229 | 1233034.6156 | 2720612.8376 | 1233036.3662 | 2720621.4649 | 1233037.8091 | 2720624.1822 | 1233037.1415 | 2720626.8206 | 1233033.6477 | 2720628.4298 | 1233030.2622
74 | 2720550.4948 | 1233047.7885 | 2720545.7273 | 1233053.8455
75 | 2720550.4948 | 1233047.7885 | 2720526.2208 | 1233028.414 | 2720522.5486 | 1233028.7398
76 | 2720642.5321 | 1233007.8729 | 2720665.0594 | 1233030.8033
77 | 2720665.0594 | 1233030.8033 | 2720648.2451 | 1233056.9028
78 | 2720679.3047 | 1233014.673 | 2720675.317 | 1233015.9957 | 2720669.9836 | 1233023.1598 | 2720665.0594 | 1233030.8033
79 | 2720642.2141 | 1233066.2642 | 2720648.2451 | 1233056.9028
80 | 2720746.3662 | 1232892.5846 | 2720757.008 | 1232877.0362

## bus_geodata
| x | y | coords
0 | 2720387.2383 | 1233017.8471
1 | 2720306.2984 | 1233052.745
2 | 2720478.3638 | 1233065.3513
3 | 2720509.7712 | 1233041.0414
4 | 2720504.9531 | 1233105.6488
5 | 2720521.7046 | 1233084.3662
6 | 2720528.5333 | 1233075.6904
7 | 2720539.4886 | 1233061.7717
8 | 2720545.1209 | 1232786.6532
9 | 2720561.8756 | 1232783.7289
10 | 2720590.6918 | 1232808.4704
11 | 2720595.6826 | 1232815.9351
12 | 2720595.7617 | 1232816.0085
13 | 2720652.8577 | 1232771.4016
14 | 2720644.8789 | 1232780.5604
15 | 2720637.0816 | 1232788.2919
16 | 2720621.8942 | 1232803.3512
17 | 2720601.2698 | 1232821.123
18 | 2720605.949 | 1232825.4677
19 | 2720618.8392 | 1232838.6078
20 | 2720630.2799 | 1232850.2702
21 | 2720654.6807 | 1232869.7589
22 | 2720618.3412 | 1232862.3455
23 | 2720666.7494 | 1232854.7015
24 | 2720658.1342 | 1232881.3272
25 | 2720601.4305 | 1232879.4497
26 | 2720564.5606 | 1232916.7413
27 | 2720580.6496 | 1232900.4683
28 | 2720541.8934 | 1232949.5349
29 | 2720590.1737 | 1232890.8353
30 | 2720596.3154 | 1232884.6233
31 | 2720667.927 | 1232853.2323
32 | 2720680.0948 | 1232896.9125
33 | 2720655.0372 | 1232892.3988
34 | 2720684.7364 | 1232832.2601
35 | 2720707.7946 | 1232917.2471
36 | 2720640.8348 | 1232919.0287
37 | 2720698.3994 | 1232815.2137
38 | 2720709.3066 | 1232824.4508
39 | 2720722.2927 | 1232835.4485
40 | 2720751.9033 | 1232732.2436
41 | 2720750.5315 | 1232731.7051
42 | 2720778.8196 | 1232790.2129
43 | 2720714.7207 | 1232844.9473
44 | 2720708.3306 | 1232852.9636
45 | 2720701.5173 | 1232861.5106
46 | 2720761.9439 | 1232859.9292
47 | 2720765.9438 | 1232863.9804
48 | 2720631.9074 | 1232932.8267
49 | 2720665.6094 | 1232924.2673
50 | 2720626.9519 | 1232940.4861
51 | 2720670.5582 | 1232920.322
52 | 2720618.2315 | 1232953.9642
53 | 2720712.3949 | 1232919.6166
54 | 2720612.6147 | 1232962.6455
55 | 2720723.8325 | 1232925.5079
56 | 2720605.0935 | 1232974.2701
57 | 2720601.6534 | 1232979.5882
58 | 2720618.4638 | 1232981.3246
59 | 2720586.8613 | 1232999.5302
60 | 2720622.4783 | 1232983.4427
61 | 2720582.5851 | 1233005.2051
62 | 2720625.6104 | 1232985.0952
63 | 2720577.1695 | 1233012.3916
64 | 2720595.3346 | 1233012.8316
65 | 2720643.2667 | 1232994.6835
66 | 2720560.2518 | 1233034.841
67 | 2720604.5674 | 1233018.0837
68 | 2720556.2217 | 1233040.1889
69 | 2720607.0053 | 1233033.8245
70 | 2720614.6073 | 1233010.9606
71 | 2720550.4947 | 1233047.7885
72 | 2720628.4298 | 1233030.2622
73 | 2720545.7273 | 1233053.8455
74 | 2720522.5486 | 1233028.7398
75 | 2720642.532 | 1233007.8729
76 | 2720665.0594 | 1233030.8033
77 | 2720648.2451 | 1233056.9028
78 | 2720642.2141 | 1233066.2642
79 | 2720679.3047 | 1233014.673
80 | 2720746.3662 | 1232892.5846
81 | 2720757.008 | 1232877.0362
82 | 2720640.8348 | 1232919.0287

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1