## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3359-18_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3359-18_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3359-18_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3359-18_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3359-18_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3359-18_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3359-18_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3359-18_0_3_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_3359-18_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_3359-18_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_3359-18_0_3_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_3359-18_0_3_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_3359-18_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_3359-18_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_3359-18_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_3359-18_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_3359-18_0_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_3359-18_0_3_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_3359-18_0_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_3359-18_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_3359-18_0_3_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_3359-18_0_3_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_3359-18_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_3359-18_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_3359-18_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_3359-18_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_3359-18_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_3359-18_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_3359-18_0_3_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_3359-18_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_3359-18_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_3359-18_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_3359-18_0_3_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_3359-18_0_3_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_3359-18_0_3_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_3359-18_0_3_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_3359-18_0_3_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_3359-18_0_3_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_3359-18_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_3359-18_0_3_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_3359-18_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_3359-18_0_3_node_56 | 0.4 | n |  | TRUE
42 | bus_LV_3359-18_0_3_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_3359-18_0_3_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_3359-18_0_3_node_51 | 0.4 | n |  | TRUE
45 | bus_LV_3359-18_0_3_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_3359-18_0_3_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_3359-18_0_3_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_3359-18_0_3_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_3359-18_0_3_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_3359-18_0_3_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_3359-18_0_3_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_3359-18_0_3_node_64 | 0.4 | n |  | TRUE
53 | bus_LV_3359-18_0_3_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_3359-18_0_3_node_66 | 0.4 | n |  | TRUE
55 | bus_LV_3359-18_0_3_node_67 | 0.4 | n |  | TRUE
56 | bus_LV_3359-18_0_3_node_68 | 0.4 | n |  | TRUE
57 | bus_LV_3359-18_0_3_node_69 | 0.4 | n |  | TRUE
58 | bus_LV_3359-18_0_3_node_74 | 0.4 | n |  | TRUE
59 | bus_LV_3359-18_0_3_node_77 | 0.4 | n |  | TRUE
60 | bus_LV_3359-18_0_3_node_82 | 0.4 | n |  | TRUE
61 | bus_LV_3359-18_0_3_node_73 | 0.4 | n |  | TRUE
62 | bus_LV_3359-18_0_3_node_70 | 0.4 | n |  | TRUE
63 | bus_LV_3359-18_0_3_node_71 | 0.4 | n |  | TRUE
64 | bus_LV_3359-18_0_3_node_72 | 0.4 | n |  | TRUE
65 | bus_LV_3359-18_0_3_node_80 | 0.4 | n |  | TRUE
66 | bus_LV_3359-18_0_3_node_76 | 0.4 | n |  | TRUE
67 | bus_LV_3359-18_0_3_node_85 | 0.4 | n |  | TRUE
68 | bus_LV_3359-18_0_3_node_79 | 0.4 | n |  | TRUE
69 | bus_LV_3359-18_0_3_node_81 | 0.4 | n |  | TRUE
70 | bus_LV_3359-18_0_3_node_83 | 0.4 | n |  | TRUE
71 | bus_LV_3359-18_0_3_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_3359-18_0_3_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_3359-18_0_3_node_43 | 0.4 | n |  | TRUE
74 | bus_LV_3359-18_0_3_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_3359-18_0_3_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_3359-18_0_3_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_3359-18_0_3_node_47 | 0.4 | n |  | TRUE
78 | bus_LV_3359-18_0_3_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_3359-18_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_3359-18_0_3_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_3359-18_0_3_node_58 | 0.4 | n |  | TRUE
82 | bus_MV_38_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3359-18_0_3_load_0 | 0 | 0.0043983 | 0.0011023 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3359-18_0_3_load_1 | 1 | 0.0025285 | 0.00063371 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3359-18_0_3_load_3 | 3 | 0.002799 | 0.00070151 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3359-18_0_3_load_4 | 4 | 0.0029096 | 0.00072921 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3359-18_0_3_load_6 | 6 | 0.0021737 | 0.00054478 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3359-18_0_3_load_34 | 7 | 0.010568 | 0.0026485 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3359-18_0_3_load_7 | 8 | 0.002922 | 0.00073233 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3359-18_0_3_load_26 | 10 | 0.0066266 | 0.0016608 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3359-18_0_3_load_27 | 11 | 0.003273 | 0.00082029 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3359-18_0_3_load_8 | 12 | 0.0037031 | 0.00092807 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3359-18_0_3_load_9 | 13 | 0.017155 | 0.0042995 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3359-18_0_3_load_29 | 17 | 0.0073329 | 0.0018378 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3359-18_0_3_load_13 | 19 | 0.0051674 | 0.0012951 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3359-18_0_3_load_30 | 20 | 0.004375 | 0.0010965 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3359-18_0_3_load_59 | 21 | 0.0040124 | 0.0010056 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3359-18_0_3_load_14 | 23 | 0.0024469 | 0.00061325 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3359-18_0_3_load_15 | 24 | 0.0059808 | 0.0014989 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3359-18_0_3_load_18 | 26 | 0.0074695 | 0.001872 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3359-18_0_3_load_20 | 27 | 0.0028009 | 0.00070198 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3359-18_0_3_load_55 | 28 | 0.044694 | 0.011201 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3359-18_0_3_load_19 | 29 | 0.0034947 | 0.00087584 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3359-18_0_3_load_24 | 30 | 0.0042117 | 0.0010555 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3359-18_0_3_load_23 | 32 | 0.0032319 | 0.00080998 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3359-18_0_3_load_84 | 34 | 0.00032086 | 8.0415e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3359-18_0_3_load_39 | 36 | 0.00072714 | 0.00018224 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3359-18_0_3_load_28 | 38 | 0.0026143 | 0.00065519 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3359-18_0_3_load_56 | 41 | 0.00093333 | 0.00023391 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3359-18_0_3_load_31 | 42 | 0.0035228 | 0.00088289 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3359-18_0_3_load_52 | 43 | 0.0037513 | 0.00094016 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3359-18_0_3_load_51 | 44 | 0.0025457 | 0.00063802 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3359-18_0_3_load_48 | 45 | 0.0029046 | 0.00072797 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3359-18_0_3_load_49 | 46 | 0.0059037 | 0.0014796 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3359-18_0_3_load_60 | 47 | 0.0047888 | 0.0012002 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3359-18_0_3_load_35 | 48 | 0.00083132 | 0.00020835 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3359-18_0_3_load_36 | 49 | 0.00078061 | 0.00019564 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3359-18_0_3_load_37 | 50 | 0.0003518 | 8.817e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3359-18_0_3_load_75 | 51 | 0.00045105 | 0.00011304 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3359-18_0_3_load_64 | 52 | 0.00038397 | 9.6232e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3359-18_0_3_load_65 | 53 | 0.00047673 | 0.00011948 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3359-18_0_3_load_67 | 55 | 0.00061689 | 0.00015461 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3359-18_0_3_load_69 | 57 | 0.00050043 | 0.00012542 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3359-18_0_3_load_77 | 59 | 0.0006983 | 0.00017501 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3359-18_0_3_load_82 | 60 | 0.00058797 | 0.00014736 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3359-18_0_3_load_73 | 61 | 0.00054194 | 0.00013582 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3359-18_0_3_load_70 | 62 | 0.00067348 | 0.00016879 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3359-18_0_3_load_71 | 63 | 0.00056142 | 0.0001407 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3359-18_0_3_load_72 | 64 | 0.0010238 | 0.00025658 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3359-18_0_3_load_76 | 66 | 0.00053561 | 0.00013424 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3359-18_0_3_load_85 | 67 | 0.00048421 | 0.00012135 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3359-18_0_3_load_79 | 68 | 0.00094157 | 0.00023598 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3359-18_0_3_load_81 | 69 | 0.00031963 | 8.0107e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3359-18_0_3_load_83 | 70 | 0.00050877 | 0.00012751 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3359-18_0_3_load_62 | 72 | 0.0040779 | 0.001022 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3359-18_0_3_load_43 | 73 | 0.0016438 | 0.00041198 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3359-18_0_3_load_44 | 74 | 0.0021284 | 0.00053342 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3359-18_0_3_load_45 | 75 | 0.0039436 | 0.00098837 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3359-18_0_3_load_47 | 77 | 0.0060313 | 0.0015116 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3359-18_0_3_load_63 | 79 | 0.0013028 | 0.00032652 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3359-18_0_3_load_50 | 80 | 0.0027327 | 0.00068489 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3359-18_0_3_load_58 | 81 | 0.0012655 | 0.00031716 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3359-18_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0014163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_3359-18_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.047278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_3359-18_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.020453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_3359-18_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.034625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3359-18_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.11044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_3359-18_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.020196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_3359-18_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.047576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_3359-18_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.023211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_3359-18_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.022039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_3359-18_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.0031489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_3359-18_0_3_line_10 | NAYY 4x150 SE | 9 | 18 | 0.10047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_3359-18_0_3_line_11 | NAYY 4x150 SE | 9 | 14 | 0.007121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_3359-18_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.011707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_3359-18_0_3_line_13 | NAYY 4x150 SE | 11 | 38 | 0.021828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_3359-18_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.017786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_3359-18_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.016887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_3359-18_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.010903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_3359-18_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.013955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3359-18_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.055492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_3359-18_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.011288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3359-18_0_3_line_20 | NAYY 4x150 SE | 17 | 20 | 0.048725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3359-18_0_3_line_21 | NAYY 4x150 SE | 18 | 21 | 0.033051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3359-18_0_3_line_22 | NAYY 4x150 SE | 18 | 22 | 0.029644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_3359-18_0_3_line_23 | NAYY 4x150 SE | 20 | 42 | 0.017679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3359-18_0_3_line_24 | NAYY 4x150 SE | 21 | 47 | 0.0064353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3359-18_0_3_line_25 | NAYY 4x150 SE | 22 | 27 | 0.074399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3359-18_0_3_line_26 | NAYY 4x150 SE | 22 | 24 | 0.044592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_3359-18_0_3_line_27 | NAYY 4x150 SE | 23 | 24 | 0.052589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_3359-18_0_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.030824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_3359-18_0_3_line_29 | NAYY 4x150 SE | 25 | 26 | 0.037427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3359-18_0_3_line_30 | NAYY 4x150 SE | 26 | 28 | 0.0041278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3359-18_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.022581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3359-18_0_3_line_32 | NAYY 4x150 SE | 29 | 32 | 0.07145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3359-18_0_3_line_33 | NAYY 4x150 SE | 30 | 31 | 0.042642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3359-18_0_3_line_34 | NAYY 4x150 SE | 30 | 32 | 0.038491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3359-18_0_3_line_35 | NAYY 4x150 SE | 31 | 33 | 0.044677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3359-18_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.084916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3359-18_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3359-18_0_3_line_38 | NAYY 4x150 SE | 35 | 37 | 0.040142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3359-18_0_3_line_39 | NAYY 4x150 SE | 36 | 37 | 0.093352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3359-18_0_3_line_40 | NAYY 4x150 SE | 38 | 39 | 0.034161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_3359-18_0_3_line_41 | NAYY 4x150 SE | 39 | 40 | 0.053279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_3359-18_0_3_line_42 | NAYY 4x150 SE | 39 | 41 | 0.011559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3359-18_0_3_line_43 | NAYY 4x150 SE | 40 | 49 | 0.01094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_3359-18_0_3_line_44 | NAYY 4x150 SE | 41 | 81 | 0.023276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3359-18_0_3_line_45 | NAYY 4x150 SE | 42 | 43 | 0.031169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3359-18_0_3_line_46 | NAYY 4x150 SE | 43 | 44 | 0.028234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3359-18_0_3_line_47 | NAYY 4x150 SE | 44 | 76 | 0.033757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3359-18_0_3_line_48 | NAYY 4x150 SE | 45 | 46 | 0.047372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3359-18_0_3_line_49 | NAYY 4x150 SE | 46 | 80 | 0.025474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3359-18_0_3_line_50 | NAYY 4x150 SE | 47 | 71 | 0.0076621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3359-18_0_3_line_51 | NAYY 4x150 SE | 48 | 49 | 0.0041111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_3359-18_0_3_line_52 | NAYY 4x150 SE | 48 | 50 | 0.070873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_3359-18_0_3_line_53 | NAYY 4x150 SE | 50 | 51 | 0.21557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3359-18_0_3_line_54 | NAYY 4x150 SE | 51 | 58 | 0.073441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3359-18_0_3_line_55 | NAYY 4x150 SE | 52 | 53 | 0.021056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3359-18_0_3_line_56 | NAYY 4x150 SE | 52 | 54 | 0.046065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3359-18_0_3_line_57 | NAYY 4x150 SE | 53 | 55 | 0.018007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3359-18_0_3_line_58 | NAYY 4x150 SE | 54 | 56 | 0.007704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3359-18_0_3_line_59 | NAYY 4x150 SE | 54 | 57 | 0.072981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3359-18_0_3_line_60 | NAYY 4x150 SE | 55 | 58 | 0.034825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3359-18_0_3_line_61 | NAYY 4x150 SE | 56 | 59 | 0.011941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3359-18_0_3_line_62 | NAYY 4x150 SE | 56 | 60 | 0.059967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3359-18_0_3_line_63 | NAYY 4x150 SE | 57 | 61 | 0.03249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3359-18_0_3_line_64 | NAYY 4x150 SE | 59 | 66 | 0.10194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3359-18_0_3_line_65 | NAYY 4x150 SE | 60 | 70 | 0.026134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3359-18_0_3_line_66 | NAYY 4x150 SE | 61 | 65 | 0.10803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3359-18_0_3_line_67 | NAYY 4x150 SE | 61 | 64 | 0.029714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3359-18_0_3_line_68 | NAYY 4x150 SE | 62 | 63 | 0.080248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3359-18_0_3_line_69 | NAYY 4x150 SE | 62 | 64 | 0.047611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3359-18_0_3_line_70 | NAYY 4x150 SE | 65 | 68 | 0.012404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3359-18_0_3_line_71 | NAYY 4x150 SE | 66 | 67 | 0.067941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3359-18_0_3_line_72 | NAYY 4x150 SE | 68 | 69 | 0.18169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3359-18_0_3_line_73 | NAYY 4x150 SE | 71 | 72 | 0.038125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3359-18_0_3_line_74 | NAYY 4x150 SE | 73 | 74 | 0.021395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3359-18_0_3_line_75 | NAYY 4x150 SE | 73 | 75 | 0.0058964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3359-18_0_3_line_76 | NAYY 4x150 SE | 74 | 76 | 0.017205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3359-18_0_3_line_77 | NAYY 4x150 SE | 75 | 77 | 0.0393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3359-18_0_3_line_78 | NAYY 4x150 SE | 76 | 78 | 0.10895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3359-18_0_3_line_79 | NAYY 4x150 SE | 77 | 79 | 0.10841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3359-18_0_3_line_80 | NAYY 4x150 SE | 78 | 80 | 0.12343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3359-18_0_3_trafo_29 | 0.25 MVA 20/0.4 kV | 82 | 17 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2743969.4986 | 1229458.0399 | 2743968.1323 | 1229457.6669
1 | 2744015.1074 | 1229470.491 | 2743969.4986 | 1229458.0399
2 | 2743968.1323 | 1229457.6669 | 2743956.1878 | 1229454.406 | 2743949.2736 | 1229450.2428
3 | 2744015.1074 | 1229470.491 | 2744013.8365 | 1229486.0296 | 2744010.2542 | 1229494.6727 | 2744000.5506 | 1229494.4375
4 | 2744015.1074 | 1229470.491 | 2744021.5008 | 1229470.646 | 2744022.7328 | 1229478.2937 | 2744029.9178 | 1229500.5095 | 2744042.229 | 1229541.0658 | 2744043.4347 | 1229548.546 | 2744039.2262 | 1229571.1419
5 | 2743931.9717 | 1229439.8248 | 2743949.2736 | 1229450.2428
6 | 2744039.2262 | 1229571.1419 | 2744008.773 | 1229560.4839 | 2743994.46 | 1229555.0448
7 | 2743912.0873 | 1229427.8518 | 2743931.9717 | 1229439.8248
8 | 2743973.8581 | 1229547.2158 | 2743994.46 | 1229555.0448
9 | 2743912.0873 | 1229427.8518 | 2743909.3897 | 1229426.2274
10 | 2743973.8581 | 1229547.2158 | 2743951.633 | 1229596.121 | 2743939.3679 | 1229641.253
11 | 2743973.8581 | 1229547.2158 | 2743967.2941 | 1229544.41
12 | 2743899.3608 | 1229420.1887 | 2743909.3897 | 1229426.2274
13 | 2743899.3608 | 1229420.1887 | 2743898.8812 | 1229419.8999 | 2743897.1423 | 1229410.3272 | 2743895.4081 | 1229398.9198
14 | 2743951.8106 | 1229537.677 | 2743935.5749 | 1229530.4147
15 | 2743967.2941 | 1229544.41 | 2743963.158 | 1229542.7528 | 2743951.8106 | 1229537.677
16 | 2743925.6223 | 1229525.9629 | 2743935.5749 | 1229530.4147
17 | 2743931.9375 | 1229538.4156 | 2743925.6223 | 1229525.9629
18 | 2743925.6223 | 1229525.9629 | 2743911.555 | 1229520.3286 | 2743896.421 | 1229514.9243 | 2743886.0114 | 1229512.5482 | 2743872.5775 | 1229510.4881
19 | 2743931.9375 | 1229538.4156 | 2743942.3755 | 1229542.7138
20 | 2743872.5775 | 1229510.4881 | 2743872.5775 | 1229510.4881 | 2743829.5615 | 1229508.4125 | 2743823.9267 | 1229507.8911
21 | 2743939.3679 | 1229641.253 | 2743949.6837 | 1229641.5473 | 2743962.9575 | 1229630.4922 | 2743968.3806 | 1229629.885
22 | 2743939.3679 | 1229641.253 | 2743933.8629 | 1229654.8095 | 2743920.6104 | 1229661.8617
23 | 2743823.9267 | 1229507.8911 | 2743806.3228 | 1229506.2623
24 | 2743968.3806 | 1229629.885 | 2743974.7759 | 1229629.1688
25 | 2743920.6104 | 1229661.8617 | 2743909.8612 | 1229667.5733 | 2743889.6596 | 1229672.0774 | 2743865.2883 | 1229683.2088 | 2743855.94 | 1229694.5998
26 | 2743920.6104 | 1229661.8617 | 2743906.6923 | 1229661.3467 | 2743882.7837 | 1229669.9536 | 2743877.6572 | 1229671.1033
27 | 2743877.6572 | 1229671.1033 | 2743854.4961 | 1229676.2972 | 2743847.0534 | 1229672.5361 | 2743835.0157 | 1229655.9253
28 | 2743823.6323 | 1229628.4418 | 2743824.8967 | 1229641.9621 | 2743835.0157 | 1229655.9253
29 | 2743823.6323 | 1229628.4418 | 2743830.197 | 1229607.4153 | 2743834.7787 | 1229592.7136
30 | 2743836.0068 | 1229588.7727 | 2743834.7787 | 1229592.7136
31 | 2743855.94 | 1229694.5998 | 2743847.9901 | 1229704.2868 | 2743841.8702 | 1229712.2575
32 | 2743841.8702 | 1229712.2575 | 2743897.6301 | 1229756.9327
33 | 2743977.4668 | 1229762.7048 | 2743970.0225 | 1229762.4577 | 2743944.9535 | 1229755.1555 | 2743935.9246 | 1229754.1645
34 | 2743935.9246 | 1229754.1645 | 2743931.3019 | 1229753.6571 | 2743907.7072 | 1229755.5768 | 2743897.6301 | 1229756.9327
35 | 2743977.4668 | 1229762.7048 | 2743977.4255 | 1229778.4844 | 2743979.8961 | 1229807.2696
36 | 2743979.8961 | 1229807.2696 | 2743980.2092 | 1229810.9249 | 2743988.9703 | 1229836.5819 | 2744018.8603 | 1229850.4068 | 2744032.0776 | 1229866.9864
37 | 2744120.3386 | 1229953.3895 | 2744115.7175 | 1229935.8064 | 2744104.2248 | 1229928.1211 | 2744096.4757 | 1229919.2032 | 2744075.3527 | 1229903.5999 | 2744054.6313 | 1229893.3111 | 2744048.648 | 1229888.1393 | 2744034.5272 | 1229870.0591 | 2744032.0776 | 1229866.9864
38 | 2744120.3386 | 1229953.3895 | 2744157.7115 | 1229968.3196
39 | 2744157.7115 | 1229968.3196 | 2744064.9781 | 1229979.0501
40 | 2743894.8635 | 1229364.8319 | 2743894.4747 | 1229392.7805 | 2743895.4081 | 1229398.9198
41 | 2743894.8635 | 1229364.8319 | 2743841.4726 | 1229362.6496
42 | 2743894.8635 | 1229364.8319 | 2743895.3337 | 1229353.2822
43 | 2743841.4726 | 1229362.6496 | 2743839.4631 | 1229351.8955
44 | 2743888.5417 | 1229333.2288 | 2743893.6789 | 1229336.4337 | 2743895.7799 | 1229342.323 | 2743895.3337 | 1229353.2822
45 | 2743775.3075 | 1229503.208 | 2743779.1047 | 1229503.744 | 2743806.3228 | 1229506.2623
46 | 2743747.3145 | 1229499.5563 | 2743755.8094 | 1229500.4558 | 2743775.3075 | 1229503.208
47 | 2743713.7452 | 1229496.002 | 2743747.3145 | 1229499.5563
48 | 2743805.0319 | 1229509.8224 | 2743786.1131 | 1229508.8624 | 2743764.2758 | 1229506.399 | 2743757.8727 | 1229505.5984
49 | 2743757.8727 | 1229505.5984 | 2743750.9309 | 1229504.7305 | 2743738.3 | 1229503.0015 | 2743732.6511 | 1229502.0458
50 | 2743982.3904 | 1229628.3162 | 2743974.7759 | 1229629.1688
51 | 2743838.708 | 1229347.8544 | 2743839.4631 | 1229351.8955
52 | 2743838.708 | 1229347.8544 | 2743836.5941 | 1229336.5419 | 2743825.6838 | 1229290.6376 | 2743814.7308 | 1229285.3054
53 | 2743814.7308 | 1229285.3054 | 2743836.8403 | 1229070.8697
54 | 2743910.1901 | 1229067.7626 | 2743884.3457 | 1229067.9376 | 2743836.8403 | 1229070.8697
55 | 2743842.7649 | 1229039.5192 | 2743851.2777 | 1229043.683 | 2743862.3229 | 1229047.1613
56 | 2743802.9597 | 1229016.5574 | 2743821.6645 | 1229029.1986 | 2743842.7649 | 1229039.5192
57 | 2743879.4987 | 1229052.5703 | 2743862.3229 | 1229047.1613
58 | 2743797.9317 | 1229010.7085 | 2743802.9597 | 1229016.5574
59 | 2743802.9597 | 1229016.5574 | 2743730.0626 | 1229013.055
60 | 2743910.1901 | 1229067.7626 | 2743898.8283 | 1229058.6575 | 2743879.4987 | 1229052.5703
61 | 2743797.9317 | 1229010.7085 | 2743790.5111 | 1229001.3526
62 | 2743797.9317 | 1229010.7085 | 2743814.1662 | 1229013.2922 | 2743830.6054 | 1229014.6241 | 2743846.9498 | 1229013.6074 | 2743857.5067 | 1229012.1332
63 | 2743730.0626 | 1229013.055 | 2743718.1165 | 1229012.4811 | 2743697.788 | 1229009.6124
64 | 2743720.9413 | 1228927.295 | 2743754.0262 | 1228956.8887 | 2743761.1679 | 1228964.3567 | 2743790.5111 | 1229001.3526
65 | 2743883.3238 | 1229008.0823 | 2743861.2715 | 1229011.6075 | 2743857.5067 | 1229012.1332
66 | 2743697.788 | 1229009.6124 | 2743663.6861 | 1229112.1207
67 | 2743697.788 | 1229009.6124 | 2743688.4434 | 1229008.2938 | 2743668.8977 | 1229002.8974
68 | 2743625.3477 | 1228984.2639 | 2743614.2427 | 1228978.4867 | 2743593.9214 | 1228966.53 | 2743595.082 | 1228957.083 | 2743599.746 | 1228941.6153 | 2743617.8073 | 1228940.7617 | 2743618.0545 | 1228940.4516
69 | 2743625.3477 | 1228984.2639 | 2743652.4209 | 1228998.3483 | 2743668.8977 | 1229002.8974
70 | 2743663.6861 | 1229112.1207 | 2743651.5603 | 1229114.7322
71 | 2743720.9413 | 1228927.295 | 2743762.6716 | 1228873.6798
72 | 2743651.5603 | 1229114.7322 | 2743470.3763 | 1229101.1438
73 | 2743991.437 | 1229594.661 | 2743991.5917 | 1229621.1215 | 2743982.3904 | 1229628.3162
74 | 2743702.6275 | 1229462.3561 | 2743709.3406 | 1229466.2693 | 2743714.3635 | 1229477.3338 | 2743714.3147 | 1229478.8061
75 | 2743702.6275 | 1229462.3561 | 2743697.5335 | 1229459.3866
76 | 2743713.7452 | 1229496.002 | 2743714.3147 | 1229478.8061
77 | 2743661.9147 | 1229443.4368 | 2743678.8686 | 1229448.5063 | 2743697.5335 | 1229459.3866
78 | 2743610.5723 | 1229483.8547 | 2743610.5271 | 1229479.4498 | 2743690.0368 | 1229491.6142 | 2743713.7452 | 1229496.002
79 | 2743661.9147 | 1229443.4368 | 2743585.5487 | 1229366.4891
80 | 2743610.5723 | 1229483.8547 | 2743621.4177 | 1229485.4514 | 2743663.0443 | 1229491.7066 | 2743706.3827 | 1229498.0036 | 2743724.4183 | 1229500.6529 | 2743732.6511 | 1229502.0458

## bus_geodata
| x | y | coords
0 | 2743969.4986 | 1229458.0399
1 | 2743968.1323 | 1229457.6669
2 | 2744015.1074 | 1229470.491
3 | 2743949.2736 | 1229450.2428
4 | 2744000.5506 | 1229494.4375
5 | 2744039.2262 | 1229571.1419
6 | 2743931.9717 | 1229439.8248
7 | 2743994.46 | 1229555.0448
8 | 2743912.0873 | 1229427.8518
9 | 2743973.8581 | 1229547.2158
10 | 2743909.3897 | 1229426.2274
11 | 2743899.3608 | 1229420.1887
12 | 2743951.8106 | 1229537.677
13 | 2743935.5749 | 1229530.4147
14 | 2743967.2941 | 1229544.41
15 | 2743925.6223 | 1229525.9629
16 | 2743931.9375 | 1229538.4156
17 | 2743872.5775 | 1229510.4881
18 | 2743939.3679 | 1229641.253
19 | 2743942.3755 | 1229542.7138
20 | 2743823.9267 | 1229507.8911
21 | 2743968.3806 | 1229629.885
22 | 2743920.6104 | 1229661.8617
23 | 2743835.0157 | 1229655.9253
24 | 2743877.6572 | 1229671.1033
25 | 2743823.6323 | 1229628.4418
26 | 2743834.7787 | 1229592.7136
27 | 2743855.94 | 1229694.5998
28 | 2743836.0068 | 1229588.7727
29 | 2743841.8702 | 1229712.2575
30 | 2743935.9246 | 1229754.1645
31 | 2743977.4668 | 1229762.7048
32 | 2743897.6301 | 1229756.9327
33 | 2743979.8961 | 1229807.2696
34 | 2744032.0776 | 1229866.9864
35 | 2744120.3386 | 1229953.3895
36 | 2744064.9781 | 1229979.0501
37 | 2744157.7115 | 1229968.3196
38 | 2743895.4081 | 1229398.9198
39 | 2743894.8635 | 1229364.8319
40 | 2743841.4726 | 1229362.6496
41 | 2743895.3337 | 1229353.2822
42 | 2743806.3228 | 1229506.2623
43 | 2743775.3075 | 1229503.208
44 | 2743747.3145 | 1229499.5563
45 | 2743805.0319 | 1229509.8224
46 | 2743757.8727 | 1229505.5984
47 | 2743974.7759 | 1229629.1688
48 | 2743838.708 | 1229347.8544
49 | 2743839.4631 | 1229351.8955
50 | 2743814.7308 | 1229285.3054
51 | 2743836.8403 | 1229070.8697
52 | 2743842.7649 | 1229039.5192
53 | 2743862.3229 | 1229047.1613
54 | 2743802.9597 | 1229016.5574
55 | 2743879.4987 | 1229052.5703
56 | 2743797.9317 | 1229010.7085
57 | 2743730.0626 | 1229013.055
58 | 2743910.1901 | 1229067.7626
59 | 2743790.5111 | 1229001.3526
60 | 2743857.5067 | 1229012.1332
61 | 2743697.788 | 1229009.6124
62 | 2743625.3477 | 1228984.2639
63 | 2743618.0545 | 1228940.4516
64 | 2743668.8977 | 1229002.8974
65 | 2743663.6861 | 1229112.1207
66 | 2743720.9413 | 1228927.295
67 | 2743762.6716 | 1228873.6798
68 | 2743651.5603 | 1229114.7322
69 | 2743470.3763 | 1229101.1438
70 | 2743883.3238 | 1229008.0823
71 | 2743982.3904 | 1229628.3162
72 | 2743991.437 | 1229594.661
73 | 2743702.6275 | 1229462.3561
74 | 2743714.3147 | 1229478.8061
75 | 2743697.5335 | 1229459.3866
76 | 2743713.7452 | 1229496.002
77 | 2743661.9147 | 1229443.4368
78 | 2743610.5723 | 1229483.8547
79 | 2743585.5487 | 1229366.4891
80 | 2743732.6511 | 1229502.0458
81 | 2743888.5417 | 1229333.2288
82 | 2743925.6223 | 1229525.9629

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1