## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3372-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3372-1_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_3372-1_0_4_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_3372-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3372-1_0_4_node_101 | 0.4 | n |  | TRUE
5 | bus_LV_3372-1_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3372-1_0_4_node_53 | 0.4 | n |  | TRUE
7 | bus_LV_3372-1_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_3372-1_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_3372-1_0_4_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_3372-1_0_4_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_3372-1_0_4_node_157 | 0.4 | n |  | TRUE
12 | bus_LV_3372-1_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_3372-1_0_4_node_95 | 0.4 | n |  | TRUE
14 | bus_LV_3372-1_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_3372-1_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_3372-1_0_4_node_159 | 0.4 | n |  | TRUE
17 | bus_LV_3372-1_0_4_node_51 | 0.4 | n |  | TRUE
18 | bus_LV_3372-1_0_4_node_98 | 0.4 | n |  | TRUE
19 | bus_LV_3372-1_0_4_node_100 | 0.4 | n |  | TRUE
20 | bus_LV_3372-1_0_4_node_97 | 0.4 | n |  | TRUE
21 | bus_LV_3372-1_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_3372-1_0_4_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_3372-1_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_3372-1_0_4_node_82 | 0.4 | n |  | TRUE
25 | bus_LV_3372-1_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_3372-1_0_4_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_3372-1_0_4_node_80 | 0.4 | n |  | TRUE
28 | bus_LV_3372-1_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_3372-1_0_4_node_111 | 0.4 | n |  | TRUE
30 | bus_LV_3372-1_0_4_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_3372-1_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_3372-1_0_4_node_133 | 0.4 | n |  | TRUE
33 | bus_LV_3372-1_0_4_node_158 | 0.4 | n |  | TRUE
34 | bus_LV_3372-1_0_4_node_75 | 0.4 | n |  | TRUE
35 | bus_LV_3372-1_0_4_node_74 | 0.4 | n |  | TRUE
36 | bus_LV_3372-1_0_4_node_93 | 0.4 | n |  | TRUE
37 | bus_LV_3372-1_0_4_node_8 | 0.4 | n |  | TRUE
38 | bus_LV_3372-1_0_4_node_9 | 0.4 | n |  | TRUE
39 | bus_LV_3372-1_0_4_node_11 | 0.4 | n |  | TRUE
40 | bus_LV_3372-1_0_4_node_86 | 0.4 | n |  | TRUE
41 | bus_LV_3372-1_0_4_node_112 | 0.4 | n |  | TRUE
42 | bus_LV_3372-1_0_4_node_12 | 0.4 | n |  | TRUE
43 | bus_LV_3372-1_0_4_node_76 | 0.4 | n |  | TRUE
44 | bus_LV_3372-1_0_4_node_136 | 0.4 | n |  | TRUE
45 | bus_LV_3372-1_0_4_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_3372-1_0_4_node_107 | 0.4 | n |  | TRUE
47 | bus_LV_3372-1_0_4_node_96 | 0.4 | n |  | TRUE
48 | bus_LV_3372-1_0_4_node_162 | 0.4 | n |  | TRUE
49 | bus_LV_3372-1_0_4_node_102 | 0.4 | n |  | TRUE
50 | bus_LV_3372-1_0_4_node_15 | 0.4 | n |  | TRUE
51 | bus_LV_3372-1_0_4_node_16 | 0.4 | n |  | TRUE
52 | bus_LV_3372-1_0_4_node_18 | 0.4 | n |  | TRUE
53 | bus_LV_3372-1_0_4_node_19 | 0.4 | n |  | TRUE
54 | bus_LV_3372-1_0_4_node_17 | 0.4 | n |  | TRUE
55 | bus_LV_3372-1_0_4_node_20 | 0.4 | n |  | TRUE
56 | bus_LV_3372-1_0_4_node_21 | 0.4 | n |  | TRUE
57 | bus_LV_3372-1_0_4_node_166 | 0.4 | n |  | TRUE
58 | bus_LV_3372-1_0_4_node_165 | 0.4 | n |  | TRUE
59 | bus_LV_3372-1_0_4_node_149 | 0.4 | n |  | TRUE
60 | bus_LV_3372-1_0_4_node_171 | 0.4 | n |  | TRUE
61 | bus_LV_3372-1_0_4_node_170 | 0.4 | n |  | TRUE
62 | bus_LV_3372-1_0_4_node_143 | 0.4 | n |  | TRUE
63 | bus_LV_3372-1_0_4_node_30 | 0.4 | n |  | TRUE
64 | bus_LV_3372-1_0_4_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_3372-1_0_4_node_151 | 0.4 | n |  | TRUE
66 | bus_LV_3372-1_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_3372-1_0_4_node_81 | 0.4 | n |  | TRUE
68 | bus_LV_3372-1_0_4_node_108 | 0.4 | n |  | TRUE
69 | bus_LV_3372-1_0_4_node_148 | 0.4 | n |  | TRUE
70 | bus_LV_3372-1_0_4_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_3372-1_0_4_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_3372-1_0_4_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_3372-1_0_4_node_103 | 0.4 | n |  | TRUE
74 | bus_LV_3372-1_0_4_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_3372-1_0_4_node_33 | 0.4 | n |  | TRUE
76 | bus_LV_3372-1_0_4_node_34 | 0.4 | n |  | TRUE
77 | bus_LV_3372-1_0_4_node_37 | 0.4 | n |  | TRUE
78 | bus_LV_3372-1_0_4_node_36 | 0.4 | n |  | TRUE
79 | bus_LV_3372-1_0_4_node_41 | 0.4 | n |  | TRUE
80 | bus_LV_3372-1_0_4_node_42 | 0.4 | n |  | TRUE
81 | bus_LV_3372-1_0_4_node_43 | 0.4 | n |  | TRUE
82 | bus_LV_3372-1_0_4_node_168 | 0.4 | n |  | TRUE
83 | bus_LV_3372-1_0_4_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_3372-1_0_4_node_140 | 0.4 | n |  | TRUE
85 | bus_LV_3372-1_0_4_node_141 | 0.4 | n |  | TRUE
86 | bus_LV_3372-1_0_4_node_139 | 0.4 | n |  | TRUE
87 | bus_LV_3372-1_0_4_node_117 | 0.4 | n |  | TRUE
88 | bus_LV_3372-1_0_4_node_167 | 0.4 | n |  | TRUE
89 | bus_LV_3372-1_0_4_node_128 | 0.4 | n |  | TRUE
90 | bus_LV_3372-1_0_4_node_129 | 0.4 | n |  | TRUE
91 | bus_LV_3372-1_0_4_node_45 | 0.4 | n |  | TRUE
92 | bus_LV_3372-1_0_4_node_46 | 0.4 | n |  | TRUE
93 | bus_LV_3372-1_0_4_node_47 | 0.4 | n |  | TRUE
94 | bus_LV_3372-1_0_4_node_48 | 0.4 | n |  | TRUE
95 | bus_LV_3372-1_0_4_node_49 | 0.4 | n |  | TRUE
96 | bus_LV_3372-1_0_4_node_64 | 0.4 | n |  | TRUE
97 | bus_LV_3372-1_0_4_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_3372-1_0_4_node_55 | 0.4 | n |  | TRUE
99 | bus_LV_3372-1_0_4_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_3372-1_0_4_node_147 | 0.4 | n |  | TRUE
101 | bus_LV_3372-1_0_4_node_56 | 0.4 | n |  | TRUE
102 | bus_LV_3372-1_0_4_node_50 | 0.4 | n |  | TRUE
103 | bus_LV_3372-1_0_4_node_52 | 0.4 | n |  | TRUE
104 | bus_LV_3372-1_0_4_node_54 | 0.4 | n |  | TRUE
105 | bus_LV_3372-1_0_4_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_3372-1_0_4_node_169 | 0.4 | n |  | TRUE
107 | bus_LV_3372-1_0_4_node_88 | 0.4 | n |  | TRUE
108 | bus_LV_3372-1_0_4_node_161 | 0.4 | n |  | TRUE
109 | bus_LV_3372-1_0_4_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_3372-1_0_4_node_58 | 0.4 | n |  | TRUE
111 | bus_LV_3372-1_0_4_node_60 | 0.4 | n |  | TRUE
112 | bus_LV_3372-1_0_4_node_61 | 0.4 | n |  | TRUE
113 | bus_LV_3372-1_0_4_node_154 | 0.4 | n |  | TRUE
114 | bus_LV_3372-1_0_4_node_152 | 0.4 | n |  | TRUE
115 | bus_LV_3372-1_0_4_node_164 | 0.4 | n |  | TRUE
116 | bus_LV_3372-1_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_3372-1_0_4_node_156 | 0.4 | n |  | TRUE
118 | bus_LV_3372-1_0_4_node_72 | 0.4 | n |  | TRUE
119 | bus_LV_3372-1_0_4_node_155 | 0.4 | n |  | TRUE
120 | bus_LV_3372-1_0_4_node_146 | 0.4 | n |  | TRUE
121 | bus_LV_3372-1_0_4_node_66 | 0.4 | n |  | TRUE
122 | bus_LV_3372-1_0_4_node_67 | 0.4 | n |  | TRUE
123 | bus_LV_3372-1_0_4_node_68 | 0.4 | n |  | TRUE
124 | bus_LV_3372-1_0_4_node_69 | 0.4 | n |  | TRUE
125 | bus_LV_3372-1_0_4_node_70 | 0.4 | n |  | TRUE
126 | bus_LV_3372-1_0_4_node_99 | 0.4 | n |  | TRUE
127 | bus_LV_3372-1_0_4_node_122 | 0.4 | n |  | TRUE
128 | bus_LV_3372-1_0_4_node_163 | 0.4 | n |  | TRUE
129 | bus_LV_3372-1_0_4_node_77 | 0.4 | n |  | TRUE
130 | bus_LV_3372-1_0_4_node_78 | 0.4 | n |  | TRUE
131 | bus_LV_3372-1_0_4_node_79 | 0.4 | n |  | TRUE
132 | bus_LV_3372-1_0_4_node_153 | 0.4 | n |  | TRUE
133 | bus_LV_3372-1_0_4_node_109 | 0.4 | n |  | TRUE
134 | bus_LV_3372-1_0_4_node_83 | 0.4 | n |  | TRUE
135 | bus_LV_3372-1_0_4_node_85 | 0.4 | n |  | TRUE
136 | bus_LV_3372-1_0_4_node_105 | 0.4 | n |  | TRUE
137 | bus_LV_3372-1_0_4_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_3372-1_0_4_node_87 | 0.4 | n |  | TRUE
139 | bus_LV_3372-1_0_4_node_89 | 0.4 | n |  | TRUE
140 | bus_LV_3372-1_0_4_node_90 | 0.4 | n |  | TRUE
141 | bus_LV_3372-1_0_4_node_121 | 0.4 | n |  | TRUE
142 | bus_LV_3372-1_0_4_node_120 | 0.4 | n |  | TRUE
143 | bus_LV_3372-1_0_4_node_92 | 0.4 | n |  | TRUE
144 | bus_LV_3372-1_0_4_node_94 | 0.4 | n |  | TRUE
145 | bus_LV_3372-1_0_4_node_104 | 0.4 | n |  | TRUE
146 | bus_LV_3372-1_0_4_node_110 | 0.4 | n |  | TRUE
147 | bus_LV_3372-1_0_4_node_160 | 0.4 | n |  | TRUE
148 | bus_LV_3372-1_0_4_node_113 | 0.4 | n |  | TRUE
149 | bus_LV_3372-1_0_4_node_114 | 0.4 | n |  | TRUE
150 | bus_LV_3372-1_0_4_node_116 | 0.4 | n |  | TRUE
151 | bus_LV_3372-1_0_4_node_138 | 0.4 | n |  | TRUE
152 | bus_LV_3372-1_0_4_node_135 | 0.4 | n |  | TRUE
153 | bus_LV_3372-1_0_4_node_118 | 0.4 | n |  | TRUE
154 | bus_LV_3372-1_0_4_node_145 | 0.4 | n |  | TRUE
155 | bus_LV_3372-1_0_4_node_127 | 0.4 | n |  | TRUE
156 | bus_LV_3372-1_0_4_node_132 | 0.4 | n |  | TRUE
157 | bus_LV_3372-1_0_4_node_124 | 0.4 | n |  | TRUE
158 | bus_LV_3372-1_0_4_node_119 | 0.4 | n |  | TRUE
159 | bus_LV_3372-1_0_4_node_123 | 0.4 | n |  | TRUE
160 | bus_LV_3372-1_0_4_node_125 | 0.4 | n |  | TRUE
161 | bus_LV_3372-1_0_4_node_130 | 0.4 | n |  | TRUE
162 | bus_LV_3372-1_0_4_node_131 | 0.4 | n |  | TRUE
163 | bus_MV_153_1_node_154 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3372-1_0_4_load_0 | 0 | 0.0098957 | 0.0024801 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3372-1_0_4_load_53 | 6 | 0.00045822 | 0.00011484 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3372-1_0_4_load_24 | 8 | 0.0026491 | 0.00066393 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3372-1_0_4_load_22 | 10 | 0.0086426 | 0.002166 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3372-1_0_4_load_157 | 11 | 0.0026433 | 0.00066248 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3372-1_0_4_load_95 | 13 | 0.0039781 | 0.000997 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3372-1_0_4_load_159 | 16 | 0.0017231 | 0.00043186 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3372-1_0_4_load_100 | 19 | 0.004065 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3372-1_0_4_load_97 | 20 | 0.001719 | 0.00043083 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3372-1_0_4_load_35 | 22 | 0.003048 | 0.00076389 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3372-1_0_4_load_32 | 23 | 0.0086127 | 0.0021586 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3372-1_0_4_load_82 | 24 | 0.0023313 | 0.00058429 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3372-1_0_4_load_80 | 27 | 0.0047131 | 0.0011812 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3372-1_0_4_load_40 | 30 | 0.0054441 | 0.0013644 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3372-1_0_4_load_133 | 32 | 0.0011654 | 0.00029208 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3372-1_0_4_load_75 | 34 | 0.002943 | 0.00073759 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3372-1_0_4_load_74 | 35 | 0.0031569 | 0.00079118 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3372-1_0_4_load_93 | 36 | 0.012502 | 0.0031333 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3372-1_0_4_load_8 | 37 | 0.0020428 | 0.00051198 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3372-1_0_4_load_9 | 38 | 0.00057691 | 0.00014459 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3372-1_0_4_load_76 | 43 | 0.0045846 | 0.001149 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3372-1_0_4_load_84 | 45 | 0.00091084 | 0.00022828 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3372-1_0_4_load_96 | 47 | 0.00080307 | 0.00020127 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3372-1_0_4_load_162 | 48 | 0.001798 | 0.00045061 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3372-1_0_4_load_102 | 49 | 0.0029427 | 0.0007375 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3372-1_0_4_load_15 | 50 | 0.0023106 | 0.00057909 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3372-1_0_4_load_20 | 55 | 0.0012214 | 0.00030611 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3372-1_0_4_load_165 | 58 | 0.00040995 | 0.00010274 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3372-1_0_4_load_149 | 59 | 0.0014843 | 0.000372 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3372-1_0_4_load_171 | 60 | 0.0020332 | 0.00050957 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3372-1_0_4_load_170 | 61 | 0.0020344 | 0.00050987 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3372-1_0_4_load_151 | 65 | 0.0058895 | 0.001476 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3372-1_0_4_load_39 | 66 | 0.002966 | 0.00074335 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3372-1_0_4_load_108 | 68 | 0.0020241 | 0.00050727 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3372-1_0_4_load_148 | 69 | 0.00084539 | 0.00021188 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3372-1_0_4_load_38 | 70 | 0.0036505 | 0.00091491 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3372-1_0_4_load_62 | 71 | 0.00051177 | 0.00012826 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3372-1_0_4_load_57 | 72 | 0.00099405 | 0.00024913 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3372-1_0_4_load_63 | 74 | 0.0044473 | 0.0011146 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3372-1_0_4_load_33 | 75 | 0.0030023 | 0.00075245 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3372-1_0_4_load_34 | 76 | 0.00074851 | 0.00018759 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3372-1_0_4_load_37 | 77 | 0.0028266 | 0.00070842 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3372-1_0_4_load_36 | 78 | 0.0028056 | 0.00070314 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3372-1_0_4_load_41 | 79 | 0.00064659 | 0.00016205 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3372-1_0_4_load_42 | 80 | 0.00016422 | 4.1157e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3372-1_0_4_load_168 | 82 | 0.00024026 | 6.0214e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3372-1_0_4_load_141 | 85 | 0.0013576 | 0.00034024 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3372-1_0_4_load_139 | 86 | 0.00091109 | 0.00022834 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3372-1_0_4_load_128 | 89 | 0.00027386 | 6.8635e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3372-1_0_4_load_45 | 91 | 0.0011327 | 0.00028389 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3372-1_0_4_load_46 | 92 | 0.0011453 | 0.00028703 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3372-1_0_4_load_47 | 93 | 0.0014837 | 0.00037185 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3372-1_0_4_load_49 | 95 | 0.0011832 | 0.00029654 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3372-1_0_4_load_65 | 97 | 0.00050227 | 0.00012588 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3372-1_0_4_load_55 | 98 | 0.00066459 | 0.00016656 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3372-1_0_4_load_147 | 100 | 0.0014492 | 0.00036319 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3372-1_0_4_load_56 | 101 | 0.00065861 | 0.00016506 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3372-1_0_4_load_50 | 102 | 0.00064167 | 0.00016082 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3372-1_0_4_load_169 | 106 | 0.00095674 | 0.00023978 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3372-1_0_4_load_161 | 108 | 0.0015666 | 0.00039263 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3372-1_0_4_load_73 | 109 | 0.0010367 | 0.00025983 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3372-1_0_4_load_61 | 112 | 0.00087193 | 0.00021853 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3372-1_0_4_load_154 | 113 | 0.0050455 | 0.0012645 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3372-1_0_4_load_152 | 114 | 0.0008278 | 0.00020747 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3372-1_0_4_load_164 | 115 | 0.0022681 | 0.00056843 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3372-1_0_4_load_115 | 116 | 0.0019949 | 0.00049998 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3372-1_0_4_load_156 | 117 | 0.002269 | 0.00056867 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3372-1_0_4_load_155 | 119 | 0.0013668 | 0.00034256 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3372-1_0_4_load_146 | 120 | 0.002592 | 0.00064963 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3372-1_0_4_load_66 | 121 | 0.0015902 | 0.00039854 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3372-1_0_4_load_67 | 122 | 0.0011113 | 0.00027853 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3372-1_0_4_load_69 | 124 | 0.0011755 | 0.00029462 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3372-1_0_4_load_70 | 125 | 0.00095833 | 0.00024018 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3372-1_0_4_load_122 | 127 | 0.0012351 | 0.00030956 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3372-1_0_4_load_163 | 128 | 0.00097646 | 0.00024472 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3372-1_0_4_load_77 | 129 | 0.00035098 | 8.7965e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3372-1_0_4_load_79 | 131 | 0.00044726 | 0.00011209 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3372-1_0_4_load_109 | 133 | 0.00070838 | 0.00017754 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3372-1_0_4_load_83 | 134 | 0.0007052 | 0.00017674 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3372-1_0_4_load_85 | 135 | 0.00075532 | 0.0001893 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3372-1_0_4_load_105 | 136 | 0.02121 | 0.0053157 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3372-1_0_4_load_134 | 137 | 0.0020349 | 0.00051001 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3372-1_0_4_load_87 | 138 | 0.0016724 | 0.00041915 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3372-1_0_4_load_89 | 139 | 0.0012036 | 0.00030165 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3372-1_0_4_load_120 | 142 | 0.0016894 | 0.0004234 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3372-1_0_4_load_92 | 143 | 0.0034095 | 0.00085449 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3372-1_0_4_load_94 | 144 | 0.00047394 | 0.00011878 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3372-1_0_4_load_104 | 145 | 0.0098488 | 0.0024683 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3372-1_0_4_load_110 | 146 | 0.00089227 | 0.00022362 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3372-1_0_4_load_160 | 147 | 0.0013181 | 0.00033035 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3372-1_0_4_load_113 | 148 | 0.00043637 | 0.00010936 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3372-1_0_4_load_114 | 149 | 0.00056575 | 0.00014179 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3372-1_0_4_load_138 | 151 | 0.0010108 | 0.00025334 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3372-1_0_4_load_145 | 154 | 0.00024526 | 6.1467e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3372-1_0_4_load_124 | 157 | 0.00024836 | 6.2246e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3372-1_0_4_load_119 | 158 | 0.0030277 | 0.00075883 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3372-1_0_4_load_123 | 159 | 0.00013902 | 3.4843e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3372-1_0_4_load_125 | 160 | 0.00039372 | 9.8677e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3372-1_0_4_load_130 | 161 | 0.00012226 | 3.064e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3372-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0053546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3372-1_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.03307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3372-1_0_4_line_2 | NAYY 4x150 SE | 2 | 12 | 0.0081097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_3372-1_0_4_line_3 | NAYY 4x150 SE | 2 | 13 | 0.022945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3372-1_0_4_line_4 | NAYY 4x150 SE | 3 | 4 | 0.014767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3372-1_0_4_line_5 | NAYY 4x150 SE | 3 | 5 | 0.007022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3372-1_0_4_line_6 | NAYY 4x150 SE | 3 | 6 | 0.11534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3372-1_0_4_line_7 | NAYY 4x150 SE | 4 | 16 | 0.028764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3372-1_0_4_line_8 | NAYY 4x150 SE | 5 | 11 | 0.0063386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3372-1_0_4_line_9 | NAYY 4x150 SE | 6 | 17 | 0.062982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3372-1_0_4_line_10 | NAYY 4x150 SE | 7 | 8 | 0.023073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_3372-1_0_4_line_11 | NAYY 4x150 SE | 7 | 9 | 0.011133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3372-1_0_4_line_12 | NAYY 4x150 SE | 7 | 10 | 0.022947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3372-1_0_4_line_13 | NAYY 4x150 SE | 8 | 21 | 0.0083987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_3372-1_0_4_line_14 | NAYY 4x150 SE | 9 | 22 | 0.017336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3372-1_0_4_line_15 | NAYY 4x150 SE | 9 | 15 | 0.010334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3372-1_0_4_line_16 | NAYY 4x150 SE | 9 | 23 | 0.019436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3372-1_0_4_line_17 | NAYY 4x150 SE | 10 | 31 | 0.022608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3372-1_0_4_line_18 | NAYY 4x150 SE | 11 | 14 | 0.014888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3372-1_0_4_line_19 | NAYY 4x150 SE | 12 | 34 | 0.012972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3372-1_0_4_line_20 | NAYY 4x150 SE | 12 | 35 | 0.019222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3372-1_0_4_line_21 | NAYY 4x150 SE | 12 | 21 | 0.014012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_3372-1_0_4_line_22 | NAYY 4x150 SE | 13 | 36 | 0.012382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3372-1_0_4_line_23 | NAYY 4x150 SE | 14 | 15 | 0.007805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3372-1_0_4_line_24 | NAYY 4x150 SE | 15 | 24 | 0.010823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3372-1_0_4_line_25 | NAYY 4x150 SE | 16 | 33 | 0.0088231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3372-1_0_4_line_26 | NAYY 4x150 SE | 17 | 102 | 0.021155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3372-1_0_4_line_27 | NAYY 4x150 SE | 18 | 19 | 0.011406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3372-1_0_4_line_28 | NAYY 4x150 SE | 18 | 20 | 0.015934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3372-1_0_4_line_29 | NAYY 4x150 SE | 19 | 108 | 0.0057753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3372-1_0_4_line_30 | NAYY 4x150 SE | 20 | 126 | 0.026943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3372-1_0_4_line_31 | NAYY 4x150 SE | 22 | 66 | 0.0071149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3372-1_0_4_line_32 | NAYY 4x150 SE | 24 | 26 | 0.029241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3372-1_0_4_line_33 | NAYY 4x150 SE | 25 | 26 | 0.00247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3372-1_0_4_line_34 | NAYY 4x150 SE | 25 | 27 | 0.015443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3372-1_0_4_line_35 | NAYY 4x150 SE | 28 | 29 | 0.027218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3372-1_0_4_line_36 | NAYY 4x150 SE | 28 | 30 | 0.0034174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3372-1_0_4_line_37 | NAYY 4x150 SE | 29 | 69 | 0.0089965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3372-1_0_4_line_38 | NAYY 4x150 SE | 29 | 67 | 0.002836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3372-1_0_4_line_39 | NAYY 4x150 SE | 30 | 70 | 0.0097485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3372-1_0_4_line_40 | NAYY 4x150 SE | 31 | 63 | 0.015228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3372-1_0_4_line_41 | NAYY 4x150 SE | 32 | 33 | 0.013527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3372-1_0_4_line_42 | NAYY 4x150 SE | 33 | 125 | 0.0081499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3372-1_0_4_line_43 | NAYY 4x150 SE | 34 | 49 | 3.0276e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3372-1_0_4_line_44 | NAYY 4x150 SE | 35 | 42 | 0.0080109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3372-1_0_4_line_45 | NAYY 4x150 SE | 36 | 143 | 0.035483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3372-1_0_4_line_46 | NAYY 4x150 SE | 37 | 38 | 0.045463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3372-1_0_4_line_47 | NAYY 4x150 SE | 38 | 39 | 0.022347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3372-1_0_4_line_48 | NAYY 4x150 SE | 39 | 40 | 0.079663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3372-1_0_4_line_49 | NAYY 4x150 SE | 39 | 41 | 0.001949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3372-1_0_4_line_50 | NAYY 4x150 SE | 40 | 44 | 0.010225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3372-1_0_4_line_51 | NAYY 4x150 SE | 40 | 45 | 0.037897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3372-1_0_4_line_52 | NAYY 4x150 SE | 41 | 46 | 0.003675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3372-1_0_4_line_53 | NAYY 4x150 SE | 41 | 47 | 0.010953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3372-1_0_4_line_54 | NAYY 4x150 SE | 42 | 43 | 0.019086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3372-1_0_4_line_55 | NAYY 4x150 SE | 43 | 48 | 0.046835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3372-1_0_4_line_56 | NAYY 4x150 SE | 44 | 137 | 0.021144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3372-1_0_4_line_57 | NAYY 4x150 SE | 45 | 134 | 0.022504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3372-1_0_4_line_58 | NAYY 4x150 SE | 46 | 136 | 0.022486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3372-1_0_4_line_59 | NAYY 4x150 SE | 47 | 144 | 0.03121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3372-1_0_4_line_60 | NAYY 4x150 SE | 48 | 128 | 0.02707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3372-1_0_4_line_61 | NAYY 4x150 SE | 50 | 51 | 0.0036157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3372-1_0_4_line_62 | NAYY 4x150 SE | 51 | 52 | 0.010853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3372-1_0_4_line_63 | NAYY 4x150 SE | 51 | 53 | 0.010576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3372-1_0_4_line_64 | NAYY 4x150 SE | 52 | 57 | 0.020487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3372-1_0_4_line_65 | NAYY 4x150 SE | 52 | 58 | 0.0054264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3372-1_0_4_line_66 | NAYY 4x150 SE | 53 | 59 | 0.0015323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3372-1_0_4_line_67 | NAYY 4x150 SE | 54 | 55 | 0.019062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3372-1_0_4_line_68 | NAYY 4x150 SE | 54 | 56 | 0.011343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3372-1_0_4_line_69 | NAYY 4x150 SE | 56 | 60 | 0.012233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3372-1_0_4_line_70 | NAYY 4x150 SE | 56 | 57 | 0.005644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3372-1_0_4_line_71 | NAYY 4x150 SE | 57 | 61 | 0.001898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3372-1_0_4_line_72 | NAYY 4x150 SE | 59 | 62 | 0.0293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3372-1_0_4_line_73 | NAYY 4x150 SE | 62 | 69 | 0.015115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3372-1_0_4_line_74 | NAYY 4x150 SE | 63 | 64 | 0.027006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3372-1_0_4_line_75 | NAYY 4x150 SE | 63 | 65 | 0.038454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3372-1_0_4_line_76 | NAYY 4x150 SE | 64 | 71 | 0.011858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3372-1_0_4_line_77 | NAYY 4x150 SE | 64 | 72 | 0.013855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3372-1_0_4_line_78 | NAYY 4x150 SE | 65 | 73 | 0.00901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3372-1_0_4_line_79 | NAYY 4x150 SE | 66 | 77 | 0.014866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3372-1_0_4_line_80 | NAYY 4x150 SE | 67 | 68 | 0.019906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3372-1_0_4_line_81 | NAYY 4x150 SE | 68 | 133 | 0.03262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3372-1_0_4_line_82 | NAYY 4x150 SE | 70 | 78 | 0.014082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3372-1_0_4_line_83 | NAYY 4x150 SE | 71 | 76 | 0.012033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3372-1_0_4_line_84 | NAYY 4x150 SE | 72 | 110 | 0.014045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3372-1_0_4_line_85 | NAYY 4x150 SE | 73 | 74 | 0.0028308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_3372-1_0_4_line_86 | NAYY 4x150 SE | 75 | 76 | 0.017832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3372-1_0_4_line_87 | NAYY 4x150 SE | 77 | 78 | 0.015793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3372-1_0_4_line_88 | NAYY 4x150 SE | 79 | 80 | 0.0097335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3372-1_0_4_line_89 | NAYY 4x150 SE | 79 | 81 | 0.10932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3372-1_0_4_line_90 | NAYY 4x150 SE | 80 | 82 | 0.14243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3372-1_0_4_line_91 | NAYY 4x150 SE | 81 | 83 | 0.084909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_3372-1_0_4_line_92 | NAYY 4x150 SE | 82 | 87 | 0.15265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3372-1_0_4_line_93 | NAYY 4x150 SE | 82 | 88 | 0.11248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3372-1_0_4_line_94 | NAYY 4x150 SE | 83 | 89 | 0.066957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_3372-1_0_4_line_95 | NAYY 4x150 SE | 84 | 85 | 0.12484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_3372-1_0_4_line_96 | NAYY 4x150 SE | 84 | 86 | 0.022182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3372-1_0_4_line_97 | NAYY 4x150 SE | 85 | 140 | 0.0049433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3372-1_0_4_line_98 | NAYY 4x150 SE | 87 | 153 | 0.097255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3372-1_0_4_line_99 | NAYY 4x150 SE | 88 | 160 | 0.1288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3372-1_0_4_line_100 | NAYY 4x150 SE | 89 | 90 | 0.0018189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3372-1_0_4_line_101 | NAYY 4x150 SE | 90 | 102 | 0.16666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3372-1_0_4_line_102 | NAYY 4x150 SE | 91 | 92 | 0.0065077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3372-1_0_4_line_103 | NAYY 4x150 SE | 91 | 93 | 0.0069868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3372-1_0_4_line_104 | NAYY 4x150 SE | 92 | 94 | 0.033264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3372-1_0_4_line_105 | NAYY 4x150 SE | 93 | 95 | 0.0093868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3372-1_0_4_line_106 | NAYY 4x150 SE | 94 | 96 | 0.033531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3372-1_0_4_line_107 | NAYY 4x150 SE | 94 | 97 | 0.092851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3372-1_0_4_line_108 | NAYY 4x150 SE | 95 | 98 | 0.010861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3372-1_0_4_line_109 | NAYY 4x150 SE | 96 | 99 | 0.046993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3372-1_0_4_line_110 | NAYY 4x150 SE | 96 | 100 | 0.029361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_3372-1_0_4_line_111 | NAYY 4x150 SE | 98 | 101 | 0.0064016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3372-1_0_4_line_112 | NAYY 4x150 SE | 99 | 117 | 0.025213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_3372-1_0_4_line_113 | NAYY 4x150 SE | 99 | 118 | 0.034901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3372-1_0_4_line_114 | NAYY 4x150 SE | 99 | 119 | 0.024575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3372-1_0_4_line_115 | NAYY 4x150 SE | 100 | 120 | 0.018008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3372-1_0_4_line_116 | NAYY 4x150 SE | 101 | 109 | 0.0041172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3372-1_0_4_line_117 | NAYY 4x150 SE | 102 | 103 | 0.0094874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3372-1_0_4_line_118 | NAYY 4x150 SE | 103 | 104 | 0.010828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3372-1_0_4_line_119 | NAYY 4x150 SE | 104 | 105 | 0.029638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3372-1_0_4_line_120 | NAYY 4x150 SE | 105 | 106 | 0.022079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3372-1_0_4_line_121 | NAYY 4x150 SE | 105 | 107 | 0.066988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3372-1_0_4_line_122 | NAYY 4x150 SE | 107 | 140 | 0.023332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3372-1_0_4_line_123 | NAYY 4x150 SE | 107 | 138 | 0.050376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3372-1_0_4_line_124 | NAYY 4x150 SE | 110 | 111 | 0.11277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3372-1_0_4_line_125 | NAYY 4x150 SE | 110 | 112 | 0.032729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3372-1_0_4_line_126 | NAYY 4x150 SE | 111 | 113 | 0.061888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3372-1_0_4_line_127 | NAYY 4x150 SE | 113 | 114 | 0.1251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3372-1_0_4_line_128 | NAYY 4x150 SE | 114 | 132 | 0.12528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3372-1_0_4_line_129 | NAYY 4x150 SE | 115 | 116 | 0.18809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3372-1_0_4_line_130 | NAYY 4x150 SE | 116 | 148 | 0.017122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3372-1_0_4_line_131 | NAYY 4x150 SE | 118 | 126 | 0.006555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3372-1_0_4_line_132 | NAYY 4x150 SE | 118 | 127 | 0.023055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3372-1_0_4_line_133 | NAYY 4x150 SE | 118 | 123 | 0.025288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3372-1_0_4_line_134 | NAYY 4x150 SE | 121 | 122 | 0.019474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3372-1_0_4_line_135 | NAYY 4x150 SE | 121 | 123 | 0.0022013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3372-1_0_4_line_136 | NAYY 4x150 SE | 122 | 124 | 0.014672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3372-1_0_4_line_137 | NAYY 4x150 SE | 123 | 125 | 0.0089128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3372-1_0_4_line_138 | NAYY 4x150 SE | 129 | 130 | 0.033853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3372-1_0_4_line_139 | NAYY 4x150 SE | 130 | 131 | 0.038343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3372-1_0_4_line_140 | NAYY 4x150 SE | 130 | 132 | 0.2404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3372-1_0_4_line_141 | NAYY 4x150 SE | 133 | 146 | 0.024721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3372-1_0_4_line_142 | NAYY 4x150 SE | 134 | 135 | 0.0025206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3372-1_0_4_line_143 | NAYY 4x150 SE | 136 | 145 | 0.02248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3372-1_0_4_line_144 | NAYY 4x150 SE | 137 | 152 | 0.0057104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3372-1_0_4_line_145 | NAYY 4x150 SE | 138 | 139 | 0.014247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3372-1_0_4_line_146 | NAYY 4x150 SE | 140 | 141 | 0.12852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3372-1_0_4_line_147 | NAYY 4x150 SE | 141 | 142 | 0.071158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3372-1_0_4_line_148 | NAYY 4x150 SE | 142 | 158 | 0.011499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3372-1_0_4_line_149 | NAYY 4x150 SE | 143 | 144 | 0.032172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_3372-1_0_4_line_150 | NAYY 4x150 SE | 146 | 147 | 0.047741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_3372-1_0_4_line_151 | NAYY 4x150 SE | 148 | 149 | 0.0335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_3372-1_0_4_line_152 | NAYY 4x150 SE | 149 | 150 | 0.047363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_3372-1_0_4_line_153 | NAYY 4x150 SE | 150 | 151 | 0.097775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_3372-1_0_4_line_154 | NAYY 4x150 SE | 151 | 152 | 0.02545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_3372-1_0_4_line_155 | NAYY 4x150 SE | 153 | 154 | 0.020898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_3372-1_0_4_line_156 | NAYY 4x150 SE | 154 | 156 | 0.017739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_3372-1_0_4_line_157 | NAYY 4x150 SE | 155 | 156 | 0.003298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_3372-1_0_4_line_158 | NAYY 4x150 SE | 155 | 157 | 0.0204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_3372-1_0_4_line_159 | NAYY 4x150 SE | 156 | 162 | 0.087432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_3372-1_0_4_line_160 | NAYY 4x150 SE | 157 | 159 | 0.0014661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_3372-1_0_4_line_161 | NAYY 4x150 SE | 161 | 162 | 0.077008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3372-1_0_4_trafo_6 | 0.25 MVA 20/0.4 kV | 163 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2731374.2569 | 1240320.638 | 2731379.6113 | 1240320.689
1 | 2731374.2569 | 1240320.638 | 2731368.4704 | 1240320.6099 | 2731359.8432 | 1240320.0741 | 2731359.6536 | 1240325.2188 | 2731359.7331 | 1240338.71
2 | 2731351.6738 | 1240337.8086 | 2731357.2282 | 1240338.4098 | 2731359.7331 | 1240338.71
3 | 2731359.7331 | 1240338.71 | 2731360.1 | 1240343.322 | 2731360.9843 | 1240353.2613 | 2731362.3578 | 1240361.4877
4 | 2731394.7536 | 1240293.8462 | 2731397.6531 | 1240297.8472 | 2731405.5802 | 1240303.6943
5 | 2731394.7536 | 1240293.8462 | 2731387.7107 | 1240293.8459
6 | 2731394.7536 | 1240293.8462 | 2731399.3682 | 1240288.0434 | 2731404.5095 | 1240284.7543 | 2731410.4141 | 1240279.1135 | 2731424.1612 | 1240260.6018 | 2731446.0812 | 1240230.0274 | 2731459.1804 | 1240211.7461 | 2731465.0687 | 1240203.0661
7 | 2731405.5802 | 1240303.6943 | 2731407.1202 | 1240314.7713 | 2731409.111 | 1240331.1073 | 2731409.3687 | 1240332.2005
8 | 2731387.7107 | 1240293.8459 | 2731387.2178 | 1240289.7982 | 2731384.957 | 1240289.7735
9 | 2731501.752 | 1240151.8817 | 2731493.6662 | 1240162.7453 | 2731476.0962 | 1240186.8103 | 2731465.0687 | 1240203.0661
10 | 2731357.7473 | 1240293.1045 | 2731356.8145 | 1240305.5056 | 2731356.4439 | 1240316.136
11 | 2731352.9201 | 1240286.6477 | 2731357.3803 | 1240286.4462 | 2731357.7473 | 1240293.1045
12 | 2731357.7473 | 1240293.1045 | 2731352.2848 | 1240292.4497 | 2731345.4181 | 1240293.0316 | 2731334.9107 | 1240294.0271
13 | 2731356.1512 | 1240324.5296 | 2731356.4439 | 1240316.136
14 | 2731352.9201 | 1240286.6477 | 2731351.9545 | 1240269.3386
15 | 2731363.2483 | 1240286.5539 | 2731357.3803 | 1240286.4462 | 2731352.9201 | 1240286.6477
16 | 2731352.9201 | 1240286.6477 | 2731353.059 | 1240288.5746 | 2731352.4807 | 1240289.7517 | 2731350.3493 | 1240290.3495 | 2731336.7203 | 1240291.2377 | 2731336.4016 | 1240291.2737
17 | 2731312.4036 | 1240296.1596 | 2731334.9107 | 1240294.0271
18 | 2731370.0733 | 1240289.9078 | 2731376.3345 | 1240289.6795 | 2731384.957 | 1240289.7735
19 | 2731351.6738 | 1240337.8086 | 2731344.1479 | 1240336.7301 | 2731338.8167 | 1240336.0964
20 | 2731351.6738 | 1240337.8086 | 2731348.6987 | 1240346.7839 | 2731345.8198 | 1240356.1166
21 | 2731351.6738 | 1240337.8086 | 2731356.1512 | 1240324.5296
22 | 2731364.2904 | 1240373.7174 | 2731363.5691 | 1240368.743 | 2731362.3578 | 1240361.4877
23 | 2731363.2483 | 1240286.5539 | 2731365.9126 | 1240288.8815 | 2731370.0733 | 1240289.9078
24 | 2731363.2483 | 1240286.5539 | 2731361.9778 | 1240281.755 | 2731361.273 | 1240275.9388
25 | 2731411.3929 | 1240340.7883 | 2731409.3687 | 1240332.2005
26 | 2731501.752 | 1240151.8817 | 2731517.4502 | 1240158.6797 | 2731520.3145 | 1240161.5403
27 | 2731430.4122 | 1240290.5438 | 2731434.6567 | 1240287.4462 | 2731438.7325 | 1240282.8388
28 | 2731430.4122 | 1240290.5438 | 2731430.589 | 1240297.5871 | 2731430.826 | 1240306.4722
29 | 2731438.7325 | 1240282.8388 | 2731441.6711 | 1240279.5169 | 2731442.4101 | 1240278.3989
30 | 2731429.7006 | 1240333.2426 | 2731430.9234 | 1240328.5879 | 2731431.2418 | 1240323.435 | 2731431.0766 | 1240315.8692 | 2731430.826 | 1240306.4722
31 | 2731351.5581 | 1240262.2348 | 2731351.9545 | 1240269.3386
32 | 2731358.6966 | 1240246.8189 | 2731359.0881 | 1240254.0783 | 2731360.7306 | 1240271.4629 | 2731361.273 | 1240275.9388
33 | 2731358.5015 | 1240244.3569 | 2731358.6966 | 1240246.8189
34 | 2731358.5015 | 1240244.3569 | 2731362.468 | 1240243.2215 | 2731365.829 | 1240242.7843 | 2731373.678 | 1240241.6703
35 | 2731347.2878 | 1240180.5761 | 2731350.7905 | 1240207.5657
36 | 2731350.7905 | 1240207.5657 | 2731347.3931 | 1240207.9353
37 | 2731347.2878 | 1240180.5761 | 2731346.1305 | 1240171.6543
38 | 2731350.1034 | 1240180.1713 | 2731347.2878 | 1240180.5761
39 | 2731347.3931 | 1240207.9353 | 2731348.4342 | 1240217.628
40 | 2731312.4036 | 1240296.1596 | 2731307.0099 | 1240296.8409 | 2731297.2474 | 1240298.0371
41 | 2731411.3929 | 1240340.7883 | 2731407.2621 | 1240342.8542 | 2731401.4164 | 1240343.7923 | 2731399.4241 | 1240346.0187
42 | 2731411.3929 | 1240340.7883 | 2731414.7267 | 1240342.9418 | 2731416.4198 | 1240346.7646
43 | 2731338.8167 | 1240336.0964 | 2731338.7866 | 1240336.0928
44 | 2731343.4584 | 1240363.7715 | 2731345.8198 | 1240356.1166
45 | 2731369.4318 | 1240408.8256 | 2731365.3147 | 1240380.7808 | 2731364.2904 | 1240373.7174
46 | 2731367.3179 | 1240414.3799 | 2731369.6219 | 1240429.8407 | 2731371.0412 | 1240443.9732 | 2731372.1903 | 1240459.5586
47 | 2731373.8335 | 1240481.8454 | 2731372.1903 | 1240459.5586
48 | 2731373.8335 | 1240481.8454 | 2731376.2946 | 1240502.5622 | 2731378.14 | 1240510.7768 | 2731381.1032 | 1240518.727 | 2731385.8863 | 1240529.5533 | 2731390.7108 | 1240538.5123 | 2731401.9507 | 1240554.953
49 | 2731375.775 | 1240481.6215 | 2731373.8335 | 1240481.8454
50 | 2731401.9507 | 1240554.953 | 2731407.2256 | 1240563.7218
51 | 2731401.9507 | 1240554.953 | 2731438.0825 | 1240543.5216
52 | 2731379.4378 | 1240481.2133 | 2731375.775 | 1240481.6215
53 | 2731375.775 | 1240481.6215 | 2731374.8367 | 1240470.7085
54 | 2731343.4584 | 1240363.7715 | 2731338.8722 | 1240382.2986
55 | 2731327.6491 | 1240427.7693 | 2731337.4434 | 1240388.0705 | 2731338.8722 | 1240382.2986
56 | 2731407.2256 | 1240563.7218 | 2731398.495 | 1240569.578 | 2731389.6573 | 1240575.4875
57 | 2731459.5382 | 1240536.7334 | 2731438.0825 | 1240543.5216
58 | 2731379.4378 | 1240481.2133 | 2731401.7796 | 1240478.6723
59 | 2731374.8367 | 1240470.7085 | 2731374.6321 | 1240468.3292 | 2731374.569 | 1240462.3004 | 2731373.3454 | 1240444.1132 | 2731375.1928 | 1240439.9394
60 | 2731327.6491 | 1240427.7693 | 2731327.5954 | 1240427.9871 | 2731320.4166 | 1240453.8554
61 | 2731311.9973 | 1240150.4806 | 2731311.4767 | 1240146.9026
62 | 2731311.9973 | 1240150.4806 | 2731303.8693 | 1240151.3015 | 2731301.1762 | 1240151.6423
63 | 2731313.6498 | 1240160.9261 | 2731311.9973 | 1240150.4806
64 | 2731297.841 | 1240131.4289 | 2731301.1762 | 1240151.6423
65 | 2731301.1762 | 1240151.6423 | 2731301.7515 | 1240157.0381
66 | 2731313.6498 | 1240160.9261 | 2731315.1674 | 1240160.7146
67 | 2731308.1302 | 1240123.8833 | 2731308.7809 | 1240121.8292 | 2731312.0377 | 1240119.2657 | 2731317.1055 | 1240117.2538 | 2731324.3164 | 1240116.0531
68 | 2731296.9279 | 1240125.8594 | 2731308.1302 | 1240123.8833
69 | 2731296.9279 | 1240125.8594 | 2731297.9617 | 1240113.6718
70 | 2731297.841 | 1240131.4289 | 2731296.9279 | 1240125.8594
71 | 2731295.9721 | 1240131.7878 | 2731297.841 | 1240131.4289
72 | 2731344.186 | 1240156.6646 | 2731329.4187 | 1240158.7286 | 2731315.1674 | 1240160.7146
73 | 2731344.186 | 1240156.6646 | 2731346.1305 | 1240171.6543
74 | 2731297.2474 | 1240298.0371 | 2731270.3644 | 1240301.3344
75 | 2731297.2474 | 1240298.0371 | 2731298.3634 | 1240312.8968 | 2731298.9161 | 1240325.5199 | 2731298.6745 | 1240336.4342
76 | 2731270.3644 | 1240301.3344 | 2731270.2568 | 1240297.651 | 2731278.409 | 1240297.063
77 | 2731270.3644 | 1240301.3344 | 2731263.0626 | 1240301.7511 | 2731256.5217 | 1240301.8125
78 | 2731295.0485 | 1240344.4062 | 2731297.7407 | 1240341.0295 | 2731298.6715 | 1240336.5685 | 2731298.6745 | 1240336.4342
79 | 2731351.5581 | 1240262.2348 | 2731351.4038 | 1240259.4685 | 2731350.9284 | 1240247.3829
80 | 2731350.1034 | 1240180.1713 | 2731348.3757 | 1240168.3451 | 2731347.252 | 1240160.4705
81 | 2731347.252 | 1240160.4705 | 2731345.3305 | 1240147.0038 | 2731342.4027 | 1240128.2137
82 | 2731349.938 | 1240231.6291 | 2731348.4342 | 1240217.628
83 | 2731290.3972 | 1240296.0292 | 2731282.88 | 1240296.7405 | 2731278.409 | 1240297.063
84 | 2731242.5299 | 1240300.7963 | 2731248.9046 | 1240301.5935 | 2731256.3587 | 1240301.814 | 2731256.5217 | 1240301.8125
85 | 2731295.0485 | 1240344.4062 | 2731294.4557 | 1240341.6382
86 | 2731290.3972 | 1240296.0292 | 2731308.1499 | 1240294.3493
87 | 2731349.938 | 1240231.6291 | 2731350.5229 | 1240237.0741 | 2731350.9284 | 1240247.3829
88 | 2731881.6462 | 1239988.0223 | 2731881.6462 | 1239988.0223 | 2731873.5964 | 1239989.0555 | 2731871.9818 | 1239988.9568
89 | 2731768.4638 | 1239966.791 | 2731785.7301 | 1239963.627 | 2731795.7132 | 1239962.7479 | 2731805.2308 | 1239963.4153 | 2731814.8714 | 1239966.0316 | 2731825.6625 | 1239971.0088 | 2731844.4257 | 1239981.5122 | 2731855.0717 | 1239986.2083 | 2731864.7343 | 1239988.5138 | 2731871.9818 | 1239988.9568
90 | 2731881.6462 | 1239988.0223 | 2731992.4154 | 1240077.5612
91 | 2731768.4638 | 1239966.791 | 2731754.7695 | 1239970.924 | 2731737.4833 | 1239978.0465 | 2731718.962 | 1239986.9655 | 2731691.1392 | 1240001.8501
92 | 2731992.4154 | 1240077.5612 | 2732102.0334 | 1239971.3296
93 | 2731992.4154 | 1240077.5612 | 2731991.6937 | 1240089.9336 | 2731991.1815 | 1240102.7555 | 2731992.5714 | 1240111.3494 | 2731993.5429 | 1240118.3437 | 2731991.8073 | 1240125.2889 | 2731987.2845 | 1240135.7752 | 2731982.3533 | 1240144.2173 | 2731975.1712 | 1240152.1645 | 2731970.9705 | 1240158.3765 | 2731968.5494 | 1240165.5289 | 2731968.9029 | 1240170.0406 | 2731971.3128 | 1240173.2525 | 2731979.6578 | 1240176.2851
94 | 2731691.1392 | 1240001.8501 | 2731660.5246 | 1240020.1535 | 2731634.8676 | 1240038.0602
95 | 2731628.9486 | 1240224.9857 | 2731612.7774 | 1240200.6506 | 2731609.0379 | 1240195.9859 | 2731605.7101 | 1240194.9223 | 2731602.0827 | 1240196.4544 | 2731598.2363 | 1240202.0628 | 2731592.2286 | 1240215.4079 | 2731587.9846 | 1240222.2308 | 2731580.1487 | 1240228.9852 | 2731570.1518 | 1240237.6711 | 2731566.6864 | 1240243.1546 | 2731565.3009 | 1240249.6851 | 2731563.7101 | 1240254.2204 | 2731558.6786 | 1240257.3227 | 2731553.4294 | 1240256.7872
96 | 2731628.9486 | 1240224.9857 | 2731635.2916 | 1240238.8049 | 2731636.5731 | 1240243.7821 | 2731636.701 | 1240245.6152
97 | 2731548.5116 | 1240256.2854 | 2731553.4294 | 1240256.7872
98 | 2732102.0334 | 1239971.3296 | 2732105.062 | 1239976.3124 | 2732111.1338 | 1239981.552 | 2732122.0346 | 1239986.6879 | 2732124.5206 | 1239988.5226 | 2732128.7536 | 1239992.4202 | 2732135.4254 | 1240002.6441 | 2732137.6955 | 1240007.3765 | 2732140.9074 | 1240009.9058 | 2732147.6251 | 1240014.3369 | 2732163.1784 | 1240023.5466 | 2732170.9322 | 1240025.2763 | 2732174.2759 | 1240025.284 | 2732177.8097 | 1240024.9068
99 | 2732056.3969 | 1240279.726 | 2731979.6578 | 1240176.2851
100 | 2731633.376 | 1240039.1012 | 2731634.8676 | 1240038.0602
101 | 2731520.3145 | 1240161.5403 | 2731633.376 | 1240039.1012
102 | 2731476.1145 | 1240418.9575 | 2731473.6424 | 1240412.9376
103 | 2731470.9883 | 1240406.4746 | 2731473.6424 | 1240412.9376
104 | 2731472.2542 | 1240447.5279 | 2731476.378 | 1240445.0949 | 2731478.8181 | 1240442.5134 | 2731480.9055 | 1240437.7555 | 2731481.303 | 1240433.4717 | 2731478.6439 | 1240425.1167 | 2731476.1145 | 1240418.9575
105 | 2731467.4224 | 1240397.7915 | 2731470.9883 | 1240406.4746
106 | 2731472.2542 | 1240447.5279 | 2731460.1556 | 1240416.2441
107 | 2731472.2542 | 1240447.5279 | 2731477.7986 | 1240461.8853 | 2731493.508 | 1240498.854 | 2731503.5893 | 1240516.7039 | 2731513.678 | 1240530.1278
108 | 2731467.4224 | 1240397.7915 | 2731463.2966 | 1240387.7446
109 | 2731442.8323 | 1240372.5451 | 2731454.9972 | 1240402.8961 | 2731460.1556 | 1240416.2441
110 | 2731460.1556 | 1240416.2441 | 2731458.5654 | 1240420.0677 | 2731458.1349 | 1240423.45 | 2731459.0514 | 1240435.0025 | 2731460.9992 | 1240443.0303 | 2731461.6752 | 1240444.8704
111 | 2731460.8648 | 1240381.823 | 2731463.2966 | 1240387.7446
112 | 2731442.8323 | 1240372.5451 | 2731439.4652 | 1240382.4791 | 2731437.7686 | 1240390.4261 | 2731437.0181 | 1240396.9819
113 | 2731431.4366 | 1240339.5643 | 2731434.3238 | 1240348.9029 | 2731442.8323 | 1240372.5451
114 | 2731442.8323 | 1240372.5451 | 2731446.2689 | 1240370.7418 | 2731447.647 | 1240368.2924 | 2731447.9734 | 1240362.439 | 2731446.5381 | 1240350.5042
115 | 2731465.7321 | 1240462.3595 | 2731464.3088 | 1240454.1243 | 2731463.3964 | 1240449.5557 | 2731461.6752 | 1240444.8704
116 | 2731459.3007 | 1240378.0144 | 2731460.8648 | 1240381.823
117 | 2731527.0274 | 1240168.2446 | 2731520.3145 | 1240161.5403
118 | 2731522.8515 | 1240178.1384 | 2731523.6079 | 1240174.73 | 2731525.4172 | 1240170.9223 | 2731527.0274 | 1240168.2446
119 | 2731522.8515 | 1240178.1384 | 2731530.6137 | 1240171.6381 | 2731534.3303 | 1240175.635 | 2731535.6174 | 1240178.9997 | 2731535.3821 | 1240182.7867 | 2731533.2676 | 1240189.1008
120 | 2731533.2676 | 1240189.1008 | 2731530.382 | 1240189.5929 | 2731525.1247 | 1240193.3241 | 2731516.8977 | 1240203.0502
121 | 2731525.1627 | 1240254.7334 | 2731525.0598 | 1240246.7465 | 2731524.6338 | 1240221.949 | 2731525.44 | 1240212.8813 | 2731527.4648 | 1240204.1297 | 2731533.2676 | 1240189.1008
122 | 2731525.1627 | 1240254.7334 | 2731548.5116 | 1240256.2854
123 | 2731525.1627 | 1240254.7334 | 2731525.3332 | 1240268.538 | 2731527.0444 | 1240282.4546 | 2731527.0319 | 1240291.5511 | 2731523.6521 | 1240298.2931 | 2731519.5632 | 1240302.5618
124 | 2731169.5931 | 1240223.6401 | 2731183.2254 | 1240259.5501 | 2731186.1839 | 1240266.021 | 2731190.7242 | 1240272.4602 | 2731195.5204 | 1240277.2481 | 2731200.4434 | 1240280.7488 | 2731206.8976 | 1240284.4502 | 2731223.496 | 1240292.9577 | 2731233.1691 | 1240297.5088 | 2731242.5299 | 1240300.7963
125 | 2731242.5299 | 1240300.7963 | 2731237.9041 | 1240306.0875 | 2731232.8449 | 1240307.3768 | 2731218.6259 | 1240310.3206 | 2731212.821 | 1240311.6672
126 | 2731169.5931 | 1240223.6401 | 2731157.8769 | 1240222.5248 | 2731140.6163 | 1240218.2954 | 2731121.1916 | 1240212.3724 | 2731109.4248 | 1240209.0986
127 | 2731109.4248 | 1240209.0986 | 2731109.7098 | 1240084.0022
128 | 2731076.3483 | 1239964.7468 | 2731079.7612 | 1239976.3433 | 2731082.8262 | 1239988.6215 | 2731085.3595 | 1239998.5971 | 2731086.5113 | 1240006.7296 | 2731086.8636 | 1240013.0428 | 2731087.1293 | 1240024.9811 | 2731087.9786 | 1240034.8195 | 2731089.8801 | 1240041.8898 | 2731093.3849 | 1240050.3522 | 2731103.3933 | 1240070.2236 | 2731109.7098 | 1240084.0022
129 | 2731200.4869 | 1240609.0544 | 2731027.5491 | 1240535.1052
130 | 2731216.1777 | 1240615.9077 | 2731207.1717 | 1240611.9942 | 2731200.4869 | 1240609.0544
131 | 2731429.7006 | 1240333.2426 | 2731431.4366 | 1240339.5643
132 | 2731431.4366 | 1240339.5643 | 2731436.6974 | 1240326.4472 | 2731439.6101 | 1240318.0137
133 | 2731420.0292 | 1240354.9139 | 2731427.823 | 1240351.4056 | 2731434.3238 | 1240348.9029 | 2731431.4366 | 1240339.5643
134 | 2731418.4423 | 1240356.4396 | 2731416.9992 | 1240357.8271 | 2731414.8774 | 1240361.4055 | 2731413.6062 | 1240367.2268 | 2731413.7578 | 1240374.5785
135 | 2731420.0292 | 1240354.9139 | 2731418.4423 | 1240356.4396
136 | 2731414.3213 | 1240389.2394 | 2731413.814 | 1240377.3068 | 2731413.7578 | 1240374.5785
137 | 2731420.0292 | 1240354.9139 | 2731416.4198 | 1240346.7646
138 | 2730861.8594 | 1240073.3199 | 2730856.402 | 1240075.1679 | 2730850.2713 | 1240077.3569 | 2730845.8537 | 1240079.7393 | 2730840.6002 | 1240083.3155 | 2730836.5149 | 1240084.6933 | 2730832.9689 | 1240084.2593 | 2730830.6881 | 1240083.8188
139 | 2730861.8594 | 1240073.3199 | 2730857.4861 | 1240069.9206 | 2730852.9422 | 1240065.3387 | 2730847.4524 | 1240060.0799 | 2730839.3239 | 1240054.0622 | 2730832.5127 | 1240048.7548
140 | 2730861.8594 | 1240073.3199 | 2731076.3483 | 1239964.7468
141 | 2731338.4478 | 1240103.8123 | 2731339.1448 | 1240108.2781 | 2731340.601 | 1240116.6508 | 2731342.4027 | 1240128.2137
142 | 2731459.5382 | 1240536.7334 | 2731461.9414 | 1240535.9731
143 | 2731411.779 | 1240459.9441 | 2731411.779 | 1240459.9441 | 2731408.2061 | 1240461.0771 | 2731401.7796 | 1240478.6723
144 | 2731385.7228 | 1240579.6262 | 2731389.6573 | 1240575.4875
145 | 2731507.3786 | 1240301.769 | 2731510.729 | 1240304.8792 | 2731514.8168 | 1240305.4369 | 2731519.5632 | 1240302.5618
146 | 2731548.5116 | 1240256.2854 | 2731589.9422 | 1240338.2521 | 2731612.4073 | 1240367.353
147 | 2731612.4073 | 1240367.353 | 2731618.9314 | 1240409.8232 | 2731631.7717 | 1240434.9184
148 | 2731631.2482 | 1240446.3945 | 2731631.5749 | 1240443.7884 | 2731631.7717 | 1240434.9184
149 | 2731369.4318 | 1240408.8256 | 2731370.2906 | 1240414.6757 | 2731372.5929 | 1240417.974 | 2731372.9478 | 1240423.8091 | 2731374.2373 | 1240427.4074 | 2731375.1928 | 1240439.9394 | 2731375.1928 | 1240439.9394
150 | 2731328.7323 | 1240057.1181 | 2731329.1685 | 1240062.0509 | 2731330.5745 | 1240067.9092 | 2731334.3236 | 1240084.1172 | 2731337.8595 | 1240100.0425 | 2731338.4478 | 1240103.8123
151 | 2731216.1777 | 1240615.9077 | 2731216.1777 | 1240615.9077 | 2731223.8862 | 1240620.6822 | 2731228.6063 | 1240625.1348 | 2731232.9174 | 1240627.5544 | 2731236.7126 | 1240627.9943 | 2731240.1762 | 1240626.6697 | 2731242.3056 | 1240621.6303
152 | 2731282.1788 | 1240613.4759 | 2731273.8886 | 1240614.1376 | 2731265.997 | 1240614.2187 | 2731257.7401 | 1240613.0351 | 2731248.3406 | 1240610.1582 | 2731243.8402 | 1240617.9988 | 2731242.3056 | 1240621.6303
153 | 2731379.5095 | 1240604.1603 | 2731282.1788 | 1240613.4759
154 | 2731385.7228 | 1240579.6262 | 2731383.0277 | 1240585.5273 | 2731380.1146 | 1240600.5869 | 2731379.5095 | 1240604.1603
155 | 2732177.8097 | 1240024.9068 | 2732178.855 | 1240035.3725 | 2732180.2122 | 1240041.3523 | 2732181.8701 | 1240045.2637
156 | 2732190.8375 | 1240060.5388 | 2732186.8717 | 1240054.5008 | 2732182.6487 | 1240047.1004 | 2732181.8701 | 1240045.2637
157 | 2732190.8375 | 1240060.5388 | 2732188.3456 | 1240062.7074
158 | 2732188.3456 | 1240062.7074 | 2732181.9269 | 1240068.2915 | 2732172.6247 | 1240075.7012
159 | 2732269.9644 | 1240093.7075 | 2732250.9557 | 1240089.5138 | 2732235.9692 | 1240086.7887 | 2732227.9006 | 1240084.596 | 2732221.3323 | 1240081.9586 | 2732213.0413 | 1240077.1809 | 2732201.3117 | 1240069.869 | 2732195.2871 | 1240065.5755 | 2732190.8375 | 1240060.5388
160 | 2732171.478 | 1240076.6147 | 2732172.6247 | 1240075.7012
161 | 2732269.9644 | 1240093.7075 | 2732266.4729 | 1240106.4408 | 2732267.5506 | 1240115.1056 | 2732263.031 | 1240127.8048 | 2732256.038 | 1240141.1606 | 2732254.68 | 1240142.0088 | 2732248.9755 | 1240137.956 | 2732244.1472 | 1240136.336 | 2732237.3406 | 1240136.5846 | 2732233.703 | 1240137.8825 | 2732233.0596 | 1240139.9366

## bus_geodata
| x | y | coords
0 | 2731379.6113 | 1240320.689
1 | 2731374.2569 | 1240320.638
2 | 2731359.7331 | 1240338.71
3 | 2731394.7536 | 1240293.8462
4 | 2731405.5802 | 1240303.6943
5 | 2731387.7107 | 1240293.8459
6 | 2731465.0687 | 1240203.0661
7 | 2731357.7473 | 1240293.1045
8 | 2731356.4439 | 1240316.136
9 | 2731352.9201 | 1240286.6477
10 | 2731334.9107 | 1240294.0271
11 | 2731384.957 | 1240289.7735
12 | 2731351.6738 | 1240337.8086
13 | 2731362.3578 | 1240361.4877
14 | 2731370.0733 | 1240289.9078
15 | 2731363.2483 | 1240286.5539
16 | 2731409.3687 | 1240332.2005
17 | 2731501.7521 | 1240151.8817
18 | 2731430.4122 | 1240290.5438
19 | 2731438.7325 | 1240282.8388
20 | 2731430.826 | 1240306.4722
21 | 2731356.1512 | 1240324.5296
22 | 2731351.9545 | 1240269.3386
23 | 2731336.4016 | 1240291.2737
24 | 2731361.273 | 1240275.9388
25 | 2731358.5015 | 1240244.3569
26 | 2731358.6966 | 1240246.8189
27 | 2731373.678 | 1240241.6703
28 | 2731350.7905 | 1240207.5657
29 | 2731347.2878 | 1240180.5761
30 | 2731347.3931 | 1240207.9353
31 | 2731312.4036 | 1240296.1596
32 | 2731399.4241 | 1240346.0187
33 | 2731411.3929 | 1240340.7883
34 | 2731338.8167 | 1240336.0964
35 | 2731345.8198 | 1240356.1166
36 | 2731364.2904 | 1240373.7174
37 | 2731367.3179 | 1240414.3799
38 | 2731372.1903 | 1240459.5586
39 | 2731373.8335 | 1240481.8454
40 | 2731401.9507 | 1240554.953
41 | 2731375.775 | 1240481.6215
42 | 2731343.4584 | 1240363.7715
43 | 2731338.8722 | 1240382.2986
44 | 2731407.2256 | 1240563.7218
45 | 2731438.0825 | 1240543.5216
46 | 2731379.4378 | 1240481.2133
47 | 2731374.8367 | 1240470.7085
48 | 2731327.6491 | 1240427.7693
49 | 2731338.7866 | 1240336.0928
50 | 2731311.4767 | 1240146.9026
51 | 2731311.9973 | 1240150.4806
52 | 2731301.1762 | 1240151.6423
53 | 2731313.6498 | 1240160.9261
54 | 2731308.1302 | 1240123.8833
55 | 2731324.3164 | 1240116.0531
56 | 2731296.9279 | 1240125.8594
57 | 2731297.841 | 1240131.4289
58 | 2731301.7515 | 1240157.0381
59 | 2731315.1674 | 1240160.7146
60 | 2731297.9617 | 1240113.6718
61 | 2731295.9721 | 1240131.7878
62 | 2731344.186 | 1240156.6646
63 | 2731297.2474 | 1240298.0371
64 | 2731270.3644 | 1240301.3344
65 | 2731298.6745 | 1240336.4342
66 | 2731351.5581 | 1240262.2348
67 | 2731350.1034 | 1240180.1713
68 | 2731347.252 | 1240160.4705
69 | 2731346.1305 | 1240171.6543
70 | 2731348.4342 | 1240217.628
71 | 2731278.409 | 1240297.063
72 | 2731256.5218 | 1240301.8125
73 | 2731295.0485 | 1240344.4062
74 | 2731294.4557 | 1240341.6382
75 | 2731308.1499 | 1240294.3493
76 | 2731290.3972 | 1240296.0292
77 | 2731350.9284 | 1240247.3829
78 | 2731349.938 | 1240231.6291
79 | 2731871.9818 | 1239988.9568
80 | 2731881.6462 | 1239988.0223
81 | 2731768.4638 | 1239966.791
82 | 2731992.4154 | 1240077.5612
83 | 2731691.1392 | 1240001.8501
84 | 2731628.9486 | 1240224.9857
85 | 2731553.4294 | 1240256.7872
86 | 2731636.701 | 1240245.6152
87 | 2732102.0334 | 1239971.3296
88 | 2731979.6578 | 1240176.2851
89 | 2731634.8676 | 1240038.0602
90 | 2731633.376 | 1240039.1012
91 | 2731473.6424 | 1240412.9376
92 | 2731476.1145 | 1240418.9575
93 | 2731470.9883 | 1240406.4746
94 | 2731472.2542 | 1240447.5279
95 | 2731467.4224 | 1240397.7915
96 | 2731460.1556 | 1240416.2441
97 | 2731513.678 | 1240530.1278
98 | 2731463.2966 | 1240387.7446
99 | 2731442.8323 | 1240372.5451
100 | 2731461.6752 | 1240444.8704
101 | 2731460.8648 | 1240381.823
102 | 2731520.3145 | 1240161.5403
103 | 2731527.0274 | 1240168.2446
104 | 2731522.8515 | 1240178.1384
105 | 2731533.2676 | 1240189.1008
106 | 2731516.8977 | 1240203.0502
107 | 2731525.1627 | 1240254.7334
108 | 2731442.4101 | 1240278.3989
109 | 2731459.3007 | 1240378.0144
110 | 2731242.5299 | 1240300.7963
111 | 2731169.5931 | 1240223.6401
112 | 2731212.821 | 1240311.6672
113 | 2731109.4248 | 1240209.0986
114 | 2731109.7098 | 1240084.0022
115 | 2731027.5491 | 1240535.1052
116 | 2731200.4869 | 1240609.0544
117 | 2731437.0181 | 1240396.9819
118 | 2731431.4366 | 1240339.5643
119 | 2731446.5381 | 1240350.5042
120 | 2731465.7321 | 1240462.3595
121 | 2731418.4423 | 1240356.4396
122 | 2731413.7578 | 1240374.5785
123 | 2731420.0292 | 1240354.9139
124 | 2731414.3213 | 1240389.2394
125 | 2731416.4198 | 1240346.7646
126 | 2731429.7006 | 1240333.2426
127 | 2731439.6101 | 1240318.0137
128 | 2731320.4166 | 1240453.8554
129 | 2730830.6881 | 1240083.8188
130 | 2730861.8594 | 1240073.3199
131 | 2730832.5127 | 1240048.7548
132 | 2731076.3483 | 1239964.7468
133 | 2731342.4027 | 1240128.2137
134 | 2731459.5382 | 1240536.7334
135 | 2731461.9414 | 1240535.9731
136 | 2731401.7796 | 1240478.6723
137 | 2731389.6573 | 1240575.4875
138 | 2731519.5632 | 1240302.5618
139 | 2731507.3786 | 1240301.769
140 | 2731548.5116 | 1240256.2854
141 | 2731612.4073 | 1240367.353
142 | 2731631.7717 | 1240434.9184
143 | 2731369.4318 | 1240408.8256
144 | 2731375.1928 | 1240439.9394
145 | 2731411.779 | 1240459.9441
146 | 2731338.4478 | 1240103.8123
147 | 2731328.7323 | 1240057.1181
148 | 2731216.1777 | 1240615.9077
149 | 2731242.3056 | 1240621.6303
150 | 2731282.1788 | 1240613.4759
151 | 2731379.5095 | 1240604.1603
152 | 2731385.7228 | 1240579.6262
153 | 2732177.8097 | 1240024.9068
154 | 2732181.8701 | 1240045.2637
155 | 2732188.3456 | 1240062.7074
156 | 2732190.8375 | 1240060.5388
157 | 2732172.6247 | 1240075.7012
158 | 2731631.2482 | 1240446.3945
159 | 2732171.478 | 1240076.6147
160 | 2732056.3969 | 1240279.726
161 | 2732233.0596 | 1240139.9366
162 | 2732269.9644 | 1240093.7075
163 | 2731357.2282 | 1240338.4098

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1