## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3372-2_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3372-2_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3372-2_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3372-2_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3372-2_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_3372-2_0_2_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_3372-2_0_2_node_295 | 0.4 | n |  | TRUE
7 | bus_LV_3372-2_0_2_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_3372-2_0_2_node_164 | 0.4 | n |  | TRUE
9 | bus_LV_3372-2_0_2_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_3372-2_0_2_node_435 | 0.4 | n |  | TRUE
11 | bus_LV_3372-2_0_2_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_3372-2_0_2_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_3372-2_0_2_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_3372-2_0_2_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_3372-2_0_2_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_3372-2_0_2_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_3372-2_0_2_node_68 | 0.4 | n |  | TRUE
18 | bus_LV_3372-2_0_2_node_411 | 0.4 | n |  | TRUE
19 | bus_LV_3372-2_0_2_node_433 | 0.4 | n |  | TRUE
20 | bus_LV_3372-2_0_2_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_3372-2_0_2_node_384 | 0.4 | n |  | TRUE
22 | bus_LV_3372-2_0_2_node_388 | 0.4 | n |  | TRUE
23 | bus_LV_3372-2_0_2_node_273 | 0.4 | n |  | TRUE
24 | bus_LV_3372-2_0_2_node_383 | 0.4 | n |  | TRUE
25 | bus_LV_3372-2_0_2_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_3372-2_0_2_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_3372-2_0_2_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_3372-2_0_2_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_3372-2_0_2_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_3372-2_0_2_node_268 | 0.4 | n |  | TRUE
31 | bus_LV_3372-2_0_2_node_188 | 0.4 | n |  | TRUE
32 | bus_LV_3372-2_0_2_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_3372-2_0_2_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_3372-2_0_2_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_3372-2_0_2_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_3372-2_0_2_node_53 | 0.4 | n |  | TRUE
37 | bus_LV_3372-2_0_2_node_69 | 0.4 | n |  | TRUE
38 | bus_LV_3372-2_0_2_node_80 | 0.4 | n |  | TRUE
39 | bus_LV_3372-2_0_2_node_59 | 0.4 | n |  | TRUE
40 | bus_LV_3372-2_0_2_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_3372-2_0_2_node_61 | 0.4 | n |  | TRUE
42 | bus_LV_3372-2_0_2_node_62 | 0.4 | n |  | TRUE
43 | bus_LV_3372-2_0_2_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_3372-2_0_2_node_65 | 0.4 | n |  | TRUE
45 | bus_LV_3372-2_0_2_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_3372-2_0_2_node_67 | 0.4 | n |  | TRUE
47 | bus_LV_3372-2_0_2_node_77 | 0.4 | n |  | TRUE
48 | bus_LV_3372-2_0_2_node_79 | 0.4 | n |  | TRUE
49 | bus_LV_3372-2_0_2_node_326 | 0.4 | n |  | TRUE
50 | bus_LV_3372-2_0_2_node_81 | 0.4 | n |  | TRUE
51 | bus_LV_3372-2_0_2_node_82 | 0.4 | n |  | TRUE
52 | bus_LV_3372-2_0_2_node_327 | 0.4 | n |  | TRUE
53 | bus_LV_3372-2_0_2_node_99 | 0.4 | n |  | TRUE
54 | bus_LV_3372-2_0_2_node_101 | 0.4 | n |  | TRUE
55 | bus_LV_3372-2_0_2_node_102 | 0.4 | n |  | TRUE
56 | bus_LV_3372-2_0_2_node_217 | 0.4 | n |  | TRUE
57 | bus_LV_3372-2_0_2_node_117 | 0.4 | n |  | TRUE
58 | bus_LV_3372-2_0_2_node_118 | 0.4 | n |  | TRUE
59 | bus_LV_3372-2_0_2_node_119 | 0.4 | n |  | TRUE
60 | bus_LV_3372-2_0_2_node_120 | 0.4 | n |  | TRUE
61 | bus_LV_3372-2_0_2_node_121 | 0.4 | n |  | TRUE
62 | bus_LV_3372-2_0_2_node_391 | 0.4 | n |  | TRUE
63 | bus_LV_3372-2_0_2_node_275 | 0.4 | n |  | TRUE
64 | bus_LV_3372-2_0_2_node_122 | 0.4 | n |  | TRUE
65 | bus_LV_3372-2_0_2_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_3372-2_0_2_node_124 | 0.4 | n |  | TRUE
67 | bus_LV_3372-2_0_2_node_125 | 0.4 | n |  | TRUE
68 | bus_LV_3372-2_0_2_node_126 | 0.4 | n |  | TRUE
69 | bus_LV_3372-2_0_2_node_158 | 0.4 | n |  | TRUE
70 | bus_LV_3372-2_0_2_node_307 | 0.4 | n |  | TRUE
71 | bus_LV_3372-2_0_2_node_159 | 0.4 | n |  | TRUE
72 | bus_LV_3372-2_0_2_node_160 | 0.4 | n |  | TRUE
73 | bus_LV_3372-2_0_2_node_161 | 0.4 | n |  | TRUE
74 | bus_LV_3372-2_0_2_node_162 | 0.4 | n |  | TRUE
75 | bus_LV_3372-2_0_2_node_163 | 0.4 | n |  | TRUE
76 | bus_LV_3372-2_0_2_node_202 | 0.4 | n |  | TRUE
77 | bus_LV_3372-2_0_2_node_364 | 0.4 | n |  | TRUE
78 | bus_LV_3372-2_0_2_node_165 | 0.4 | n |  | TRUE
79 | bus_LV_3372-2_0_2_node_166 | 0.4 | n |  | TRUE
80 | bus_LV_3372-2_0_2_node_167 | 0.4 | n |  | TRUE
81 | bus_LV_3372-2_0_2_node_168 | 0.4 | n |  | TRUE
82 | bus_LV_3372-2_0_2_node_329 | 0.4 | n |  | TRUE
83 | bus_LV_3372-2_0_2_node_200 | 0.4 | n |  | TRUE
84 | bus_LV_3372-2_0_2_node_189 | 0.4 | n |  | TRUE
85 | bus_LV_3372-2_0_2_node_320 | 0.4 | n |  | TRUE
86 | bus_LV_3372-2_0_2_node_192 | 0.4 | n |  | TRUE
87 | bus_LV_3372-2_0_2_node_194 | 0.4 | n |  | TRUE
88 | bus_LV_3372-2_0_2_node_220 | 0.4 | n |  | TRUE
89 | bus_LV_3372-2_0_2_node_198 | 0.4 | n |  | TRUE
90 | bus_LV_3372-2_0_2_node_199 | 0.4 | n |  | TRUE
91 | bus_LV_3372-2_0_2_node_201 | 0.4 | n |  | TRUE
92 | bus_LV_3372-2_0_2_node_389 | 0.4 | n |  | TRUE
93 | bus_LV_3372-2_0_2_node_271 | 0.4 | n |  | TRUE
94 | bus_LV_3372-2_0_2_node_285 | 0.4 | n |  | TRUE
95 | bus_LV_3372-2_0_2_node_212 | 0.4 | n |  | TRUE
96 | bus_LV_3372-2_0_2_node_214 | 0.4 | n |  | TRUE
97 | bus_LV_3372-2_0_2_node_231 | 0.4 | n |  | TRUE
98 | bus_LV_3372-2_0_2_node_218 | 0.4 | n |  | TRUE
99 | bus_LV_3372-2_0_2_node_219 | 0.4 | n |  | TRUE
100 | bus_LV_3372-2_0_2_node_355 | 0.4 | n |  | TRUE
101 | bus_LV_3372-2_0_2_node_354 | 0.4 | n |  | TRUE
102 | bus_LV_3372-2_0_2_node_221 | 0.4 | n |  | TRUE
103 | bus_LV_3372-2_0_2_node_230 | 0.4 | n |  | TRUE
104 | bus_LV_3372-2_0_2_node_318 | 0.4 | n |  | TRUE
105 | bus_LV_3372-2_0_2_node_270 | 0.4 | n |  | TRUE
106 | bus_LV_3372-2_0_2_node_232 | 0.4 | n |  | TRUE
107 | bus_LV_3372-2_0_2_node_233 | 0.4 | n |  | TRUE
108 | bus_LV_3372-2_0_2_node_234 | 0.4 | n |  | TRUE
109 | bus_LV_3372-2_0_2_node_235 | 0.4 | n |  | TRUE
110 | bus_LV_3372-2_0_2_node_236 | 0.4 | n |  | TRUE
111 | bus_LV_3372-2_0_2_node_260 | 0.4 | n |  | TRUE
112 | bus_LV_3372-2_0_2_node_430 | 0.4 | n |  | TRUE
113 | bus_LV_3372-2_0_2_node_256 | 0.4 | n |  | TRUE
114 | bus_LV_3372-2_0_2_node_258 | 0.4 | n |  | TRUE
115 | bus_LV_3372-2_0_2_node_261 | 0.4 | n |  | TRUE
116 | bus_LV_3372-2_0_2_node_262 | 0.4 | n |  | TRUE
117 | bus_LV_3372-2_0_2_node_263 | 0.4 | n |  | TRUE
118 | bus_LV_3372-2_0_2_node_394 | 0.4 | n |  | TRUE
119 | bus_LV_3372-2_0_2_node_427 | 0.4 | n |  | TRUE
120 | bus_LV_3372-2_0_2_node_298 | 0.4 | n |  | TRUE
121 | bus_LV_3372-2_0_2_node_296 | 0.4 | n |  | TRUE
122 | bus_LV_3372-2_0_2_node_272 | 0.4 | n |  | TRUE
123 | bus_LV_3372-2_0_2_node_324 | 0.4 | n |  | TRUE
124 | bus_LV_3372-2_0_2_node_436 | 0.4 | n |  | TRUE
125 | bus_LV_3372-2_0_2_node_274 | 0.4 | n |  | TRUE
126 | bus_LV_3372-2_0_2_node_283 | 0.4 | n |  | TRUE
127 | bus_LV_3372-2_0_2_node_284 | 0.4 | n |  | TRUE
128 | bus_LV_3372-2_0_2_node_286 | 0.4 | n |  | TRUE
129 | bus_LV_3372-2_0_2_node_287 | 0.4 | n |  | TRUE
130 | bus_LV_3372-2_0_2_node_297 | 0.4 | n |  | TRUE
131 | bus_LV_3372-2_0_2_node_299 | 0.4 | n |  | TRUE
132 | bus_LV_3372-2_0_2_node_386 | 0.4 | n |  | TRUE
133 | bus_LV_3372-2_0_2_node_319 | 0.4 | n |  | TRUE
134 | bus_LV_3372-2_0_2_node_356 | 0.4 | n |  | TRUE
135 | bus_LV_3372-2_0_2_node_325 | 0.4 | n |  | TRUE
136 | bus_LV_3372-2_0_2_node_365 | 0.4 | n |  | TRUE
137 | bus_LV_3372-2_0_2_node_366 | 0.4 | n |  | TRUE
138 | bus_LV_3372-2_0_2_node_392 | 0.4 | n |  | TRUE
139 | bus_LV_3372-2_0_2_node_382 | 0.4 | n |  | TRUE
140 | bus_LV_3372-2_0_2_node_415 | 0.4 | n |  | TRUE
141 | bus_LV_3372-2_0_2_node_432 | 0.4 | n |  | TRUE
142 | bus_LV_3372-2_0_2_node_428 | 0.4 | n |  | TRUE
143 | bus_LV_3372-2_0_2_node_420 | 0.4 | n |  | TRUE
144 | bus_LV_3372-2_0_2_node_395 | 0.4 | n |  | TRUE
145 | bus_LV_3372-2_0_2_node_397 | 0.4 | n |  | TRUE
146 | bus_LV_3372-2_0_2_node_398 | 0.4 | n |  | TRUE
147 | bus_LV_3372-2_0_2_node_399 | 0.4 | n |  | TRUE
148 | bus_LV_3372-2_0_2_node_414 | 0.4 | n |  | TRUE
149 | bus_LV_3372-2_0_2_node_410 | 0.4 | n |  | TRUE
150 | bus_LV_3372-2_0_2_node_412 | 0.4 | n |  | TRUE
151 | bus_LV_3372-2_0_2_node_413 | 0.4 | n |  | TRUE
152 | bus_LV_3372-2_0_2_node_416 | 0.4 | n |  | TRUE
153 | bus_LV_3372-2_0_2_node_421 | 0.4 | n |  | TRUE
154 | bus_LV_3372-2_0_2_node_417 | 0.4 | n |  | TRUE
155 | bus_LV_3372-2_0_2_node_442 | 0.4 | n |  | TRUE
156 | bus_LV_3372-2_0_2_node_440 | 0.4 | n |  | TRUE
157 | bus_LV_3372-2_0_2_node_418 | 0.4 | n |  | TRUE
158 | bus_LV_3372-2_0_2_node_419 | 0.4 | n |  | TRUE
159 | bus_LV_3372-2_0_2_node_438 | 0.4 | n |  | TRUE
160 | bus_LV_3372-2_0_2_node_439 | 0.4 | n |  | TRUE
161 | bus_LV_3372-2_0_2_node_441 | 0.4 | n |  | TRUE
162 | bus_MV_153_1_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3372-2_0_2_load_0 | 0 | 0.00040386 | 0.00010122 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3372-2_0_2_load_1 | 1 | 0.00021662 | 5.4291e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3372-2_0_2_load_4 | 7 | 0.00043947 | 0.00011014 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3372-2_0_2_load_164 | 8 | 0.00013692 | 3.4314e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3372-2_0_2_load_64 | 9 | 0.00067979 | 0.00017037 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3372-2_0_2_load_435 | 10 | 0.00056331 | 0.00014118 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3372-2_0_2_load_22 | 11 | 0.0023134 | 0.00057978 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3372-2_0_2_load_23 | 12 | 0.0015568 | 0.00039017 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3372-2_0_2_load_25 | 14 | 0.0027277 | 0.00068363 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3372-2_0_2_load_68 | 17 | 0.0024622 | 0.00061708 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3372-2_0_2_load_433 | 19 | 0.0017766 | 0.00044526 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3372-2_0_2_load_384 | 21 | 0.0033802 | 0.00084717 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3372-2_0_2_load_383 | 24 | 0.0003982 | 9.9797e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3372-2_0_2_load_38 | 25 | 0.00029806 | 7.4701e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3372-2_0_2_load_39 | 26 | 0.00013621 | 3.4138e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3372-2_0_2_load_42 | 27 | 0.00038131 | 9.5565e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3372-2_0_2_load_40 | 28 | 0.00017841 | 4.4713e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3372-2_0_2_load_41 | 29 | 0.00051017 | 0.00012786 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3372-2_0_2_load_188 | 31 | 0.00019678 | 4.9317e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3372-2_0_2_load_49 | 32 | 0.00033617 | 8.4253e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3372-2_0_2_load_50 | 33 | 0.00021889 | 5.486e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3372-2_0_2_load_51 | 34 | 0.0011674 | 0.00029257 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3372-2_0_2_load_52 | 35 | 0.00047251 | 0.00011842 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3372-2_0_2_load_69 | 37 | 0.0016523 | 0.00041411 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3372-2_0_2_load_80 | 38 | 0.0020135 | 0.00050464 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3372-2_0_2_load_59 | 39 | 0.00027694 | 6.9409e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3372-2_0_2_load_62 | 42 | 0.00022665 | 5.6804e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3372-2_0_2_load_63 | 43 | 0.00025115 | 6.2945e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3372-2_0_2_load_65 | 44 | 0.00023947 | 6.0017e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3372-2_0_2_load_67 | 46 | 0.0022221 | 0.0005569 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3372-2_0_2_load_79 | 48 | 0.00013005 | 3.2593e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3372-2_0_2_load_326 | 49 | 0.00035594 | 8.9207e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3372-2_0_2_load_81 | 50 | 0.000355 | 8.8971e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3372-2_0_2_load_82 | 51 | 0.00053537 | 0.00013418 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3372-2_0_2_load_99 | 53 | 0.00044649 | 0.0001119 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3372-2_0_2_load_101 | 54 | 0.00080975 | 0.00020294 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3372-2_0_2_load_102 | 55 | 8.6362e-05 | 2.1644e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3372-2_0_2_load_117 | 57 | 0.0012276 | 0.00030766 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3372-2_0_2_load_118 | 58 | 0.00073829 | 0.00018503 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3372-2_0_2_load_121 | 61 | 0.00020471 | 5.1305e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3372-2_0_2_load_275 | 63 | 0.00017019 | 4.2653e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3372-2_0_2_load_122 | 64 | 0.0017209 | 0.00043131 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3372-2_0_2_load_123 | 65 | 0.0013861 | 0.0003474 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3372-2_0_2_load_124 | 66 | 0.00045841 | 0.00011489 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3372-2_0_2_load_125 | 67 | 0.0015363 | 0.00038502 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3372-2_0_2_load_126 | 68 | 0.00046646 | 0.0001169 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3372-2_0_2_load_158 | 69 | 0.0012995 | 0.00032569 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3372-2_0_2_load_307 | 70 | 0.00050866 | 0.00012748 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3372-2_0_2_load_159 | 71 | 0.0022703 | 0.00056899 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3372-2_0_2_load_160 | 72 | 0.00065601 | 0.00016441 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3372-2_0_2_load_161 | 73 | 0.0020385 | 0.00051089 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3372-2_0_2_load_162 | 74 | 0.00043224 | 0.00010833 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3372-2_0_2_load_163 | 75 | 0.00087527 | 0.00021936 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3372-2_0_2_load_364 | 77 | 0.0001403 | 3.5163e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3372-2_0_2_load_165 | 78 | 0.00040877 | 0.00010245 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3372-2_0_2_load_166 | 79 | 0.0004842 | 0.00012135 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3372-2_0_2_load_167 | 80 | 0.0018228 | 0.00045685 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3372-2_0_2_load_168 | 81 | 0.0002314 | 5.7995e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3372-2_0_2_load_329 | 82 | 0.00052282 | 0.00013103 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3372-2_0_2_load_192 | 86 | 0.00016239 | 4.07e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3372-2_0_2_load_194 | 87 | 0.00012712 | 3.1859e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3372-2_0_2_load_220 | 88 | 0.00025578 | 6.4104e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3372-2_0_2_load_198 | 89 | 0.00037 | 9.273e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3372-2_0_2_load_199 | 90 | 0.00049485 | 0.00012402 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3372-2_0_2_load_201 | 91 | 0.00051361 | 0.00012872 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3372-2_0_2_load_389 | 92 | 0.00041144 | 0.00010312 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3372-2_0_2_load_212 | 95 | 0.00012949 | 3.2453e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3372-2_0_2_load_219 | 99 | 0.00015462 | 3.8751e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3372-2_0_2_load_355 | 100 | 0.00015951 | 3.9977e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3372-2_0_2_load_354 | 101 | 0.00013269 | 3.3256e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3372-2_0_2_load_221 | 102 | 0.00027944 | 7.0035e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3372-2_0_2_load_318 | 104 | 0.00095527 | 0.00023941 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3372-2_0_2_load_270 | 105 | 0.00018936 | 4.7459e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3372-2_0_2_load_232 | 106 | 0.00021464 | 5.3793e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3372-2_0_2_load_233 | 107 | 0.00019423 | 4.8678e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3372-2_0_2_load_234 | 108 | 0.0011416 | 0.0002861 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3372-2_0_2_load_235 | 109 | 0.00061477 | 0.00015408 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3372-2_0_2_load_236 | 110 | 0.00035061 | 8.7871e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3372-2_0_2_load_260 | 111 | 0.00030955 | 7.7581e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3372-2_0_2_load_430 | 112 | 0.00022576 | 5.6582e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3372-2_0_2_load_256 | 113 | 0.00094633 | 0.00023717 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3372-2_0_2_load_262 | 116 | 0.00021815 | 5.4673e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3372-2_0_2_load_263 | 117 | 0.0002951 | 7.3958e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3372-2_0_2_load_394 | 118 | 0.00056368 | 0.00014127 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3372-2_0_2_load_427 | 119 | 0.00016726 | 4.1919e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3372-2_0_2_load_298 | 120 | 0.00042677 | 0.00010696 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3372-2_0_2_load_296 | 121 | 0.00014187 | 3.5557e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3372-2_0_2_load_272 | 122 | 0.0011042 | 0.00027673 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3372-2_0_2_load_324 | 123 | 0.0002457 | 6.1579e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3372-2_0_2_load_436 | 124 | 0.00039555 | 9.9134e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3372-2_0_2_load_274 | 125 | 0.00017447 | 4.3725e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3372-2_0_2_load_283 | 126 | 0.0004816 | 0.0001207 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3372-2_0_2_load_284 | 127 | 0.00050507 | 0.00012658 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3372-2_0_2_load_286 | 128 | 0.0002881 | 7.2204e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3372-2_0_2_load_287 | 129 | 0.001211 | 0.00030351 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3372-2_0_2_load_356 | 134 | 0.00092314 | 0.00023136 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3372-2_0_2_load_325 | 135 | 0.00050021 | 0.00012536 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3372-2_0_2_load_365 | 136 | 0.0006887 | 0.00017261 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3372-2_0_2_load_366 | 137 | 0.00045959 | 0.00011518 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3372-2_0_2_load_392 | 138 | 0.00041771 | 0.00010469 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3372-2_0_2_load_382 | 139 | 0.0007075 | 0.00017732 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3372-2_0_2_load_432 | 141 | 0.00056536 | 0.00014169 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3372-2_0_2_load_428 | 142 | 0.0002669 | 6.6892e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3372-2_0_2_load_420 | 143 | 0.00022641 | 5.6745e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3372-2_0_2_load_395 | 144 | 0.00018891 | 4.7345e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3372-2_0_2_load_397 | 145 | 0.00096076 | 0.00024079 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3372-2_0_2_load_398 | 146 | 0.0050778 | 0.0012726 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3372-2_0_2_load_399 | 147 | 0.0025809 | 0.00064683 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3372-2_0_2_load_410 | 149 | 0.00077003 | 0.00019299 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3372-2_0_2_load_421 | 153 | 0.00050797 | 0.00012731 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3372-2_0_2_load_417 | 154 | 0.0014472 | 0.00036271 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3372-2_0_2_load_442 | 155 | 0.00090648 | 0.00022718 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3372-2_0_2_load_418 | 157 | 0.0042768 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3372-2_0_2_load_419 | 158 | 0.0024318 | 0.00060947 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3372-2_0_2_load_438 | 159 | 0.0011892 | 0.00029805 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3372-2_0_2_load_441 | 161 | 0.0036827 | 0.00092296 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 155 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3372-2_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3372-2_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.10653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3372-2_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.20729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3372-2_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.12055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3372-2_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.19288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3372-2_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.13369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3372-2_0_2_line_6 | NAYY 4x150 SE | 4 | 8 | 0.0077156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3372-2_0_2_line_7 | NAYY 4x150 SE | 4 | 9 | 0.031287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3372-2_0_2_line_8 | NAYY 4x150 SE | 5 | 10 | 0.025792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3372-2_0_2_line_9 | NAYY 4x150 SE | 6 | 7 | 0.016609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3372-2_0_2_line_10 | NAYY 4x150 SE | 6 | 61 | 0.034628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3372-2_0_2_line_11 | NAYY 4x150 SE | 8 | 42 | 0.0030058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3372-2_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.0035099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3372-2_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.031435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3372-2_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.014639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3372-2_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.011087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_3372-2_0_2_line_16 | NAYY 4x150 SE | 13 | 16 | 0.011787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_3372-2_0_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.0019661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3372-2_0_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.007106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_3372-2_0_2_line_19 | NAYY 4x150 SE | 15 | 19 | 0.01983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3372-2_0_2_line_20 | NAYY 4x150 SE | 16 | 23 | 0.17381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_3372-2_0_2_line_21 | NAYY 4x150 SE | 16 | 24 | 0.016327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3372-2_0_2_line_22 | NAYY 4x150 SE | 17 | 46 | 0.0091227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3372-2_0_2_line_23 | NAYY 4x150 SE | 18 | 151 | 0.003485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_3372-2_0_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.03816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3372-2_0_2_line_25 | NAYY 4x150 SE | 20 | 22 | 0.00711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3372-2_0_2_line_26 | NAYY 4x150 SE | 21 | 139 | 0.017383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3372-2_0_2_line_27 | NAYY 4x150 SE | 22 | 69 | 0.019566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3372-2_0_2_line_28 | NAYY 4x150 SE | 22 | 114 | 0.095112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3372-2_0_2_line_29 | NAYY 4x150 SE | 23 | 124 | 0.14933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3372-2_0_2_line_30 | NAYY 4x150 SE | 23 | 97 | 0.28599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3372-2_0_2_line_31 | NAYY 4x150 SE | 24 | 139 | 0.0077183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3372-2_0_2_line_32 | NAYY 4x150 SE | 25 | 26 | 0.0076326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3372-2_0_2_line_33 | NAYY 4x150 SE | 26 | 27 | 0.009396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3372-2_0_2_line_34 | NAYY 4x150 SE | 27 | 31 | 0.011066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3372-2_0_2_line_35 | NAYY 4x150 SE | 28 | 29 | 0.0076214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3372-2_0_2_line_36 | NAYY 4x150 SE | 29 | 30 | 0.037494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3372-2_0_2_line_37 | NAYY 4x150 SE | 30 | 120 | 0.014109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3372-2_0_2_line_38 | NAYY 4x150 SE | 30 | 121 | 0.058536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3372-2_0_2_line_39 | NAYY 4x150 SE | 31 | 84 | 0.065614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3372-2_0_2_line_40 | NAYY 4x150 SE | 32 | 33 | 0.017168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3372-2_0_2_line_41 | NAYY 4x150 SE | 32 | 34 | 0.0206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3372-2_0_2_line_42 | NAYY 4x150 SE | 33 | 35 | 0.040215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3372-2_0_2_line_43 | NAYY 4x150 SE | 34 | 36 | 0.015111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3372-2_0_2_line_44 | NAYY 4x150 SE | 36 | 37 | 0.0060956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3372-2_0_2_line_45 | NAYY 4x150 SE | 36 | 38 | 0.03798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3372-2_0_2_line_46 | NAYY 4x150 SE | 37 | 46 | 0.024333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3372-2_0_2_line_47 | NAYY 4x150 SE | 38 | 50 | 0.039194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3372-2_0_2_line_48 | NAYY 4x150 SE | 39 | 40 | 0.017911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3372-2_0_2_line_49 | NAYY 4x150 SE | 39 | 41 | 0.036235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3372-2_0_2_line_50 | NAYY 4x150 SE | 40 | 42 | 0.0068328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3372-2_0_2_line_51 | NAYY 4x150 SE | 40 | 43 | 0.12101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3372-2_0_2_line_52 | NAYY 4x150 SE | 41 | 44 | 0.063061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3372-2_0_2_line_53 | NAYY 4x150 SE | 43 | 45 | 0.083645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3372-2_0_2_line_54 | NAYY 4x150 SE | 45 | 55 | 0.065626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3372-2_0_2_line_55 | NAYY 4x150 SE | 45 | 53 | 0.054434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3372-2_0_2_line_56 | NAYY 4x150 SE | 47 | 48 | 0.018617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3372-2_0_2_line_57 | NAYY 4x150 SE | 47 | 49 | 0.14898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3372-2_0_2_line_58 | NAYY 4x150 SE | 49 | 52 | 0.099977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3372-2_0_2_line_59 | NAYY 4x150 SE | 50 | 51 | 0.019203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3372-2_0_2_line_60 | NAYY 4x150 SE | 51 | 52 | 0.1979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3372-2_0_2_line_61 | NAYY 4x150 SE | 52 | 82 | 0.038537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3372-2_0_2_line_62 | NAYY 4x150 SE | 53 | 54 | 0.11797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3372-2_0_2_line_63 | NAYY 4x150 SE | 55 | 56 | 0.12922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3372-2_0_2_line_64 | NAYY 4x150 SE | 56 | 98 | 0.12754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3372-2_0_2_line_65 | NAYY 4x150 SE | 56 | 99 | 0.0098913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3372-2_0_2_line_66 | NAYY 4x150 SE | 57 | 58 | 0.0086863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3372-2_0_2_line_67 | NAYY 4x150 SE | 57 | 59 | 0.015772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3372-2_0_2_line_68 | NAYY 4x150 SE | 59 | 60 | 0.22084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3372-2_0_2_line_69 | NAYY 4x150 SE | 59 | 61 | 0.14663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3372-2_0_2_line_70 | NAYY 4x150 SE | 60 | 62 | 0.14048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3372-2_0_2_line_71 | NAYY 4x150 SE | 60 | 63 | 0.053614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3372-2_0_2_line_72 | NAYY 4x150 SE | 62 | 141 | 0.036739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3372-2_0_2_line_73 | NAYY 4x150 SE | 62 | 142 | 0.006622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3372-2_0_2_line_74 | NAYY 4x150 SE | 63 | 125 | 0.012746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3372-2_0_2_line_75 | NAYY 4x150 SE | 64 | 65 | 0.0017457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3372-2_0_2_line_76 | NAYY 4x150 SE | 64 | 66 | 0.020083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3372-2_0_2_line_77 | NAYY 4x150 SE | 65 | 67 | 0.01598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3372-2_0_2_line_78 | NAYY 4x150 SE | 66 | 68 | 0.0089076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3372-2_0_2_line_79 | NAYY 4x150 SE | 67 | 69 | 0.011804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3372-2_0_2_line_80 | NAYY 4x150 SE | 68 | 70 | 0.010468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3372-2_0_2_line_81 | NAYY 4x150 SE | 71 | 72 | 0.18844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3372-2_0_2_line_82 | NAYY 4x150 SE | 71 | 73 | 0.012524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3372-2_0_2_line_83 | NAYY 4x150 SE | 72 | 74 | 0.02361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3372-2_0_2_line_84 | NAYY 4x150 SE | 73 | 75 | 0.0024251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3372-2_0_2_line_85 | NAYY 4x150 SE | 74 | 76 | 0.095484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_3372-2_0_2_line_86 | NAYY 4x150 SE | 75 | 77 | 0.097845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3372-2_0_2_line_87 | NAYY 4x150 SE | 76 | 93 | 0.16389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3372-2_0_2_line_88 | NAYY 4x150 SE | 76 | 94 | 0.11254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3372-2_0_2_line_89 | NAYY 4x150 SE | 77 | 136 | 0.10278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3372-2_0_2_line_90 | NAYY 4x150 SE | 78 | 79 | 0.1349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3372-2_0_2_line_91 | NAYY 4x150 SE | 78 | 80 | 0.0062558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_3372-2_0_2_line_92 | NAYY 4x150 SE | 79 | 81 | 0.012259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3372-2_0_2_line_93 | NAYY 4x150 SE | 79 | 82 | 0.11314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3372-2_0_2_line_94 | NAYY 4x150 SE | 81 | 83 | 0.085909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_3372-2_0_2_line_95 | NAYY 4x150 SE | 83 | 89 | 0.054244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_3372-2_0_2_line_96 | NAYY 4x150 SE | 84 | 85 | 0.017564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3372-2_0_2_line_97 | NAYY 4x150 SE | 85 | 134 | 0.067356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3372-2_0_2_line_98 | NAYY 4x150 SE | 85 | 133 | 0.022438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3372-2_0_2_line_99 | NAYY 4x150 SE | 86 | 87 | 0.00076894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3372-2_0_2_line_100 | NAYY 4x150 SE | 87 | 88 | 0.037896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3372-2_0_2_line_101 | NAYY 4x150 SE | 88 | 102 | 0.0034789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3372-2_0_2_line_102 | NAYY 4x150 SE | 89 | 90 | 0.034639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3372-2_0_2_line_103 | NAYY 4x150 SE | 90 | 91 | 0.15422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3372-2_0_2_line_104 | NAYY 4x150 SE | 91 | 92 | 0.0074067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3372-2_0_2_line_105 | NAYY 4x150 SE | 93 | 122 | 0.10623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3372-2_0_2_line_106 | NAYY 4x150 SE | 93 | 105 | 0.14198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3372-2_0_2_line_107 | NAYY 4x150 SE | 94 | 129 | 0.010296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3372-2_0_2_line_108 | NAYY 4x150 SE | 94 | 126 | 0.011166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3372-2_0_2_line_109 | NAYY 4x150 SE | 95 | 96 | 0.06923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3372-2_0_2_line_110 | NAYY 4x150 SE | 96 | 97 | 0.2825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_3372-2_0_2_line_111 | NAYY 4x150 SE | 97 | 105 | 0.091779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3372-2_0_2_line_112 | NAYY 4x150 SE | 97 | 103 | 0.15505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_3372-2_0_2_line_113 | NAYY 4x150 SE | 98 | 100 | 0.070589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3372-2_0_2_line_114 | NAYY 4x150 SE | 98 | 101 | 0.17145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3372-2_0_2_line_115 | NAYY 4x150 SE | 102 | 103 | 0.13725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3372-2_0_2_line_116 | NAYY 4x150 SE | 103 | 104 | 0.15571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3372-2_0_2_line_117 | NAYY 4x150 SE | 104 | 133 | 0.025306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3372-2_0_2_line_118 | NAYY 4x150 SE | 106 | 107 | 0.010041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3372-2_0_2_line_119 | NAYY 4x150 SE | 106 | 108 | 0.092595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3372-2_0_2_line_120 | NAYY 4x150 SE | 107 | 109 | 0.035094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3372-2_0_2_line_121 | NAYY 4x150 SE | 108 | 110 | 0.13443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3372-2_0_2_line_122 | NAYY 4x150 SE | 109 | 111 | 0.0067935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3372-2_0_2_line_123 | NAYY 4x150 SE | 110 | 112 | 0.026596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3372-2_0_2_line_124 | NAYY 4x150 SE | 111 | 115 | 0.20442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3372-2_0_2_line_125 | NAYY 4x150 SE | 112 | 132 | 0.0072541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3372-2_0_2_line_126 | NAYY 4x150 SE | 113 | 114 | 0.084179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3372-2_0_2_line_127 | NAYY 4x150 SE | 115 | 116 | 0.11514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3372-2_0_2_line_128 | NAYY 4x150 SE | 115 | 117 | 0.079771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3372-2_0_2_line_129 | NAYY 4x150 SE | 116 | 118 | 0.015616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3372-2_0_2_line_130 | NAYY 4x150 SE | 117 | 119 | 0.032038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3372-2_0_2_line_131 | NAYY 4x150 SE | 118 | 144 | 0.0035707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3372-2_0_2_line_132 | NAYY 4x150 SE | 119 | 142 | 0.0038384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3372-2_0_2_line_133 | NAYY 4x150 SE | 121 | 130 | 0.013151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3372-2_0_2_line_134 | NAYY 4x150 SE | 122 | 123 | 0.015345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3372-2_0_2_line_135 | NAYY 4x150 SE | 123 | 135 | 0.00096851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3372-2_0_2_line_136 | NAYY 4x150 SE | 126 | 127 | 0.1007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3372-2_0_2_line_137 | NAYY 4x150 SE | 127 | 128 | 0.002242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3372-2_0_2_line_138 | NAYY 4x150 SE | 130 | 131 | 0.002694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3372-2_0_2_line_139 | NAYY 4x150 SE | 131 | 132 | 0.04481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3372-2_0_2_line_140 | NAYY 4x150 SE | 132 | 140 | 0.054831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3372-2_0_2_line_141 | NAYY 4x150 SE | 136 | 137 | 0.015104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3372-2_0_2_line_142 | NAYY 4x150 SE | 137 | 138 | 0.020324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3372-2_0_2_line_143 | NAYY 4x150 SE | 138 | 143 | 0.0043444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3372-2_0_2_line_144 | NAYY 4x150 SE | 140 | 154 | 0.013331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3372-2_0_2_line_145 | NAYY 4x150 SE | 140 | 148 | 0.049587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3372-2_0_2_line_146 | NAYY 4x150 SE | 145 | 146 | 0.0024796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3372-2_0_2_line_147 | NAYY 4x150 SE | 146 | 147 | 0.014089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3372-2_0_2_line_148 | NAYY 4x150 SE | 147 | 148 | 0.029737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3372-2_0_2_line_149 | NAYY 4x150 SE | 148 | 153 | 0.086677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
150 | LV_3372-2_0_2_line_150 | NAYY 4x150 SE | 148 | 150 | 0.0069039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
151 | LV_3372-2_0_2_line_151 | NAYY 4x150 SE | 149 | 150 | 0.022519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_3372-2_0_2_line_152 | NAYY 4x150 SE | 150 | 152 | 0.025812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
153 | LV_3372-2_0_2_line_153 | NAYY 4x150 SE | 151 | 153 | 0.020571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
154 | LV_3372-2_0_2_line_154 | NAYY 4x150 SE | 152 | 155 | 0.016118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
155 | LV_3372-2_0_2_line_155 | NAYY 4x150 SE | 152 | 156 | 0.054656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_3372-2_0_2_line_156 | NAYY 4x150 SE | 154 | 157 | 0.015299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_3372-2_0_2_line_157 | NAYY 4x150 SE | 156 | 161 | 0.020879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_3372-2_0_2_line_158 | NAYY 4x150 SE | 156 | 160 | 0.010007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_3372-2_0_2_line_159 | NAYY 4x150 SE | 157 | 158 | 0.010054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_3372-2_0_2_line_160 | NAYY 4x150 SE | 159 | 160 | 0.019172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3372-2_0_2_trafo_442 | 0.25 MVA 20/0.4 kV | 162 | 155 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2732421.7671 | 1241913.9245 | 2732422.0659 | 1241918.6489 | 2732423.9335 | 1241928.488 | 2732422.1515 | 1241933.4415
1 | 2732506.5033 | 1241858.5143 | 2732505.0726 | 1241860.9401 | 2732503.0448 | 1241865.0428 | 2732499.7772 | 1241868.1059 | 2732494.7314 | 1241870.8734 | 2732431.2747 | 1241899.471 | 2732423.005 | 1241904.7022 | 2732421.4455 | 1241908.8376 | 2732421.7671 | 1241913.9245
2 | 2732219.0789 | 1241908.0699 | 2732226.9817 | 1241910.1255 | 2732272.7957 | 1241918.0199 | 2732336.9663 | 1241928.2147 | 2732347.1301 | 1241931.978 | 2732354.4631 | 1241931.0963 | 2732370.6539 | 1241927.0872 | 2732381.4886 | 1241928.5746 | 2732404.9917 | 1241934.1037 | 2732417.9247 | 1241935.4378 | 2732422.1515 | 1241933.4415
3 | 2732506.5033 | 1241858.5143 | 2732516.5383 | 1241858.5607 | 2732523.3846 | 1241857.4681 | 2732529.4572 | 1241856.1359 | 2732539.9102 | 1241851.354 | 2732549.2018 | 1241845.4119 | 2732557.8535 | 1241837.9875 | 2732577.9161 | 1241816.428 | 2732601.8336 | 1241792.2746
4 | 2732506.5033 | 1241858.5143 | 2732516.5383 | 1241858.5607 | 2732523.3846 | 1241857.4681 | 2732529.4572 | 1241856.1359 | 2732529.8676 | 1241858.4137 | 2732533.5043 | 1241864.5558 | 2732539.993 | 1241877.0894 | 2732547.7374 | 1241897.0575 | 2732561.6521 | 1241935.0013 | 2732593.0204 | 1242013.2479
5 | 2732219.0789 | 1241908.0699 | 2732221.9134 | 1241902.7173 | 2732228.5079 | 1241888.4852 | 2732230.9779 | 1241880.8224 | 2732230.8502 | 1241867.8972 | 2732227.4175 | 1241843.4328 | 2732215.0852 | 1241795.4719 | 2732211.7603 | 1241782.4532 | 2732211.562 | 1241779.1348
6 | 2732601.8336 | 1241792.2746 | 2732607.2649 | 1241786.7944
7 | 2732601.8336 | 1241792.2746 | 2732594.5866 | 1241787.6086 | 2732589.0844 | 1241786.4291 | 2732576.185 | 1241784.9285 | 2732572.3902 | 1241783.5016
8 | 2732593.0204 | 1242013.2479 | 2732596.2371 | 1242021.5937 | 2732600.1776 | 1242029.6999 | 2732604.5237 | 1242036.2361
9 | 2732211.562 | 1241779.1348 | 2732225.2949 | 1241777.8507 | 2732228.1109 | 1241777.8074
10 | 2732211.562 | 1241779.1348 | 2732211.2348 | 1241776.1694 | 2732209.5445 | 1241765.8227 | 2732204.0893 | 1241752.0114 | 2732202.4438 | 1241745.919
11 | 2732609.3808 | 1241784.6595 | 2732607.2649 | 1241786.7944
12 | 2732787.5503 | 1240872.2401 | 2732784.4732 | 1240870.5516
13 | 2732814.4392 | 1240888.4748 | 2732800.9393 | 1240879.5873 | 2732787.5503 | 1240872.2401
14 | 2732771.461 | 1240863.8471 | 2732781.8397 | 1240869.1065 | 2732784.4732 | 1240870.5516
15 | 2732814.4392 | 1240888.4748 | 2732814.7695 | 1240893.6533 | 2732815.9563 | 1240899.4293
16 | 2732814.4392 | 1240888.4748 | 2732825.2315 | 1240893.2871
17 | 2732769.7072 | 1240862.9584 | 2732771.461 | 1240863.8471
18 | 2732818.409 | 1240906.1011 | 2732815.9563 | 1240899.4293
19 | 2732815.9563 | 1240899.4293 | 2732809.4991 | 1240902.6877 | 2732799.0475 | 1240909.7198
20 | 2732825.2315 | 1240893.2871 | 2732831.8276 | 1240896.6598 | 2732840.6185 | 1240902.684 | 2732870.1124 | 1240924.5853 | 2732915.8168 | 1240961.6519 | 2732941.0571 | 1240984.9929 | 2732959.4025 | 1241003.1084
21 | 2732825.2315 | 1240893.2871 | 2732826.5339 | 1240887.1442 | 2732824.7509 | 1240880.632 | 2732823.2283 | 1240877.7093
22 | 2732761.5697 | 1240858.8348 | 2732769.7072 | 1240862.9584
23 | 2732821.8693 | 1240905.6115 | 2732818.409 | 1240906.1011
24 | 2732785.4572 | 1240830.5094 | 2732788.2499 | 1240830.1048 | 2732790.814 | 1240831.1297 | 2732793.7878 | 1240834.1211 | 2732799.3678 | 1240843.3539 | 2732803.1188 | 1240847.7861 | 2732807.4902 | 1240851.8764 | 2732809.7721 | 1240854.3518 | 2732810.2835 | 1240856.7077
25 | 2732785.4572 | 1240830.5094 | 2732781.9191 | 1240824.336
26 | 2732819.0903 | 1240871.2415 | 2732817.4494 | 1240869.2365 | 2732813.0429 | 1240864.6895 | 2732810.6429 | 1240858.3637 | 2732810.2835 | 1240856.7077
27 | 2732781.9191 | 1240824.336 | 2732773.5536 | 1240827.3515 | 2732769.3379 | 1240827.4573 | 2732765.7582 | 1240826.5209 | 2732763.3193 | 1240825.2359
28 | 2732781.9191 | 1240824.336 | 2732780.6236 | 1240822.0606 | 2732762.4891 | 1240787.3804 | 2732757.7629 | 1240775.8202 | 2732753.1102 | 1240763.0051 | 2732749.193 | 1240750.7846 | 2732745.3212 | 1240736.8749
29 | 2733014.0498 | 1241140.5301 | 2733002.6697 | 1241096.1809 | 2732998.3134 | 1241082.3268 | 2732960.6969 | 1241013.5243 | 2732959.0951 | 1241008.3839 | 2732959.4025 | 1241003.1084
30 | 2732959.4025 | 1241003.1084 | 2732965.917 | 1241010.4496 | 2732985.401 | 1241032.4274 | 2733000.9353 | 1241048.723 | 2733014.1229 | 1241060.373 | 2733029.2999 | 1241070.3329 | 2733046.743 | 1241082.1119 | 2733052.9591 | 1241086.8998 | 2733058.7072 | 1241092.3223 | 2733106.3441 | 1241147.9832 | 2733133.2448 | 1241177.8235 | 2733161.1037 | 1241204.7274
31 | 2732819.0903 | 1240871.2415 | 2732821.2044 | 1240873.8245 | 2732823.2283 | 1240877.7093
32 | 2733060.6152 | 1241515.3336 | 2733060.6152 | 1241515.3336 | 2733056.2955 | 1241509.0411
33 | 2733060.6152 | 1241515.3336 | 2733066.1576 | 1241519.4503 | 2733068.5735 | 1241520.0615
34 | 2733079.4001 | 1241522.2329 | 2733075.3706 | 1241521.7811 | 2733068.5735 | 1241520.0615
35 | 2732904.0618 | 1241243.5944 | 2732911.027 | 1241246.6883
36 | 2732894.6799 | 1241209.5499 | 2732896.1705 | 1241217.29 | 2732895.7534 | 1241228.8129 | 2732896.8667 | 1241235.1656 | 2732900.5701 | 1241242.0434 | 2732904.0618 | 1241243.5944
37 | 2732903.3753 | 1241217.785 | 2732904.5485 | 1241215.387 | 2732894.6799 | 1241209.5499
38 | 2732894.6799 | 1241209.5499 | 2732889.8289 | 1241200.2109 | 2732871.9924 | 1241182.6964 | 2732856.63 | 1241165.5597
39 | 2733144.6954 | 1241519.1668 | 2733113.2293 | 1241522.6307 | 2733093.847 | 1241523.8527 | 2733079.4001 | 1241522.2329
40 | 2732702.7958 | 1240828.5107 | 2732687.4775 | 1240820.758
41 | 2732702.7958 | 1240828.5107 | 2732714.5516 | 1240834.4606 | 2732721.0996 | 1240837.9593
42 | 2732687.4775 | 1240820.758 | 2732679.8611 | 1240816.9032 | 2732661.7794 | 1240806.8904 | 2732653.4533 | 1240799.687
43 | 2732734.4275 | 1240845.0808 | 2732721.0996 | 1240837.9593
44 | 2732734.4275 | 1240845.0808 | 2732739.8648 | 1240847.8361
45 | 2732734.4275 | 1240845.0808 | 2732735.1809 | 1240842.1729 | 2732734.3536 | 1240838.9183 | 2732730.0837 | 1240831.9834 | 2732727.5779 | 1240825.3105 | 2732723.8499 | 1240813.7616 | 2732721.7084 | 1240810.1362
46 | 2732761.5697 | 1240858.8348 | 2732739.8648 | 1240847.8361
47 | 2732698.3639 | 1240779.0483 | 2732705.2523 | 1240784.8874 | 2732714.4699 | 1240797.8825 | 2732721.7084 | 1240810.1362
48 | 2732614.1907 | 1241779.8064 | 2732599.0627 | 1241770.2171
49 | 2732575.992 | 1241743.1545 | 2732579.9197 | 1241750.8267 | 2732586.9152 | 1241760.9918 | 2732595.2414 | 1241767.7949 | 2732599.0627 | 1241770.2171
50 | 2732614.1907 | 1241779.8064 | 2732609.3808 | 1241784.6595
51 | 2732614.1907 | 1241779.8064 | 2732647.3314 | 1241744.3383 | 2732697.0592 | 1241691.6237
52 | 2732575.992 | 1241743.1545 | 2732574.1078 | 1241739.4759 | 2732570.7815 | 1241733.9968 | 2732567.2402 | 1241731.371 | 2732563.2152 | 1241730.08 | 2732558.5732 | 1241729.9985 | 2732551.8954 | 1241732.685 | 2732543.4598 | 1241737.8789 | 2732531.5777 | 1241746.0207 | 2732524.4035 | 1241743.1374
53 | 2732754.4567 | 1241630.7789 | 2732697.0592 | 1241691.6237
54 | 2732754.4567 | 1241630.7789 | 2732799.5669 | 1241583.1156
55 | 2732754.4567 | 1241630.7789 | 2732757.0921 | 1241637.0433 | 2732758.6682 | 1241643.6732 | 2732760.3137 | 1241663.7497 | 2732759.7013 | 1241678.2709 | 2732759.0382 | 1241684.3804
56 | 2732407.3797 | 1240442.4281 | 2732404.2958 | 1240443.6715 | 2732401.3897 | 1240446.0977 | 2732399.2468 | 1240449.2415 | 2732398.2444 | 1240452.8 | 2732399.0039 | 1240456.7315
57 | 2732536.9128 | 1240516.0309 | 2732407.3797 | 1240442.4281
58 | 2732563.4085 | 1240611.7903 | 2732559.7351 | 1240601.4993 | 2732548.2163 | 1240572.2946 | 2732543.0165 | 1240556.1756 | 2732539.6382 | 1240540.4643 | 2732537.3314 | 1240525.2107 | 2732536.7078 | 1240517.2343 | 2732536.9128 | 1240516.0309
59 | 2732698.3639 | 1240779.0483 | 2732684.4068 | 1240767.2172 | 2732683.731 | 1240766.6132
60 | 2732563.4085 | 1240611.7903 | 2732575.5769 | 1240634.9376 | 2732587.7489 | 1240656.2279 | 2732600.5499 | 1240677.4656 | 2732611.2477 | 1240693.9745 | 2732625.5245 | 1240711.1083 | 2732647.7231 | 1240732.5562 | 2732663.1447 | 1240748.2144 | 2732683.731 | 1240766.6132
61 | 2732563.4085 | 1240611.7903 | 2732561.4975 | 1240615.384 | 2732560.826 | 1240622.7532 | 2732561.886 | 1240638.9576 | 2732563.6739 | 1240645.2697 | 2732565.906 | 1240648.9067
62 | 2732759.1471 | 1241798.9747 | 2732757.1944 | 1241786.8761 | 2732758.6593 | 1241768.7375 | 2732762.3664 | 1241745.7115 | 2732767.3 | 1241724.9926 | 2732768.903 | 1241716.5656 | 2732768.6061 | 1241710.9096 | 2732762.6784 | 1241696.976 | 2732759.4106 | 1241691.2535 | 2732758.8151 | 1241686.4359 | 2732759.0382 | 1241684.3804
63 | 2732873.4036 | 1241479.9312 | 2732870.7626 | 1241491.8046 | 2732867.0634 | 1241502.976 | 2732860.9035 | 1241514.9374 | 2732855.875 | 1241522.3091 | 2732849.3299 | 1241530.5364 | 2732799.5669 | 1241583.1156
64 | 2732873.4036 | 1241479.9312 | 2732877.5864 | 1241485.9968 | 2732880.0468 | 1241492.6465 | 2732883.9401 | 1241508.2584 | 2732884.1609 | 1241537.9003 | 2732882.0834 | 1241571.8834 | 2732876.3478 | 1241593.2625 | 2732871.7332 | 1241603.4347
65 | 2732873.4036 | 1241479.9312 | 2732874.1449 | 1241472.1632 | 2732874.1436 | 1241470.0752
66 | 2732128.7113 | 1241638.3371 | 2732129.4047 | 1241637.2265 | 2732135.9263 | 1241633.7786
67 | 2732150.4531 | 1241629.7664 | 2732147.5907 | 1241628.9019 | 2732143.9012 | 1241629.5203 | 2732136.9739 | 1241633.2248 | 2732135.9263 | 1241633.7786
68 | 2732339.29 | 1241515.3297 | 2732241.7537 | 1241569.87 | 2732178.5796 | 1241606.4057 | 2732161.5375 | 1241620.0714 | 2732150.4531 | 1241629.7664
69 | 2732150.4531 | 1241629.7664 | 2732154.1172 | 1241632.6616 | 2732160.4747 | 1241637.2182 | 2732166.7859 | 1241640.7951 | 2732171.3172 | 1241644.4881 | 2732175.2959 | 1241648.2022 | 2732188.1086 | 1241662.7668 | 2732197.7176 | 1241672.7784 | 2732206.3188 | 1241679.8206 | 2732210.5021 | 1241684.1953 | 2732212.3918 | 1241687.974 | 2732213.8803 | 1241693.4675 | 2732213.6969 | 1241698.9793 | 2732212.2297 | 1241704.4069 | 2732209.993 | 1241709.4059 | 2732203.7672 | 1241720.9995 | 2732202.1123 | 1241726.0226 | 2732200.944 | 1241733.6476 | 2732201.0222 | 1241740.6555 | 2732202.4438 | 1241745.919
70 | 2732470.9497 | 1241498.5965 | 2732457.845 | 1241502.8744 | 2732435.3293 | 1241513.6814 | 2732406.2631 | 1241529.6024 | 2732403.2481 | 1241530.4914 | 2732400.2848 | 1241530.4253 | 2732339.29 | 1241515.3297
71 | 2732339.29 | 1241515.3297 | 2732354.8666 | 1241555.5008 | 2732357.4022 | 1241565.7201
72 | 2732470.9497 | 1241498.5965 | 2732470.9198 | 1241504.3341 | 2732472.1741 | 1241510.145 | 2732473.9922 | 1241515.4346 | 2732478.3374 | 1241525.7628 | 2732481.3801 | 1241533.4485
73 | 2732470.9497 | 1241498.5965 | 2732472.1572 | 1241493.2966 | 2732472.5437 | 1241492.175
74 | 2732357.4022 | 1241565.7201 | 2732358.6346 | 1241570.6869 | 2732358.7298 | 1241578.3149
75 | 2732743.3782 | 1240804.1522 | 2732744.2112 | 1240805.6863
76 | 2732735.8977 | 1240785.5463 | 2732738.6926 | 1240793.7538 | 2732742.3597 | 1240802.2766 | 2732743.3782 | 1240804.1522
77 | 2732753.8895 | 1240818.2561 | 2732750.1454 | 1240814.6948 | 2732746.2537 | 1240809.4476 | 2732744.2112 | 1240805.6863
78 | 2732735.8977 | 1240785.5463 | 2732734.1287 | 1240780.3513 | 2732732.7561 | 1240777.2192
79 | 2732763.3193 | 1240825.2359 | 2732759.7399 | 1240823.3502 | 2732754.7671 | 1240819.0908 | 2732753.8895 | 1240818.2561
80 | 2732732.7561 | 1240777.2192 | 2732730.7965 | 1240772.7479 | 2732728.0698 | 1240767.8723
81 | 2733322.0172 | 1241040.0576 | 2733290.1924 | 1241027.8594 | 2733264.6954 | 1241012.6403 | 2733225.0145 | 1240990.3969 | 2733212.5403 | 1240978.6512 | 2733202.7636 | 1240959.96 | 2733195.3322 | 1240936.1948 | 2733195.7919 | 1240925.8294 | 2733197.9941 | 1240920.6037
82 | 2733333.7119 | 1241044.5401 | 2733333.7119 | 1241044.5401 | 2733322.0172 | 1241040.0576
83 | 2733212.3013 | 1240901.9499 | 2733203.6237 | 1240911.893 | 2733198.8281 | 1240918.6246 | 2733197.9941 | 1240920.6037
84 | 2733333.7119 | 1241044.5401 | 2733336.137 | 1241044.5545
85 | 2733155.1158 | 1240855.222 | 2733162.4653 | 1240863.1049 | 2733170.507 | 1240869.4686 | 2733182.7822 | 1240874.5929 | 2733202.3977 | 1240877.9025 | 2733217.8096 | 1240881.1178 | 2733221.2787 | 1240884.2762 | 2733221.6207 | 1240888.9213 | 2733219.2916 | 1240893.94 | 2733212.3013 | 1240901.9499
86 | 2733432.9426 | 1241032.8818 | 2733432.9426 | 1241032.8818 | 2733365.923 | 1241044.7305 | 2733336.137 | 1241044.5545
87 | 2733080.1533 | 1240988.0567 | 2733078.8812 | 1240983.7355 | 2733079.4239 | 1240974.7176 | 2733081.1925 | 1240956.5748 | 2733098.192 | 1240902.52 | 2733111.0755 | 1240883.2365 | 2733131.3285 | 1240869.6011 | 2733145.4909 | 1240860.0771 | 2733155.1158 | 1240855.222
88 | 2733155.1158 | 1240855.222 | 2733190.8532 | 1240830.4689 | 2733248.1433 | 1240791.5095
89 | 2733432.9426 | 1241032.8818 | 2733449.1519 | 1241024.8392 | 2733458.1206 | 1241009.8166 | 2733465.5752 | 1240983.0831 | 2733467.1076 | 1240955.6603 | 2733466.6112 | 1240943.7042
90 | 2732459.7991 | 1240688.1825 | 2732461.255 | 1240693.1473 | 2732463.4005 | 1240703.7711 | 2732463.9172 | 1240714.8477 | 2732463.2423 | 1240727.4547 | 2732457.1074 | 1240766.0736 | 2732452.7613 | 1240782.8578 | 2732441.2613 | 1240819.8456
91 | 2732439.404 | 1240825.8193 | 2732441.2613 | 1240819.8456
92 | 2732455.5126 | 1240676.7504 | 2732457.7263 | 1240681.1137 | 2732459.7991 | 1240688.1825
93 | 2732565.906 | 1240648.9067 | 2732459.7991 | 1240688.1825
94 | 2732409.2326 | 1240605.1104 | 2732413.1837 | 1240614.8292 | 2732418.5139 | 1240623.767 | 2732444.3727 | 1240654.7929 | 2732455.5126 | 1240676.7504
95 | 2732409.2326 | 1240605.1104 | 2732402.1371 | 1240610.1899 | 2732397.5783 | 1240616.8496 | 2732386.3078 | 1240652.5606
96 | 2733157.6103 | 1241531.1113 | 2733144.6954 | 1241519.1668
97 | 2733157.6103 | 1241531.1113 | 2733158.7157 | 1241541.1671 | 2733157.2842 | 1241552.0334 | 2733156.0764 | 1241559.6796 | 2733160.1035 | 1241564.919 | 2733165.662 | 1241574.0405 | 2733166.2884 | 1241585.5535 | 2733165.0088 | 1241595.1876
98 | 2733157.6103 | 1241531.1113 | 2733162.3048 | 1241519.4287 | 2733165.2238 | 1241510.0193
99 | 2733334.9898 | 1241433.8656 | 2733335.7133 | 1241433.6053
100 | 2733301.3132 | 1241445.084 | 2733305.0202 | 1241447.4026 | 2733309.1322 | 1241447.5173 | 2733313.0082 | 1241445.3469 | 2733325.076 | 1241437.4332 | 2733334.9898 | 1241433.8656
101 | 2733299.4687 | 1241442.1343 | 2733301.3132 | 1241445.084 | 2733301.3132 | 1241445.084
102 | 2732373.0775 | 1240684.0623 | 2732375.3742 | 1240682.022 | 2732378.8558 | 1240676.1724 | 2732386.3078 | 1240652.5606
103 | 2732290.6993 | 1240808.1284 | 2732294.104 | 1240792.8064 | 2732308.2125 | 1240758.5133 | 2732317.0129 | 1240737.6914 | 2732324.0564 | 1240726.7945 | 2732331.0001 | 1240717.3189 | 2732343.4724 | 1240703.4849 | 2732360.5505 | 1240691.7333 | 2732370.4041 | 1240686.4373 | 2732373.0775 | 1240684.0623
104 | 2732289.0926 | 1240815.3587 | 2732290.6993 | 1240808.1284
105 | 2733080.1533 | 1240988.0567 | 2733073.5425 | 1240979.957 | 2733067.3824 | 1240965.2505 | 2733058.6469 | 1240956.7696 | 2733007.2676 | 1240913.7474 | 2733006.8624 | 1240913.2464
106 | 2733080.1533 | 1240988.0567 | 2733093.6453 | 1241017.8295 | 2733117.1764 | 1241076.8419 | 2733122.137 | 1241089.3751 | 2733123.7243 | 1241100.2091 | 2733127.173 | 1241117.0789 | 2733128.3182 | 1241121.0271
107 | 2733248.1433 | 1240791.5095 | 2733245.8955 | 1240781.4614
108 | 2733248.1433 | 1240791.5095 | 2733257.5103 | 1240785.4322
109 | 2733367.7619 | 1241396.8679 | 2733369.6151 | 1241394.8411 | 2733409.9822 | 1241354.1571 | 2733417.8414 | 1241349.4296 | 2733417.8414 | 1241349.4296
110 | 2733161.1037 | 1241204.7274 | 2733206.1293 | 1241247.2525 | 2733237.8764 | 1241276.8018 | 2733263.3556 | 1241299.16 | 2733315.2709 | 1241341.9964 | 2733333.2128 | 1241358.7807 | 2733349.841 | 1241377.1369 | 2733367.7619 | 1241396.8679
111 | 2733161.1037 | 1241204.7274 | 2733162.3133 | 1241202.397 | 2733161.9423 | 1241192.9804 | 2733152.1551 | 1241175.7792 | 2733140.0375 | 1241153.8884 | 2733133.5415 | 1241137.6507 | 2733130.7184 | 1241129.3024 | 2733128.3182 | 1241121.0271
112 | 2733161.1037 | 1241204.7274 | 2733206.1293 | 1241247.2525 | 2733204.3097 | 1241249.8027 | 2733202.4352 | 1241253.108 | 2733201.5928 | 1241258.9609 | 2733202.2429 | 1241266.0483 | 2733208.8053 | 1241317.7073 | 2733211.5277 | 1241338.6088
113 | 2732828.3699 | 1241656.2324 | 2732832.2806 | 1241642.0298 | 2732835.0252 | 1241635.6523 | 2732841.5444 | 1241627.9026 | 2732855.6288 | 1241616.0185 | 2732871.7332 | 1241603.4347
114 | 2732871.7332 | 1241603.4347 | 2732870.8631 | 1241612.9013 | 2732870.616 | 1241623.9276 | 2732870.744 | 1241631.3814 | 2732869.0768 | 1241637.605 | 2732863.512 | 1241650.0135 | 2732862.0951 | 1241663.9717 | 2732862.0952 | 1241670.0437 | 2732866.9423 | 1241718.361 | 2732868.4792 | 1241753.059 | 2732870.076 | 1241773.0202
115 | 2733211.5277 | 1241338.6088 | 2733242.7025 | 1241370.7143 | 2733278.6479 | 1241404.2394 | 2733285.1557 | 1241413.527 | 2733291.8161 | 1241427.4664 | 2733297.5678 | 1241439.0946 | 2733299.4687 | 1241442.1343
116 | 2733211.5277 | 1241338.6088 | 2733213.0803 | 1241361.7527 | 2733213.5604 | 1241382.4704 | 2733211.8428 | 1241394.2866 | 2733208.2109 | 1241408.1506 | 2733196.3651 | 1241442.8928 | 2733185.7521 | 1241470.2341 | 2733177.2304 | 1241487.7564
117 | 2733165.2238 | 1241510.0193 | 2733173.2866 | 1241495.8656 | 2733177.2304 | 1241487.7564
118 | 2732620.3898 | 1241234.704 | 2732620.3898 | 1241234.704 | 2732630.4302 | 1241234.6019
119 | 2732722.0948 | 1241227.1706 | 2732722.0948 | 1241227.1706 | 2732717.3287 | 1241229.5772 | 2732711.5008 | 1241231.4374 | 2732704.1746 | 1241231.9741 | 2732632.6989 | 1241234.5789 | 2732630.4302 | 1241234.6019
120 | 2732586.6392 | 1241232.4457 | 2732588.5198 | 1241230.8109 | 2732593.6851 | 1241229.4918 | 2732599.2332 | 1241230.3386 | 2732611.1867 | 1241233.5974 | 2732620.3898 | 1241234.704
121 | 2732817.9306 | 1241132.9849 | 2732748.6657 | 1241201.5202 | 2732727.7736 | 1241222.8493 | 2732722.0948 | 1241227.1706
122 | 2732586.6392 | 1241232.4457 | 2732584.6784 | 1241234.1502 | 2732583.1989 | 1241238.0761
123 | 2732817.9306 | 1241132.9849 | 2732831.1933 | 1241119.862 | 2732836.973 | 1241114.4199
124 | 2732542.8567 | 1241401.0724 | 2732557.9996 | 1241391.569 | 2732576.6553 | 1241380.565 | 2732585.5803 | 1241373.8029 | 2732594.9818 | 1241364.6716 | 2732605.278 | 1241351.0453 | 2732610.9668 | 1241341.5308 | 2732614.1938 | 1241334.886 | 2732617.0226 | 1241324.7404 | 2732617.2501 | 1241316.5939 | 2732615.6658 | 1241307.6174 | 2732612.5451 | 1241298.6843 | 2732585.7592 | 1241249.0762 | 2732583.4926 | 1241242.531 | 2732583.1989 | 1241238.0761
125 | 2732843.9731 | 1241112.5749 | 2732840.8437 | 1241113.161 | 2732836.973 | 1241114.4199 | 2732836.973 | 1241114.4199
126 | 2732745.3212 | 1240736.8749 | 2732743.4588 | 1240730.183 | 2732723.8757 | 1240655.4742
127 | 2732542.8567 | 1241401.0724 | 2732536.4367 | 1241403.3755 | 2732526.3842 | 1241410.1681 | 2732509.0479 | 1241421.0238 | 2732484.0029 | 1241433.3088 | 2732457.9803 | 1241438.2323 | 2732448.1001 | 1241437.6558 | 2732438.0782 | 1241434.9521 | 2732437.0072 | 1241434.9115
128 | 2732542.8567 | 1241401.0724 | 2732538.0865 | 1241406.7153 | 2732524.9856 | 1241420.9685 | 2732491.214 | 1241461.8443
129 | 2732437.0072 | 1241434.9115 | 2732430.9443 | 1241434.6816 | 2732423.4073 | 1241437.5604 | 2732422.4119 | 1241438.656
130 | 2732491.214 | 1241461.8443 | 2732487.1585 | 1241466.7528 | 2732475.0364 | 1241484.9425 | 2732473.7944 | 1241488.5461
131 | 2732420.011 | 1241441.2989 | 2732422.4119 | 1241438.656
132 | 2732472.5437 | 1241492.175 | 2732473.7944 | 1241488.5461
133 | 2732846.586 | 1241157.339 | 2732847.6584 | 1241157.7523 | 2732849.7014 | 1241158.7322 | 2732854.5547 | 1241163.2447 | 2732856.63 | 1241165.5597
134 | 2733006.8624 | 1240913.2464 | 2732997.2118 | 1240901.3166
135 | 2732996.6027 | 1240900.5637 | 2732997.2118 | 1240901.3166
136 | 2733349.6799 | 1240753.6014 | 2733323.0655 | 1240752.6134 | 2733296.1203 | 1240760.3817 | 2733257.5103 | 1240785.4322
137 | 2733351.9204 | 1240753.6846 | 2733349.6799 | 1240753.6014
138 | 2732846.586 | 1241157.339 | 2732843.8848 | 1241157.3786
139 | 2732843.8848 | 1241157.3786 | 2732843.9525 | 1241136.4619 | 2732843.9731 | 1241112.5749
140 | 2732841.3189 | 1241057.8346 | 2732843.0214 | 1241079.7584 | 2732843.8653 | 1241099.8281 | 2732843.9731 | 1241112.5749
141 | 2733466.6112 | 1240943.7042 | 2733465.9846 | 1240928.6131
142 | 2733465.9846 | 1240928.6131 | 2733465.9499 | 1240927.7767 | 2733465.6647 | 1240908.292
143 | 2733465.6011 | 1240903.9481 | 2733465.6647 | 1240908.292
144 | 2732841.3189 | 1241057.8346 | 2732828.0425 | 1241059.0383
145 | 2732838.8115 | 1241011.3936 | 2732835.8585 | 1241011.5277 | 2732838.6061 | 1241032.3851 | 2732841.3189 | 1241057.8346
146 | 2732844.833 | 1241057.2763 | 2732844.6831 | 1241054.8012
147 | 2732843.2972 | 1241040.7877 | 2732844.3198 | 1241048.805 | 2732844.6831 | 1241054.8012
148 | 2732838.8115 | 1241011.3936 | 2732842.3638 | 1241033.4701 | 2732843.2972 | 1241040.7877
149 | 2732838.8115 | 1241011.3936 | 2732833.0494 | 1240968.761 | 2732830.6076 | 1240950.4571 | 2732828.0988 | 1240932.7856 | 2732826.7887 | 1240925.5616
150 | 2732831.9133 | 1241011.3837 | 2732835.8585 | 1241011.5277 | 2732838.8115 | 1241011.3936
151 | 2732831.9133 | 1241011.3837 | 2732831.4754 | 1241005.2686 | 2732829.0898 | 1240989.0553
152 | 2732806.7952 | 1241015.3363 | 2732808.1157 | 1241014.4651 | 2732814.1685 | 1241012.0317 | 2732821.4607 | 1241011.3387 | 2732831.9133 | 1241011.3837
153 | 2732821.8693 | 1240905.6115 | 2732825.446 | 1240918.158 | 2732826.7887 | 1240925.5616
154 | 2732806.7952 | 1241015.3363 | 2732815.2544 | 1241029.0708
155 | 2732771.1175 | 1240996.3217 | 2732790.427 | 1241025.7903 | 2732796.815 | 1241021.8965 | 2732806.7952 | 1241015.3363
156 | 2732828.0425 | 1241059.0383 | 2732819.8767 | 1241059.7787 | 2732818.0852 | 1241060.7395 | 2732816.8709 | 1241062.9475 | 2732816.6633 | 1241065.4859
157 | 2732771.1175 | 1240996.3217 | 2732792.0473 | 1240997.0015
158 | 2732765.6243 | 1240987.9471 | 2732771.1175 | 1240996.3217
159 | 2732816.8916 | 1241075.5367 | 2732816.6522 | 1241065.6227 | 2732816.6633 | 1241065.4859
160 | 2732781.2888 | 1240976.8322 | 2732765.6243 | 1240987.9471

## bus_geodata
| x | y | coords
0 | 2732421.7671 | 1241913.9245
1 | 2732422.1515 | 1241933.4415
2 | 2732506.5033 | 1241858.5143
3 | 2732219.0789 | 1241908.0699
4 | 2732601.8336 | 1241792.2746
5 | 2732593.0204 | 1242013.2479
6 | 2732211.562 | 1241779.1348
7 | 2732228.1109 | 1241777.8074
8 | 2732607.2649 | 1241786.7944
9 | 2732572.3902 | 1241783.5016
10 | 2732604.5237 | 1242036.2361
11 | 2732787.5503 | 1240872.2401
12 | 2732784.4732 | 1240870.5516
13 | 2732814.4392 | 1240888.4748
14 | 2732771.461 | 1240863.8471
15 | 2732815.9563 | 1240899.4293
16 | 2732825.2315 | 1240893.2871
17 | 2732769.7072 | 1240862.9584
18 | 2732818.409 | 1240906.1011
19 | 2732799.0475 | 1240909.7198
20 | 2732785.4572 | 1240830.5094
21 | 2732810.2835 | 1240856.7077
22 | 2732781.9191 | 1240824.336
23 | 2732959.4025 | 1241003.1084
24 | 2732823.2283 | 1240877.7093
25 | 2733056.2955 | 1241509.0411
26 | 2733060.6152 | 1241515.3336
27 | 2733068.5735 | 1241520.0615
28 | 2732911.027 | 1241246.6883
29 | 2732904.0618 | 1241243.5944
30 | 2732894.6799 | 1241209.5499
31 | 2733079.4001 | 1241522.2329
32 | 2732702.7958 | 1240828.5107
33 | 2732687.4775 | 1240820.758
34 | 2732721.0996 | 1240837.9593
35 | 2732653.4533 | 1240799.687
36 | 2732734.4275 | 1240845.0808
37 | 2732739.8648 | 1240847.8361
38 | 2732721.7084 | 1240810.1362
39 | 2732599.0627 | 1241770.2171
40 | 2732614.1907 | 1241779.8064
41 | 2732575.992 | 1241743.1545
42 | 2732609.3808 | 1241784.6595
43 | 2732697.0592 | 1241691.6237
44 | 2732524.4035 | 1241743.1374
45 | 2732754.4567 | 1241630.7789
46 | 2732761.5697 | 1240858.8348
47 | 2732407.3797 | 1240442.4281
48 | 2732399.0039 | 1240456.7315
49 | 2732536.9128 | 1240516.0309
50 | 2732698.3639 | 1240779.0483
51 | 2732683.731 | 1240766.6132
52 | 2732563.4085 | 1240611.7903
53 | 2732759.0382 | 1241684.3804
54 | 2732759.1471 | 1241798.9747
55 | 2732799.567 | 1241583.1156
56 | 2732873.4036 | 1241479.9312
57 | 2732135.9264 | 1241633.7786
58 | 2732128.7113 | 1241638.3371
59 | 2732150.4531 | 1241629.7664
60 | 2732339.29 | 1241515.3297
61 | 2732202.4438 | 1241745.919
62 | 2732470.9497 | 1241498.5965
63 | 2732357.4022 | 1241565.7201
64 | 2732743.3782 | 1240804.1522
65 | 2732744.2112 | 1240805.6863
66 | 2732735.8977 | 1240785.5463
67 | 2732753.8895 | 1240818.2561
68 | 2732732.7561 | 1240777.2192
69 | 2732763.3193 | 1240825.2359
70 | 2732728.0698 | 1240767.8723
71 | 2733322.0172 | 1241040.0576
72 | 2733197.9941 | 1240920.6037
73 | 2733333.7119 | 1241044.5401
74 | 2733212.3013 | 1240901.9499
75 | 2733336.137 | 1241044.5545
76 | 2733155.1158 | 1240855.222
77 | 2733432.9426 | 1241032.8818
78 | 2732441.2613 | 1240819.8456
79 | 2732459.7991 | 1240688.1825
80 | 2732439.404 | 1240825.8193
81 | 2732455.5126 | 1240676.7504
82 | 2732565.906 | 1240648.9067
83 | 2732409.2326 | 1240605.1104
84 | 2733144.6954 | 1241519.1668
85 | 2733157.6103 | 1241531.1113
86 | 2733335.7133 | 1241433.6053
87 | 2733334.9898 | 1241433.8656
88 | 2733301.3132 | 1241445.084
89 | 2732386.3078 | 1240652.5606
90 | 2732373.0775 | 1240684.0623
91 | 2732290.6993 | 1240808.1284
92 | 2732289.0926 | 1240815.3587
93 | 2733080.1533 | 1240988.0567
94 | 2733248.1433 | 1240791.5095
95 | 2733417.8414 | 1241349.4296
96 | 2733367.7619 | 1241396.8679
97 | 2733161.1037 | 1241204.7274
98 | 2732871.7332 | 1241603.4347
99 | 2732874.1435 | 1241470.0752
100 | 2732828.3699 | 1241656.2324
101 | 2732870.076 | 1241773.0202
102 | 2733299.4686 | 1241442.1343
103 | 2733211.5277 | 1241338.6088
104 | 2733177.2304 | 1241487.7564
105 | 2733128.3182 | 1241121.0271
106 | 2732630.4302 | 1241234.6019
107 | 2732620.3898 | 1241234.704
108 | 2732722.0948 | 1241227.1706
109 | 2732586.6392 | 1241232.4457
110 | 2732817.9306 | 1241132.9849
111 | 2732583.1989 | 1241238.0761
112 | 2732836.973 | 1241114.4199
113 | 2732723.8757 | 1240655.4742
114 | 2732745.3212 | 1240736.8749
115 | 2732542.8567 | 1241401.0724
116 | 2732437.0072 | 1241434.9115
117 | 2732491.214 | 1241461.8443
118 | 2732422.4119 | 1241438.656
119 | 2732473.7944 | 1241488.5461
120 | 2732903.3753 | 1241217.785
121 | 2732856.63 | 1241165.5597
122 | 2733006.8624 | 1240913.2464
123 | 2732997.2118 | 1240901.3166
124 | 2733014.0498 | 1241140.5301
125 | 2732358.7298 | 1241578.3149
126 | 2733257.5103 | 1240785.4322
127 | 2733349.6799 | 1240753.6014
128 | 2733351.9204 | 1240753.6846
129 | 2733245.8955 | 1240781.4614
130 | 2732846.586 | 1241157.339
131 | 2732843.8848 | 1241157.3786
132 | 2732843.9731 | 1241112.5749
133 | 2733165.2238 | 1241510.0193
134 | 2733165.0088 | 1241595.1876
135 | 2732996.6027 | 1240900.5637
136 | 2733466.6112 | 1240943.7042
137 | 2733465.9846 | 1240928.6131
138 | 2733465.6647 | 1240908.292
139 | 2732819.0903 | 1240871.2415
140 | 2732841.3189 | 1241057.8346
141 | 2732481.3801 | 1241533.4485
142 | 2732472.5437 | 1241492.175
143 | 2733465.6011 | 1240903.9481
144 | 2732420.011 | 1241441.2989
145 | 2732844.833 | 1241057.2763
146 | 2732844.6831 | 1241054.8012
147 | 2732843.2972 | 1241040.7877
148 | 2732838.8115 | 1241011.3936
149 | 2732829.0898 | 1240989.0553
150 | 2732831.9133 | 1241011.3837
151 | 2732821.8693 | 1240905.6115
152 | 2732806.7952 | 1241015.3363
153 | 2732826.7887 | 1240925.5616
154 | 2732828.0425 | 1241059.0383
155 | 2732815.2544 | 1241029.0708
156 | 2732771.1175 | 1240996.3216
157 | 2732816.6633 | 1241065.4859
158 | 2732816.8916 | 1241075.5367
159 | 2732781.2888 | 1240976.8322
160 | 2732765.6243 | 1240987.9471
161 | 2732792.0473 | 1240997.0015
162 | 2732806.7952 | 1241015.3363

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1