## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3375-2_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3375-2_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3375-2_0_2_node_114 | 0.4 | n |  | TRUE
3 | bus_LV_3375-2_0_2_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_3375-2_0_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_3375-2_0_2_node_94 | 0.4 | n |  | TRUE
6 | bus_LV_3375-2_0_2_node_61 | 0.4 | n |  | TRUE
7 | bus_LV_3375-2_0_2_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_3375-2_0_2_node_63 | 0.4 | n |  | TRUE
9 | bus_LV_3375-2_0_2_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_3375-2_0_2_node_65 | 0.4 | n |  | TRUE
11 | bus_LV_3375-2_0_2_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_3375-2_0_2_node_67 | 0.4 | n |  | TRUE
13 | bus_LV_3375-2_0_2_node_68 | 0.4 | n |  | TRUE
14 | bus_LV_3375-2_0_2_node_69 | 0.4 | n |  | TRUE
15 | bus_LV_3375-2_0_2_node_70 | 0.4 | n |  | TRUE
16 | bus_LV_3375-2_0_2_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_3375-2_0_2_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_3375-2_0_2_node_91 | 0.4 | n |  | TRUE
19 | bus_LV_3375-2_0_2_node_95 | 0.4 | n |  | TRUE
20 | bus_LV_3375-2_0_2_node_92 | 0.4 | n |  | TRUE
21 | bus_LV_3375-2_0_2_node_83 | 0.4 | n |  | TRUE
22 | bus_LV_3375-2_0_2_node_85 | 0.4 | n |  | TRUE
23 | bus_LV_3375-2_0_2_node_89 | 0.4 | n |  | TRUE
24 | bus_LV_3375-2_0_2_node_87 | 0.4 | n |  | TRUE
25 | bus_LV_3375-2_0_2_node_88 | 0.4 | n |  | TRUE
26 | bus_LV_3375-2_0_2_node_93 | 0.4 | n |  | TRUE
27 | bus_LV_3375-2_0_2_node_102 | 0.4 | n |  | TRUE
28 | bus_LV_3375-2_0_2_node_96 | 0.4 | n |  | TRUE
29 | bus_LV_3375-2_0_2_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_3375-2_0_2_node_98 | 0.4 | n |  | TRUE
31 | bus_LV_3375-2_0_2_node_99 | 0.4 | n |  | TRUE
32 | bus_LV_3375-2_0_2_node_100 | 0.4 | n |  | TRUE
33 | bus_LV_3375-2_0_2_node_101 | 0.4 | n |  | TRUE
34 | bus_LV_3375-2_0_2_node_118 | 0.4 | n |  | TRUE
35 | bus_LV_3375-2_0_2_node_106 | 0.4 | n |  | TRUE
36 | bus_LV_3375-2_0_2_node_103 | 0.4 | n |  | TRUE
37 | bus_LV_3375-2_0_2_node_104 | 0.4 | n |  | TRUE
38 | bus_LV_3375-2_0_2_node_105 | 0.4 | n |  | TRUE
39 | bus_LV_3375-2_0_2_node_107 | 0.4 | n |  | TRUE
40 | bus_LV_3375-2_0_2_node_108 | 0.4 | n |  | TRUE
41 | bus_LV_3375-2_0_2_node_117 | 0.4 | n |  | TRUE
42 | bus_LV_3375-2_0_2_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_3375-2_0_2_node_110 | 0.4 | n |  | TRUE
44 | bus_LV_3375-2_0_2_node_111 | 0.4 | n |  | TRUE
45 | bus_LV_3375-2_0_2_node_112 | 0.4 | n |  | TRUE
46 | bus_LV_3375-2_0_2_node_116 | 0.4 | n |  | TRUE
47 | bus_LV_3375-2_0_2_node_113 | 0.4 | n |  | TRUE
48 | bus_LV_3375-2_0_2_node_115 | 0.4 | n |  | TRUE
49 | bus_LV_3375-2_0_2_node_119 | 0.4 | n |  | TRUE
50 | bus_LV_3375-2_0_2_node_124 | 0.4 | n |  | TRUE
51 | bus_LV_3375-2_0_2_node_121 | 0.4 | n |  | TRUE
52 | bus_LV_3375-2_0_2_node_122 | 0.4 | n |  | TRUE
53 | bus_LV_3375-2_0_2_node_123 | 0.4 | n |  | TRUE
54 | bus_LV_3375-2_0_2_node_125 | 0.4 | n |  | TRUE
55 | bus_LV_3375-2_0_2_node_126 | 0.4 | n |  | TRUE
56 | bus_LV_3375-2_0_2_node_127 | 0.4 | n |  | TRUE
57 | bus_MV_154_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3375-2_0_2_load_0 | 0 | 0.00036987 | 9.2698e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3375-2_0_2_load_114 | 2 | 0.00093361 | 0.00023398 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3375-2_0_2_load_2 | 3 | 0.0014094 | 0.00035323 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3375-2_0_2_load_94 | 5 | 0.00074053 | 0.00018559 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3375-2_0_2_load_61 | 6 | 0.0011389 | 0.00028543 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3375-2_0_2_load_62 | 7 | 0.0013084 | 0.00032792 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3375-2_0_2_load_63 | 8 | 0.0013316 | 0.00033374 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3375-2_0_2_load_64 | 9 | 0.0012037 | 0.00030167 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3375-2_0_2_load_65 | 10 | 0.0011816 | 0.00029613 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3375-2_0_2_load_66 | 11 | 0.00037684 | 9.4444e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3375-2_0_2_load_67 | 12 | 0.00047976 | 0.00012024 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3375-2_0_2_load_69 | 14 | 0.0027289 | 0.00068394 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3375-2_0_2_load_70 | 15 | 0.00052811 | 0.00013236 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3375-2_0_2_load_90 | 17 | 0.0037501 | 0.00093986 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3375-2_0_2_load_91 | 18 | 0.0028798 | 0.00072174 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3375-2_0_2_load_95 | 19 | 0.0040342 | 0.0010111 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3375-2_0_2_load_92 | 20 | 0.0010009 | 0.00025086 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3375-2_0_2_load_83 | 21 | 0.0037652 | 0.00094364 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3375-2_0_2_load_85 | 22 | 0.0027192 | 0.00068151 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3375-2_0_2_load_89 | 23 | 0.0028384 | 0.00071138 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3375-2_0_2_load_87 | 24 | 0.0020224 | 0.00050687 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3375-2_0_2_load_88 | 25 | 0.0018122 | 0.00045418 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3375-2_0_2_load_93 | 26 | 0.00093684 | 0.0002348 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3375-2_0_2_load_102 | 27 | 0.0030417 | 0.00076231 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3375-2_0_2_load_96 | 28 | 0.0030541 | 0.00076543 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3375-2_0_2_load_97 | 29 | 0.0023904 | 0.00059909 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3375-2_0_2_load_98 | 30 | 0.0015401 | 0.00038599 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3375-2_0_2_load_100 | 32 | 0.0017291 | 0.00043335 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3375-2_0_2_load_101 | 33 | 0.003874 | 0.0009709 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3375-2_0_2_load_103 | 36 | 0.0014377 | 0.00036032 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3375-2_0_2_load_104 | 37 | 0.002407 | 0.00060325 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3375-2_0_2_load_105 | 38 | 0.001682 | 0.00042154 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3375-2_0_2_load_107 | 39 | 0.0011847 | 0.00029691 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3375-2_0_2_load_108 | 40 | 0.00069134 | 0.00017327 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3375-2_0_2_load_117 | 41 | 0.00093757 | 0.00023498 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3375-2_0_2_load_109 | 42 | 0.00066681 | 0.00016712 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3375-2_0_2_load_111 | 44 | 0.0010435 | 0.00026153 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3375-2_0_2_load_112 | 45 | 0.00086147 | 0.0002159 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3375-2_0_2_load_116 | 46 | 0.00076137 | 0.00019082 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3375-2_0_2_load_113 | 47 | 0.00079306 | 0.00019876 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3375-2_0_2_load_115 | 48 | 0.0018216 | 0.00045654 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3375-2_0_2_load_119 | 49 | 0.0016816 | 0.00042146 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3375-2_0_2_load_124 | 50 | 0.0013964 | 0.00034998 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3375-2_0_2_load_121 | 51 | 0.00085042 | 0.00021314 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3375-2_0_2_load_122 | 52 | 0.003116 | 0.00078094 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3375-2_0_2_load_125 | 54 | 0.00087121 | 0.00021835 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3375-2_0_2_load_126 | 55 | 0.00082261 | 0.00020616 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3375-2_0_2_load_127 | 56 | 0.0046919 | 0.0011759 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3375-2_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.011517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3375-2_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.13522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3375-2_0_2_line_2 | NAYY 4x150 SE | 2 | 46 | 0.02279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3375-2_0_2_line_3 | NAYY 4x150 SE | 2 | 47 | 0.012739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3375-2_0_2_line_4 | NAYY 4x150 SE | 3 | 4 | 0.03517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3375-2_0_2_line_5 | NAYY 4x150 SE | 4 | 5 | 0.30229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3375-2_0_2_line_6 | NAYY 4x150 SE | 5 | 26 | 0.034682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3375-2_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.018647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3375-2_0_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.0219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3375-2_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.022225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3375-2_0_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.020876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3375-2_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.02284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3375-2_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.022709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3375-2_0_2_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3375-2_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.062489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3375-2_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0077297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3375-2_0_2_line_16 | NAYY 4x150 SE | 13 | 16 | 0.02675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3375-2_0_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.056885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3375-2_0_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.047323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3375-2_0_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.020969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3375-2_0_2_line_20 | NAYY 4x150 SE | 16 | 20 | 0.019303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3375-2_0_2_line_21 | NAYY 4x150 SE | 17 | 23 | 0.034908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3375-2_0_2_line_22 | NAYY 4x150 SE | 18 | 25 | 0.039704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3375-2_0_2_line_23 | NAYY 4x150 SE | 19 | 27 | 0.028035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3375-2_0_2_line_24 | NAYY 4x150 SE | 20 | 26 | 0.0036846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3375-2_0_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.02678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3375-2_0_2_line_26 | NAYY 4x150 SE | 22 | 23 | 0.023101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3375-2_0_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.025057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3375-2_0_2_line_28 | NAYY 4x150 SE | 27 | 31 | 0.014666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3375-2_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.023022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3375-2_0_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.026421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3375-2_0_2_line_31 | NAYY 4x150 SE | 29 | 31 | 0.015618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3375-2_0_2_line_32 | NAYY 4x150 SE | 30 | 32 | 0.025077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3375-2_0_2_line_33 | NAYY 4x150 SE | 31 | 33 | 0.042539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3375-2_0_2_line_34 | NAYY 4x150 SE | 32 | 34 | 0.042338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3375-2_0_2_line_35 | NAYY 4x150 SE | 33 | 35 | 0.0062673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3375-2_0_2_line_36 | NAYY 4x150 SE | 34 | 49 | 0.014544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3375-2_0_2_line_37 | NAYY 4x150 SE | 35 | 40 | 0.020095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3375-2_0_2_line_38 | NAYY 4x150 SE | 35 | 37 | 0.020222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3375-2_0_2_line_39 | NAYY 4x150 SE | 36 | 37 | 0.025641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3375-2_0_2_line_40 | NAYY 4x150 SE | 36 | 38 | 0.025334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3375-2_0_2_line_41 | NAYY 4x150 SE | 38 | 39 | 0.013171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3375-2_0_2_line_42 | NAYY 4x150 SE | 39 | 41 | 0.010036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3375-2_0_2_line_43 | NAYY 4x150 SE | 40 | 42 | 0.0015459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3375-2_0_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.017505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3375-2_0_2_line_45 | NAYY 4x150 SE | 43 | 44 | 0.0086268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3375-2_0_2_line_46 | NAYY 4x150 SE | 43 | 45 | 0.01919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3375-2_0_2_line_47 | NAYY 4x150 SE | 44 | 46 | 0.025452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3375-2_0_2_line_48 | NAYY 4x150 SE | 47 | 48 | 0.0035156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3375-2_0_2_line_49 | NAYY 4x150 SE | 49 | 50 | 0.00070712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3375-2_0_2_line_50 | NAYY 4x150 SE | 50 | 53 | 0.014125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3375-2_0_2_line_51 | NAYY 4x150 SE | 51 | 52 | 0.017375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3375-2_0_2_line_52 | NAYY 4x150 SE | 51 | 53 | 0.014048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3375-2_0_2_line_53 | NAYY 4x150 SE | 53 | 54 | 0.008191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3375-2_0_2_line_54 | NAYY 4x150 SE | 54 | 55 | 0.0023242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3375-2_0_2_line_55 | NAYY 4x150 SE | 55 | 56 | 0.032403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3375-2_0_2_trafo_96 | 0.25 MVA 20/0.4 kV | 57 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2725839.0972 | 1246222.5852 | 2725850.6099 | 1246222.9045
1 | 2725826.9952 | 1246357.2663 | 2725839.0972 | 1246222.5852
2 | 2725826.9952 | 1246357.2663 | 2725826.9952 | 1246357.2663 | 2725837.1322 | 1246357.1145 | 2725848.9439 | 1246361.013 | 2725849.1398 | 1246361.0966
3 | 2725816.4959 | 1246364.1286 | 2725819.5047 | 1246360.8994 | 2725826.9952 | 1246357.2663
4 | 2725444.6047 | 1246444.9634 | 2725439.29 | 1246438.6456 | 2725430.9964 | 1246431.6864 | 2725424.3321 | 1246420.2246 | 2725423.6229 | 1246417.4856
5 | 2725742.7565 | 1246395.1122 | 2725444.6047 | 1246444.9634
6 | 2725742.7565 | 1246395.1122 | 2725748.5518 | 1246401.207 | 2725768.3035 | 1246418.5297
7 | 2725892.1184 | 1246547.4428 | 2725881.4425 | 1246539.7562 | 2725877.1794 | 1246536.2935
8 | 2725877.1794 | 1246536.2935 | 2725860.1803 | 1246522.486
9 | 2725860.1803 | 1246522.486 | 2725852.0033 | 1246515.8442 | 2725843.0017 | 1246508.385
10 | 2725843.0017 | 1246508.385 | 2725826.9276 | 1246495.0652
11 | 2725826.9276 | 1246495.0652 | 2725824.4157 | 1246492.9837 | 2725809.3098 | 1246480.5293
12 | 2725809.3098 | 1246480.5293 | 2725791.7883 | 1246466.0833
13 | 2725785.1075 | 1246456.2294 | 2725783.0339 | 1246458.8655 | 2725791.7883 | 1246466.0833
14 | 2725785.1075 | 1246456.2294 | 2725787.1509 | 1246453.5927 | 2725783.8798 | 1246449.9869 | 2725782.8995 | 1246445.9738 | 2725783.3909 | 1246442.0475 | 2725785.3337 | 1246438.8081 | 2725788.4216 | 1246436.8052 | 2725792.0375 | 1246435.9145 | 2725796.2212 | 1246436.7595 | 2725808.4367 | 1246441.5672 | 2725824.5144 | 1246448.7745
15 | 2725785.1075 | 1246456.2294 | 2725790.9547 | 1246461.285
16 | 2725785.1075 | 1246456.2294 | 2725782.8941 | 1246454.4142 | 2725780.6644 | 1246451.2309 | 2725779.3636 | 1246447.3666 | 2725779.5979 | 1246441.6667 | 2725781.0153 | 1246437.9046 | 2725785.586 | 1246433.6869
17 | 2725876.3626 | 1246472.1745 | 2725865.8056 | 1246467.2843 | 2725824.5144 | 1246448.7745
18 | 2725827.3388 | 1246491.5383 | 2725825.8848 | 1246490.3459 | 2725801.6553 | 1246470.5371 | 2725790.9547 | 1246461.285
19 | 2725785.586 | 1246433.6869 | 2725789.6285 | 1246432.2825 | 2725795.8279 | 1246433.2148 | 2725805.4606 | 1246437.1904
20 | 2725785.586 | 1246433.6869 | 2725771.0737 | 1246420.9592
21 | 2725908.0371 | 1246486.8466 | 2725876.3626 | 1246472.1745
22 | 2725858.0401 | 1246516.7152 | 2725827.3388 | 1246491.5383
23 | 2725831.108 | 1246448.5107 | 2725807.8437 | 1246438.1739 | 2725805.4606 | 1246437.1904
24 | 2725771.0737 | 1246420.9592 | 2725768.3035 | 1246418.5297
25 | 2725954.1245 | 1246505.6435 | 2725947.3186 | 1246503.9796 | 2725939.1231 | 1246500.9697 | 2725929.0535 | 1246496.4367
26 | 2725929.0535 | 1246496.4367 | 2725917.9403 | 1246491.4339 | 2725908.0371 | 1246486.8466
27 | 2725877.4151 | 1246532.6038 | 2725858.0401 | 1246516.7152
28 | 2725844.5108 | 1246454.4658 | 2725831.108 | 1246448.5107
29 | 2725879.6262 | 1246470.5896 | 2725858.7043 | 1246460.983
30 | 2725879.6262 | 1246470.5896 | 2725903.6366 | 1246481.6144
31 | 2725844.5108 | 1246454.4658 | 2725858.7043 | 1246460.983
32 | 2725903.6366 | 1246481.6144 | 2725926.4263 | 1246492.0786
33 | 2725844.5108 | 1246454.4658 | 2725861.316 | 1246415.7336 | 2725861.5186 | 1246415.4878
34 | 2725966.5103 | 1246505.1549 | 2725950.9818 | 1246501.9334 | 2725935.6253 | 1246496.3025 | 2725926.4263 | 1246492.0786
35 | 2725865.5047 | 1246410.6515 | 2725861.5186 | 1246415.4878
36 | 2725966.5103 | 1246505.1549 | 2725970.2548 | 1246491.1011
37 | 2725865.5047 | 1246410.6515 | 2725873.192 | 1246392.0847
38 | 2725865.5047 | 1246410.6515 | 2725871.0295 | 1246406.3428 | 2725877.4438 | 1246406.4123 | 2725883.6595 | 1246409.1735
39 | 2725907.2272 | 1246419.1897 | 2725904.9181 | 1246418.6171 | 2725883.6595 | 1246409.1735
40 | 2725907.2272 | 1246419.1897 | 2725915.6601 | 1246421.2808 | 2725924.039 | 1246418.8677 | 2725929.5481 | 1246413.1687
41 | 2725929.7993 | 1246400.3687 | 2725931.2147 | 1246405.5086 | 2725929.5481 | 1246413.1687 | 2725929.5481 | 1246413.1687
42 | 2725922.5139 | 1246393.9571 | 2725925.4056 | 1246395.4544 | 2725929.4188 | 1246398.9871 | 2725929.7993 | 1246400.3687
43 | 2725873.7834 | 1246390.6563 | 2725873.192 | 1246392.0847
44 | 2725880.4798 | 1246374.4827 | 2725873.7834 | 1246390.6563
45 | 2725880.4798 | 1246374.4827 | 2725872.5464 | 1246371.0941
46 | 2725880.4798 | 1246374.4827 | 2725897.92 | 1246382.4897
47 | 2725849.1398 | 1246361.0966 | 2725872.5464 | 1246371.0941
48 | 2725814.0993 | 1246366.7008 | 2725816.4959 | 1246364.1286
49 | 2725970.4369 | 1246490.4178 | 2725970.2548 | 1246491.1011
50 | 2725974.0735 | 1246476.7689 | 2725970.4369 | 1246490.4178
51 | 2725944.1486 | 1246467.1807 | 2725960.6952 | 1246472.4824
52 | 2725974.0735 | 1246476.7689 | 2725960.6952 | 1246472.4824
53 | 2725974.0735 | 1246476.7689 | 2725976.146 | 1246468.8444
54 | 2725976.734 | 1246466.5958 | 2725976.146 | 1246468.8444
55 | 2725996.6064 | 1246445.9099 | 2725985.5494 | 1246448.1103 | 2725981.6804 | 1246451.3086 | 2725979.2391 | 1246457.0172 | 2725976.734 | 1246466.5958

## bus_geodata
| x | y | coords
0 | 2725850.6099 | 1246222.9045
1 | 2725839.0972 | 1246222.5852
2 | 2725826.9952 | 1246357.2663
3 | 2725423.6229 | 1246417.4856
4 | 2725444.6047 | 1246444.9634
5 | 2725742.7565 | 1246395.1122
6 | 2725892.1184 | 1246547.4428
7 | 2725877.1794 | 1246536.2935
8 | 2725860.1803 | 1246522.486
9 | 2725843.0017 | 1246508.385
10 | 2725826.9276 | 1246495.0652
11 | 2725809.3098 | 1246480.5293
12 | 2725791.7883 | 1246466.0833
13 | 2725785.1075 | 1246456.2294
14 | 2725824.5144 | 1246448.7745
15 | 2725790.9547 | 1246461.285
16 | 2725785.586 | 1246433.6869
17 | 2725876.3626 | 1246472.1745
18 | 2725827.3388 | 1246491.5383
19 | 2725805.4606 | 1246437.1904
20 | 2725771.0737 | 1246420.9592
21 | 2725954.1245 | 1246505.6435
22 | 2725929.0535 | 1246496.4367
23 | 2725908.0371 | 1246486.8466
24 | 2725877.4151 | 1246532.6038
25 | 2725858.0401 | 1246516.7152
26 | 2725768.3035 | 1246418.5297
27 | 2725831.108 | 1246448.5107
28 | 2725879.6262 | 1246470.5896
29 | 2725858.7043 | 1246460.983
30 | 2725903.6366 | 1246481.6144
31 | 2725844.5108 | 1246454.4658
32 | 2725926.4263 | 1246492.0786
33 | 2725861.5186 | 1246415.4878
34 | 2725966.5103 | 1246505.1549
35 | 2725865.5047 | 1246410.6515
36 | 2725907.2272 | 1246419.1897
37 | 2725883.6595 | 1246409.1735
38 | 2725929.5481 | 1246413.1687
39 | 2725929.7993 | 1246400.3687
40 | 2725873.192 | 1246392.0847
41 | 2725922.5139 | 1246393.9571
42 | 2725873.7834 | 1246390.6563
43 | 2725880.4798 | 1246374.4827
44 | 2725872.5464 | 1246371.0941
45 | 2725897.92 | 1246382.4897
46 | 2725849.1398 | 1246361.0966
47 | 2725816.4959 | 1246364.1286
48 | 2725814.0993 | 1246366.7008
49 | 2725970.2548 | 1246491.1011
50 | 2725970.4369 | 1246490.4178
51 | 2725960.6952 | 1246472.4824
52 | 2725944.1486 | 1246467.1807
53 | 2725974.0735 | 1246476.7689
54 | 2725976.146 | 1246468.8444
55 | 2725976.734 | 1246466.5958
56 | 2725996.6064 | 1246445.9099
57 | 2725844.5108 | 1246454.4658

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1