## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3394-1_2_3_node_9 | 0.4 | n |  | TRUE
1 | bus_LV_3394-1_2_3_node_10 | 0.4 | n |  | TRUE
2 | bus_LV_3394-1_2_3_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_3394-1_2_3_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_3394-1_2_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_3394-1_2_3_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_3394-1_2_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_3394-1_2_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_3394-1_2_3_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_3394-1_2_3_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_3394-1_2_3_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_3394-1_2_3_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_3394-1_2_3_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_3394-1_2_3_node_187 | 0.4 | n |  | TRUE
14 | bus_LV_3394-1_2_3_node_188 | 0.4 | n |  | TRUE
15 | bus_LV_3394-1_2_3_node_186 | 0.4 | n |  | TRUE
16 | bus_LV_3394-1_2_3_node_189 | 0.4 | n |  | TRUE
17 | bus_LV_3394-1_2_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_3394-1_2_3_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_3394-1_2_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_3394-1_2_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_3394-1_2_3_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_3394-1_2_3_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_3394-1_2_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_3394-1_2_3_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_3394-1_2_3_node_111 | 0.4 | n |  | TRUE
26 | bus_LV_3394-1_2_3_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_3394-1_2_3_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_3394-1_2_3_node_112 | 0.4 | n |  | TRUE
29 | bus_LV_3394-1_2_3_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_3394-1_2_3_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_3394-1_2_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_3394-1_2_3_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_3394-1_2_3_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_3394-1_2_3_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_3394-1_2_3_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_3394-1_2_3_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_3394-1_2_3_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_3394-1_2_3_node_48 | 0.4 | n |  | TRUE
39 | bus_LV_3394-1_2_3_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_3394-1_2_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_3394-1_2_3_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_3394-1_2_3_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_3394-1_2_3_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_3394-1_2_3_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_3394-1_2_3_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_3394-1_2_3_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_3394-1_2_3_node_276 | 0.4 | n |  | TRUE
48 | bus_LV_3394-1_2_3_node_284 | 0.4 | n |  | TRUE
49 | bus_LV_3394-1_2_3_node_274 | 0.4 | n |  | TRUE
50 | bus_LV_3394-1_2_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_3394-1_2_3_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_3394-1_2_3_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_3394-1_2_3_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_3394-1_2_3_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_3394-1_2_3_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_3394-1_2_3_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_3394-1_2_3_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_3394-1_2_3_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_3394-1_2_3_node_346 | 0.4 | n |  | TRUE
60 | bus_LV_3394-1_2_3_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_3394-1_2_3_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_3394-1_2_3_node_61 | 0.4 | n |  | TRUE
63 | bus_LV_3394-1_2_3_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_3394-1_2_3_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_3394-1_2_3_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_3394-1_2_3_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_3394-1_2_3_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_3394-1_2_3_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_3394-1_2_3_node_70 | 0.4 | n |  | TRUE
70 | bus_LV_3394-1_2_3_node_265 | 0.4 | n |  | TRUE
71 | bus_LV_3394-1_2_3_node_262 | 0.4 | n |  | TRUE
72 | bus_LV_3394-1_2_3_node_285 | 0.4 | n |  | TRUE
73 | bus_LV_3394-1_2_3_node_263 | 0.4 | n |  | TRUE
74 | bus_LV_3394-1_2_3_node_264 | 0.4 | n |  | TRUE
75 | bus_LV_3394-1_2_3_node_104 | 0.4 | n |  | TRUE
76 | bus_LV_3394-1_2_3_node_295 | 0.4 | n |  | TRUE
77 | bus_LV_3394-1_2_3_node_288 | 0.4 | n |  | TRUE
78 | bus_LV_3394-1_2_3_node_113 | 0.4 | n |  | TRUE
79 | bus_LV_3394-1_2_3_node_114 | 0.4 | n |  | TRUE
80 | bus_LV_3394-1_2_3_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_3394-1_2_3_node_116 | 0.4 | n |  | TRUE
82 | bus_LV_3394-1_2_3_node_292 | 0.4 | n |  | TRUE
83 | bus_LV_3394-1_2_3_node_290 | 0.4 | n |  | TRUE
84 | bus_LV_3394-1_2_3_node_117 | 0.4 | n |  | TRUE
85 | bus_LV_3394-1_2_3_node_118 | 0.4 | n |  | TRUE
86 | bus_LV_3394-1_2_3_node_121 | 0.4 | n |  | TRUE
87 | bus_LV_3394-1_2_3_node_119 | 0.4 | n |  | TRUE
88 | bus_LV_3394-1_2_3_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_3394-1_2_3_node_123 | 0.4 | n |  | TRUE
90 | bus_LV_3394-1_2_3_node_126 | 0.4 | n |  | TRUE
91 | bus_LV_3394-1_2_3_node_127 | 0.4 | n |  | TRUE
92 | bus_LV_3394-1_2_3_node_229 | 0.4 | n |  | TRUE
93 | bus_LV_3394-1_2_3_node_136 | 0.4 | n |  | TRUE
94 | bus_LV_3394-1_2_3_node_133 | 0.4 | n |  | TRUE
95 | bus_LV_3394-1_2_3_node_128 | 0.4 | n |  | TRUE
96 | bus_LV_3394-1_2_3_node_244 | 0.4 | n |  | TRUE
97 | bus_LV_3394-1_2_3_node_232 | 0.4 | n |  | TRUE
98 | bus_LV_3394-1_2_3_node_227 | 0.4 | n |  | TRUE
99 | bus_LV_3394-1_2_3_node_134 | 0.4 | n |  | TRUE
100 | bus_LV_3394-1_2_3_node_131 | 0.4 | n |  | TRUE
101 | bus_LV_3394-1_2_3_node_240 | 0.4 | n |  | TRUE
102 | bus_LV_3394-1_2_3_node_129 | 0.4 | n |  | TRUE
103 | bus_LV_3394-1_2_3_node_130 | 0.4 | n |  | TRUE
104 | bus_LV_3394-1_2_3_node_132 | 0.4 | n |  | TRUE
105 | bus_LV_3394-1_2_3_node_135 | 0.4 | n |  | TRUE
106 | bus_LV_3394-1_2_3_node_153 | 0.4 | n |  | TRUE
107 | bus_LV_3394-1_2_3_node_158 | 0.4 | n |  | TRUE
108 | bus_LV_3394-1_2_3_node_151 | 0.4 | n |  | TRUE
109 | bus_LV_3394-1_2_3_node_147 | 0.4 | n |  | TRUE
110 | bus_LV_3394-1_2_3_node_148 | 0.4 | n |  | TRUE
111 | bus_LV_3394-1_2_3_node_149 | 0.4 | n |  | TRUE
112 | bus_LV_3394-1_2_3_node_150 | 0.4 | n |  | TRUE
113 | bus_LV_3394-1_2_3_node_152 | 0.4 | n |  | TRUE
114 | bus_LV_3394-1_2_3_node_154 | 0.4 | n |  | TRUE
115 | bus_LV_3394-1_2_3_node_155 | 0.4 | n |  | TRUE
116 | bus_LV_3394-1_2_3_node_156 | 0.4 | n |  | TRUE
117 | bus_LV_3394-1_2_3_node_159 | 0.4 | n |  | TRUE
118 | bus_LV_3394-1_2_3_node_157 | 0.4 | n |  | TRUE
119 | bus_LV_3394-1_2_3_node_339 | 0.4 | n |  | TRUE
120 | bus_LV_3394-1_2_3_node_192 | 0.4 | n |  | TRUE
121 | bus_LV_3394-1_2_3_node_340 | 0.4 | n |  | TRUE
122 | bus_LV_3394-1_2_3_node_341 | 0.4 | n |  | TRUE
123 | bus_LV_3394-1_2_3_node_160 | 0.4 | n |  | TRUE
124 | bus_LV_3394-1_2_3_node_161 | 0.4 | n |  | TRUE
125 | bus_LV_3394-1_2_3_node_162 | 0.4 | n |  | TRUE
126 | bus_LV_3394-1_2_3_node_163 | 0.4 | n |  | TRUE
127 | bus_LV_3394-1_2_3_node_164 | 0.4 | n |  | TRUE
128 | bus_LV_3394-1_2_3_node_165 | 0.4 | n |  | TRUE
129 | bus_LV_3394-1_2_3_node_166 | 0.4 | n |  | TRUE
130 | bus_LV_3394-1_2_3_node_167 | 0.4 | n |  | TRUE
131 | bus_LV_3394-1_2_3_node_168 | 0.4 | n |  | TRUE
132 | bus_LV_3394-1_2_3_node_169 | 0.4 | n |  | TRUE
133 | bus_LV_3394-1_2_3_node_170 | 0.4 | n |  | TRUE
134 | bus_LV_3394-1_2_3_node_184 | 0.4 | n |  | TRUE
135 | bus_LV_3394-1_2_3_node_185 | 0.4 | n |  | TRUE
136 | bus_LV_3394-1_2_3_node_171 | 0.4 | n |  | TRUE
137 | bus_LV_3394-1_2_3_node_172 | 0.4 | n |  | TRUE
138 | bus_LV_3394-1_2_3_node_173 | 0.4 | n |  | TRUE
139 | bus_LV_3394-1_2_3_node_174 | 0.4 | n |  | TRUE
140 | bus_LV_3394-1_2_3_node_175 | 0.4 | n |  | TRUE
141 | bus_LV_3394-1_2_3_node_176 | 0.4 | n |  | TRUE
142 | bus_LV_3394-1_2_3_node_177 | 0.4 | n |  | TRUE
143 | bus_LV_3394-1_2_3_node_178 | 0.4 | n |  | TRUE
144 | bus_LV_3394-1_2_3_node_182 | 0.4 | n |  | TRUE
145 | bus_LV_3394-1_2_3_node_179 | 0.4 | n |  | TRUE
146 | bus_LV_3394-1_2_3_node_180 | 0.4 | n |  | TRUE
147 | bus_LV_3394-1_2_3_node_181 | 0.4 | n |  | TRUE
148 | bus_LV_3394-1_2_3_node_183 | 0.4 | n |  | TRUE
149 | bus_LV_3394-1_2_3_node_190 | 0.4 | n |  | TRUE
150 | bus_LV_3394-1_2_3_node_226 | 0.4 | n |  | TRUE
151 | bus_LV_3394-1_2_3_node_230 | 0.4 | n |  | TRUE
152 | bus_LV_3394-1_2_3_node_233 | 0.4 | n |  | TRUE
153 | bus_LV_3394-1_2_3_node_234 | 0.4 | n |  | TRUE
154 | bus_LV_3394-1_2_3_node_291 | 0.4 | n |  | TRUE
155 | bus_LV_3394-1_2_3_node_242 | 0.4 | n |  | TRUE
156 | bus_LV_3394-1_2_3_node_239 | 0.4 | n |  | TRUE
157 | bus_LV_3394-1_2_3_node_236 | 0.4 | n |  | TRUE
158 | bus_LV_3394-1_2_3_node_237 | 0.4 | n |  | TRUE
159 | bus_LV_3394-1_2_3_node_238 | 0.4 | n |  | TRUE
160 | bus_LV_3394-1_2_3_node_241 | 0.4 | n |  | TRUE
161 | bus_LV_3394-1_2_3_node_243 | 0.4 | n |  | TRUE
162 | bus_LV_3394-1_2_3_node_245 | 0.4 | n |  | TRUE
163 | bus_LV_3394-1_2_3_node_246 | 0.4 | n |  | TRUE
164 | bus_LV_3394-1_2_3_node_247 | 0.4 | n |  | TRUE
165 | bus_LV_3394-1_2_3_node_248 | 0.4 | n |  | TRUE
166 | bus_LV_3394-1_2_3_node_261 | 0.4 | n |  | TRUE
167 | bus_LV_3394-1_2_3_node_250 | 0.4 | n |  | TRUE
168 | bus_LV_3394-1_2_3_node_259 | 0.4 | n |  | TRUE
169 | bus_LV_3394-1_2_3_node_249 | 0.4 | n |  | TRUE
170 | bus_LV_3394-1_2_3_node_273 | 0.4 | n |  | TRUE
171 | bus_LV_3394-1_2_3_node_267 | 0.4 | n |  | TRUE
172 | bus_LV_3394-1_2_3_node_275 | 0.4 | n |  | TRUE
173 | bus_LV_3394-1_2_3_node_266 | 0.4 | n |  | TRUE
174 | bus_LV_3394-1_2_3_node_251 | 0.4 | n |  | TRUE
175 | bus_LV_3394-1_2_3_node_252 | 0.4 | n |  | TRUE
176 | bus_LV_3394-1_2_3_node_253 | 0.4 | n |  | TRUE
177 | bus_LV_3394-1_2_3_node_254 | 0.4 | n |  | TRUE
178 | bus_LV_3394-1_2_3_node_255 | 0.4 | n |  | TRUE
179 | bus_LV_3394-1_2_3_node_256 | 0.4 | n |  | TRUE
180 | bus_LV_3394-1_2_3_node_257 | 0.4 | n |  | TRUE
181 | bus_LV_3394-1_2_3_node_258 | 0.4 | n |  | TRUE
182 | bus_LV_3394-1_2_3_node_260 | 0.4 | n |  | TRUE
183 | bus_LV_3394-1_2_3_node_286 | 0.4 | n |  | TRUE
184 | bus_LV_3394-1_2_3_node_268 | 0.4 | n |  | TRUE
185 | bus_LV_3394-1_2_3_node_269 | 0.4 | n |  | TRUE
186 | bus_LV_3394-1_2_3_node_270 | 0.4 | n |  | TRUE
187 | bus_LV_3394-1_2_3_node_271 | 0.4 | n |  | TRUE
188 | bus_LV_3394-1_2_3_node_272 | 0.4 | n |  | TRUE
189 | bus_LV_3394-1_2_3_node_289 | 0.4 | n |  | TRUE
190 | bus_LV_3394-1_2_3_node_278 | 0.4 | n |  | TRUE
191 | bus_LV_3394-1_2_3_node_279 | 0.4 | n |  | TRUE
192 | bus_LV_3394-1_2_3_node_277 | 0.4 | n |  | TRUE
193 | bus_LV_3394-1_2_3_node_293 | 0.4 | n |  | TRUE
194 | bus_LV_3394-1_2_3_node_310 | 0.4 | n |  | TRUE
195 | bus_LV_3394-1_2_3_node_311 | 0.4 | n |  | TRUE
196 | bus_MV_154_0_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3394-1_2_3_load_9 | 0 | 0.001106 | 0.0002772 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3394-1_2_3_load_10 | 1 | 0.00090025 | 0.00022562 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3394-1_2_3_load_13 | 4 | 0.00010734 | 2.6902e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3394-1_2_3_load_14 | 5 | 0.00065176 | 0.00016335 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3394-1_2_3_load_15 | 6 | 0.00045116 | 0.00011307 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3394-1_2_3_load_20 | 8 | 0.00047995 | 0.00012029 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3394-1_2_3_load_17 | 9 | 0.00024608 | 6.1673e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3394-1_2_3_load_21 | 10 | 0.00021739 | 5.4483e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3394-1_2_3_load_18 | 11 | 6.6724e-05 | 1.6723e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3394-1_2_3_load_186 | 15 | 8.9374e-05 | 2.2399e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3394-1_2_3_load_189 | 16 | 0.00014619 | 3.6638e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3394-1_2_3_load_22 | 17 | 0.00031934 | 8.0035e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3394-1_2_3_load_23 | 18 | 0.0024688 | 0.00061873 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3394-1_2_3_load_25 | 20 | 0.00098615 | 0.00024715 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3394-1_2_3_load_26 | 21 | 0.00068193 | 0.00017091 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3394-1_2_3_load_28 | 23 | 0.0029452 | 0.00073814 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3394-1_2_3_load_111 | 25 | 0.0015885 | 0.00039812 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3394-1_2_3_load_31 | 27 | 0.0003356 | 8.411e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3394-1_2_3_load_112 | 28 | 0.00039514 | 9.9032e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3394-1_2_3_load_33 | 29 | 0.00091016 | 0.00022811 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3394-1_2_3_load_39 | 31 | 0.0011312 | 0.00028352 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3394-1_2_3_load_35 | 32 | 0.0012169 | 0.00030498 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3394-1_2_3_load_37 | 33 | 0.0007027 | 0.00017611 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3394-1_2_3_load_45 | 35 | 0.00084656 | 0.00021217 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3394-1_2_3_load_46 | 36 | 0.00050918 | 0.00012761 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3394-1_2_3_load_47 | 37 | 0.00030148 | 7.5558e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3394-1_2_3_load_48 | 38 | 0.00050936 | 0.00012766 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3394-1_2_3_load_42 | 39 | 0.0031493 | 0.00078928 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3394-1_2_3_load_34 | 40 | 0.0015664 | 0.00039257 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3394-1_2_3_load_54 | 42 | 0.0012648 | 0.00031699 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3394-1_2_3_load_49 | 43 | 0.0010498 | 0.0002631 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3394-1_2_3_load_43 | 44 | 0.00046636 | 0.00011688 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3394-1_2_3_load_40 | 45 | 0.00075822 | 0.00019003 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3394-1_2_3_load_41 | 46 | 0.00090809 | 0.00022759 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3394-1_2_3_load_44 | 50 | 0.0010886 | 0.00027282 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3394-1_2_3_load_52 | 53 | 0.0011697 | 0.00029315 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3394-1_2_3_load_55 | 54 | 0.00067922 | 0.00017023 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3394-1_2_3_load_51 | 56 | 0.00086496 | 0.00021678 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3394-1_2_3_load_57 | 57 | 0.00028352 | 7.1057e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3394-1_2_3_load_346 | 59 | 0.00036519 | 9.1525e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3394-1_2_3_load_59 | 60 | 0.00011542 | 2.8927e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3394-1_2_3_load_60 | 61 | 0.00016102 | 4.0356e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3394-1_2_3_load_62 | 63 | 0.00014349 | 3.5963e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3394-1_2_3_load_63 | 64 | 7.3596e-05 | 1.8445e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3394-1_2_3_load_68 | 67 | 0.00022561 | 5.6544e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3394-1_2_3_load_69 | 68 | 0.00067314 | 0.0001687 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3394-1_2_3_load_70 | 69 | 9.7715e-05 | 2.449e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3394-1_2_3_load_265 | 70 | 6.6966e-05 | 1.6783e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3394-1_2_3_load_262 | 71 | 0.00011273 | 2.8252e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3394-1_2_3_load_264 | 74 | 0.00021283 | 5.3339e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3394-1_2_3_load_295 | 76 | 0.00035247 | 8.8338e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3394-1_2_3_load_288 | 77 | 0.00013822 | 3.4641e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3394-1_2_3_load_114 | 79 | 0.0040878 | 0.0010245 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3394-1_2_3_load_115 | 80 | 0.000614 | 0.00015388 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3394-1_2_3_load_116 | 81 | 0.0013296 | 0.00033324 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3394-1_2_3_load_290 | 83 | 0.00072177 | 0.00018089 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3394-1_2_3_load_117 | 84 | 0.00050384 | 0.00012627 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3394-1_2_3_load_121 | 86 | 0.00043845 | 0.00010989 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3394-1_2_3_load_122 | 88 | 0.00044817 | 0.00011232 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3394-1_2_3_load_136 | 93 | 0.00084618 | 0.00021207 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3394-1_2_3_load_128 | 95 | 0.00090087 | 0.00022578 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3394-1_2_3_load_244 | 96 | 0.0021075 | 0.00052818 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3394-1_2_3_load_232 | 97 | 0.00067819 | 0.00016997 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3394-1_2_3_load_134 | 99 | 0.00098574 | 0.00024705 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3394-1_2_3_load_131 | 100 | 0.00024899 | 6.2402e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3394-1_2_3_load_240 | 101 | 0.0013271 | 0.0003326 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3394-1_2_3_load_129 | 102 | 0.00086791 | 0.00021752 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3394-1_2_3_load_130 | 103 | 0.00039094 | 9.7979e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3394-1_2_3_load_132 | 104 | 0.00032342 | 8.1057e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3394-1_2_3_load_135 | 105 | 0.00038753 | 9.7123e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3394-1_2_3_load_158 | 107 | 0.0008185 | 0.00020514 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3394-1_2_3_load_151 | 108 | 0.00035622 | 8.9277e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3394-1_2_3_load_147 | 109 | 0.00023144 | 5.8005e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3394-1_2_3_load_148 | 110 | 0.0010496 | 0.00026305 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3394-1_2_3_load_150 | 112 | 0.00016996 | 4.2597e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3394-1_2_3_load_152 | 113 | 0.00067131 | 0.00016825 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3394-1_2_3_load_155 | 115 | 0.00025359 | 6.3557e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3394-1_2_3_load_156 | 116 | 0.00028295 | 7.0915e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3394-1_2_3_load_159 | 117 | 0.00061008 | 0.0001529 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3394-1_2_3_load_157 | 118 | 6.318e-05 | 1.5834e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3394-1_2_3_load_339 | 119 | 8.9399e-05 | 2.2405e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3394-1_2_3_load_192 | 120 | 7.2241e-05 | 1.8105e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3394-1_2_3_load_340 | 121 | 0.00016192 | 4.058e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3394-1_2_3_load_341 | 122 | 4.4634e-05 | 1.1186e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3394-1_2_3_load_160 | 123 | 0.0010789 | 0.00027039 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3394-1_2_3_load_161 | 124 | 0.00020706 | 5.1894e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3394-1_2_3_load_162 | 125 | 0.00045936 | 0.00011513 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3394-1_2_3_load_163 | 126 | 0.00065616 | 0.00016445 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3394-1_2_3_load_164 | 127 | 0.00021146 | 5.2997e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3394-1_2_3_load_165 | 128 | 0.00011851 | 2.9702e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3394-1_2_3_load_167 | 130 | 0.00026713 | 6.6949e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3394-1_2_3_load_168 | 131 | 0.00011065 | 2.7732e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3394-1_2_3_load_169 | 132 | 7.2903e-05 | 1.8271e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3394-1_2_3_load_170 | 133 | 0.0001188 | 2.9773e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3394-1_2_3_load_184 | 134 | 4.4868e-05 | 1.1245e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3394-1_2_3_load_185 | 135 | 7.8113e-05 | 1.9577e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3394-1_2_3_load_171 | 136 | 0.00015452 | 3.8727e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3394-1_2_3_load_172 | 137 | 0.00026789 | 6.714e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3394-1_2_3_load_173 | 138 | 0.00013339 | 3.343e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3394-1_2_3_load_174 | 139 | 6.1969e-05 | 1.5531e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3394-1_2_3_load_176 | 141 | 0.00012624 | 3.1639e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3394-1_2_3_load_177 | 142 | 9.5416e-05 | 2.3914e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3394-1_2_3_load_178 | 143 | 7.7739e-05 | 1.9483e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3394-1_2_3_load_182 | 144 | 0.0005945 | 0.000149 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3394-1_2_3_load_179 | 145 | 8.9029e-05 | 2.2313e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3394-1_2_3_load_180 | 146 | 8.1031e-05 | 2.0308e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3394-1_2_3_load_181 | 147 | 8.9328e-05 | 2.2388e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3394-1_2_3_load_183 | 148 | 0.00091077 | 0.00022826 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3394-1_2_3_load_190 | 149 | 0.00059767 | 0.00014979 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3394-1_2_3_load_226 | 150 | 0.00161 | 0.0004035 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3394-1_2_3_load_233 | 152 | 0.00047915 | 0.00012009 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3394-1_2_3_load_234 | 153 | 0.00046669 | 0.00011696 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3394-1_2_3_load_291 | 154 | 0.0021279 | 0.0005333 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3394-1_2_3_load_242 | 155 | 0.0008036 | 0.0002014 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3394-1_2_3_load_236 | 157 | 0.00086816 | 0.00021758 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3394-1_2_3_load_237 | 158 | 0.00052991 | 0.00013281 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3394-1_2_3_load_238 | 159 | 0.0020835 | 0.00052217 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3394-1_2_3_load_241 | 160 | 0.0011176 | 0.0002801 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3394-1_2_3_load_243 | 161 | 0.00097084 | 0.00024331 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3394-1_2_3_load_246 | 163 | 0.00058215 | 0.0001459 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3394-1_2_3_load_247 | 164 | 0.0011376 | 0.00028512 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3394-1_2_3_load_248 | 165 | 0.00043702 | 0.00010953 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3394-1_2_3_load_261 | 166 | 0.0021625 | 0.00054198 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_3394-1_2_3_load_250 | 167 | 0.00051074 | 0.000128 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_3394-1_2_3_load_249 | 169 | 0.00062034 | 0.00015547 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_3394-1_2_3_load_267 | 171 | 0.001429 | 0.00035813 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_3394-1_2_3_load_275 | 172 | 0.00066472 | 0.0001666 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_3394-1_2_3_load_266 | 173 | 0.00061208 | 0.0001534 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_3394-1_2_3_load_251 | 174 | 0.00014854 | 3.7229e-05 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_3394-1_2_3_load_252 | 175 | 0.00014608 | 3.6611e-05 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_3394-1_2_3_load_253 | 176 | 0.00015193 | 3.8076e-05 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_3394-1_2_3_load_254 | 177 | 0.00011598 | 2.9068e-05 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_3394-1_2_3_load_255 | 178 | 0.00030119 | 7.5485e-05 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_3394-1_2_3_load_256 | 179 | 0.00039949 | 0.00010012 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_3394-1_2_3_load_257 | 180 | 8.436e-05 | 2.1143e-05 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_3394-1_2_3_load_258 | 181 | 0.00010815 | 2.7105e-05 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_3394-1_2_3_load_260 | 182 | 0.00050915 | 0.00012761 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_3394-1_2_3_load_286 | 183 | 5.6606e-05 | 1.4187e-05 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_3394-1_2_3_load_269 | 185 | 0.0015487 | 0.00038813 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_3394-1_2_3_load_270 | 186 | 0.0013791 | 0.00034564 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_3394-1_2_3_load_271 | 187 | 0.000797 | 0.00019975 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_3394-1_2_3_load_272 | 188 | 0.0027098 | 0.00067913 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_3394-1_2_3_load_289 | 189 | 0.0010363 | 0.00025973 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_3394-1_2_3_load_278 | 190 | 0.00083846 | 0.00021014 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_3394-1_2_3_load_279 | 191 | 0.00087409 | 0.00021907 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_3394-1_2_3_load_277 | 192 | 0.00084209 | 0.00021105 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_3394-1_2_3_load_293 | 193 | 0.00059876 | 0.00015006 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_3394-1_2_3_load_310 | 194 | 6.1701e-05 | 1.5464e-05 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_3394-1_2_3_load_311 | 195 | 9.3835e-05 | 2.3517e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3394-1_2_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.14079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3394-1_2_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.03719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3394-1_2_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0089848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3394-1_2_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.15396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3394-1_2_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.070993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3394-1_2_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.12724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3394-1_2_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.029089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3394-1_2_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.044037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3394-1_2_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.01361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3394-1_2_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.070005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3394-1_2_3_line_10 | NAYY 4x150 SE | 10 | 17 | 0.02807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3394-1_2_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.18147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3394-1_2_3_line_12 | NAYY 4x150 SE | 12 | 13 | 0.45904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3394-1_2_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.034109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3394-1_2_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.30327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3394-1_2_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.089992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3394-1_2_3_line_16 | NAYY 4x150 SE | 15 | 144 | 0.036048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3394-1_2_3_line_17 | NAYY 4x150 SE | 16 | 149 | 0.010497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3394-1_2_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.0053204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3394-1_2_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.021809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3394-1_2_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.1045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_3394-1_2_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.080213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_3394-1_2_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.069847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_3394-1_2_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.18894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_3394-1_2_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.27664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_3394-1_2_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.068779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_3394-1_2_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.51074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_3394-1_2_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.043158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3394-1_2_3_line_28 | NAYY 4x150 SE | 25 | 28 | 0.018141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_3394-1_2_3_line_29 | NAYY 4x150 SE | 26 | 29 | 0.081573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_3394-1_2_3_line_30 | NAYY 4x150 SE | 28 | 78 | 0.23738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_3394-1_2_3_line_31 | NAYY 4x150 SE | 29 | 33 | 0.037445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_3394-1_2_3_line_32 | NAYY 4x150 SE | 30 | 31 | 0.059005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_3394-1_2_3_line_33 | NAYY 4x150 SE | 30 | 32 | 0.03502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_3394-1_2_3_line_34 | NAYY 4x150 SE | 31 | 39 | 0.21118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_3394-1_2_3_line_35 | NAYY 4x150 SE | 32 | 40 | 0.020497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_3394-1_2_3_line_36 | NAYY 4x150 SE | 33 | 41 | 0.012465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_3394-1_2_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.060375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3394-1_2_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.052335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3394-1_2_3_line_39 | NAYY 4x150 SE | 34 | 37 | 0.41223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3394-1_2_3_line_40 | NAYY 4x150 SE | 34 | 38 | 0.0436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3394-1_2_3_line_41 | NAYY 4x150 SE | 36 | 42 | 0.037432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3394-1_2_3_line_42 | NAYY 4x150 SE | 38 | 43 | 0.031712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3394-1_2_3_line_43 | NAYY 4x150 SE | 39 | 44 | 0.019194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_3394-1_2_3_line_44 | NAYY 4x150 SE | 40 | 41 | 0.03558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_3394-1_2_3_line_45 | NAYY 4x150 SE | 42 | 54 | 0.00056988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3394-1_2_3_line_46 | NAYY 4x150 SE | 43 | 55 | 0.21313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3394-1_2_3_line_47 | NAYY 4x150 SE | 44 | 50 | 0.010361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3394-1_2_3_line_48 | NAYY 4x150 SE | 45 | 46 | 0.021282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3394-1_2_3_line_49 | NAYY 4x150 SE | 46 | 47 | 0.0097636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3394-1_2_3_line_50 | NAYY 4x150 SE | 47 | 48 | 0.007956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3394-1_2_3_line_51 | NAYY 4x150 SE | 47 | 49 | 0.014273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3394-1_2_3_line_52 | NAYY 4x150 SE | 48 | 72 | 0.34496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3394-1_2_3_line_53 | NAYY 4x150 SE | 48 | 177 | 0.02194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3394-1_2_3_line_54 | NAYY 4x150 SE | 49 | 170 | 0.006458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3394-1_2_3_line_55 | NAYY 4x150 SE | 49 | 182 | 0.026483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3394-1_2_3_line_56 | NAYY 4x150 SE | 50 | 51 | 0.017745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3394-1_2_3_line_57 | NAYY 4x150 SE | 51 | 52 | 0.17472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3394-1_2_3_line_58 | NAYY 4x150 SE | 51 | 53 | 0.034413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3394-1_2_3_line_59 | NAYY 4x150 SE | 52 | 57 | 0.33266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3394-1_2_3_line_60 | NAYY 4x150 SE | 52 | 58 | 0.006975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3394-1_2_3_line_61 | NAYY 4x150 SE | 53 | 55 | 0.071664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3394-1_2_3_line_62 | NAYY 4x150 SE | 55 | 56 | 0.36274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3394-1_2_3_line_63 | NAYY 4x150 SE | 58 | 59 | 0.16057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3394-1_2_3_line_64 | NAYY 4x150 SE | 60 | 61 | 0.013185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3394-1_2_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.0722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3394-1_2_3_line_66 | NAYY 4x150 SE | 61 | 63 | 0.4604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3394-1_2_3_line_67 | NAYY 4x150 SE | 62 | 64 | 0.092189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3394-1_2_3_line_68 | NAYY 4x150 SE | 64 | 65 | 0.40988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3394-1_2_3_line_69 | NAYY 4x150 SE | 65 | 66 | 0.077837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3394-1_2_3_line_70 | NAYY 4x150 SE | 65 | 67 | 0.17076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3394-1_2_3_line_71 | NAYY 4x150 SE | 66 | 68 | 0.017407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3394-1_2_3_line_72 | NAYY 4x150 SE | 66 | 69 | 0.024389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3394-1_2_3_line_73 | NAYY 4x150 SE | 68 | 70 | 0.1493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3394-1_2_3_line_74 | NAYY 4x150 SE | 69 | 71 | 0.016642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3394-1_2_3_line_75 | NAYY 4x150 SE | 70 | 72 | 0.05085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3394-1_2_3_line_76 | NAYY 4x150 SE | 71 | 73 | 0.17508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3394-1_2_3_line_77 | NAYY 4x150 SE | 72 | 183 | 0.0096859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3394-1_2_3_line_78 | NAYY 4x150 SE | 73 | 74 | 0.23383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3394-1_2_3_line_79 | NAYY 4x150 SE | 74 | 77 | 0.020002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3394-1_2_3_line_80 | NAYY 4x150 SE | 75 | 76 | 0.015179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3394-1_2_3_line_81 | NAYY 4x150 SE | 75 | 77 | 0.017454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3394-1_2_3_line_82 | NAYY 4x150 SE | 78 | 79 | 0.055074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_3394-1_2_3_line_83 | NAYY 4x150 SE | 78 | 80 | 0.16939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_3394-1_2_3_line_84 | NAYY 4x150 SE | 80 | 81 | 0.0036525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_3394-1_2_3_line_85 | NAYY 4x150 SE | 81 | 82 | 0.033492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_3394-1_2_3_line_86 | NAYY 4x150 SE | 82 | 83 | 0.010842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_3394-1_2_3_line_87 | NAYY 4x150 SE | 83 | 189 | 0.010081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_3394-1_2_3_line_88 | NAYY 4x150 SE | 84 | 85 | 0.0022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3394-1_2_3_line_89 | NAYY 4x150 SE | 85 | 86 | 0.08979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3394-1_2_3_line_90 | NAYY 4x150 SE | 86 | 90 | 0.030023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3394-1_2_3_line_91 | NAYY 4x150 SE | 87 | 88 | 0.11035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_3394-1_2_3_line_92 | NAYY 4x150 SE | 87 | 89 | 0.17505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_3394-1_2_3_line_93 | NAYY 4x150 SE | 88 | 90 | 0.0095549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_3394-1_2_3_line_94 | NAYY 4x150 SE | 89 | 91 | 0.032279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_3394-1_2_3_line_95 | NAYY 4x150 SE | 90 | 92 | 0.047655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_3394-1_2_3_line_96 | NAYY 4x150 SE | 91 | 93 | 0.066432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3394-1_2_3_line_97 | NAYY 4x150 SE | 91 | 94 | 0.030922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_3394-1_2_3_line_98 | NAYY 4x150 SE | 92 | 97 | 0.0084749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3394-1_2_3_line_99 | NAYY 4x150 SE | 92 | 98 | 0.007417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_3394-1_2_3_line_100 | NAYY 4x150 SE | 94 | 99 | 0.28215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_3394-1_2_3_line_101 | NAYY 4x150 SE | 94 | 100 | 0.25295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3394-1_2_3_line_102 | NAYY 4x150 SE | 95 | 96 | 0.023885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3394-1_2_3_line_103 | NAYY 4x150 SE | 96 | 101 | 0.032742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3394-1_2_3_line_104 | NAYY 4x150 SE | 97 | 154 | 0.04262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3394-1_2_3_line_105 | NAYY 4x150 SE | 98 | 151 | 0.033873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_3394-1_2_3_line_106 | NAYY 4x150 SE | 98 | 150 | 0.025459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3394-1_2_3_line_107 | NAYY 4x150 SE | 99 | 105 | 0.20231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_3394-1_2_3_line_108 | NAYY 4x150 SE | 100 | 102 | 0.023135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3394-1_2_3_line_109 | NAYY 4x150 SE | 101 | 159 | 0.00083492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3394-1_2_3_line_110 | NAYY 4x150 SE | 102 | 103 | 0.0018855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_3394-1_2_3_line_111 | NAYY 4x150 SE | 103 | 104 | 0.20158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3394-1_2_3_line_112 | NAYY 4x150 SE | 105 | 106 | 0.17138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
113 | LV_3394-1_2_3_line_113 | NAYY 4x150 SE | 106 | 107 | 0.015399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3394-1_2_3_line_114 | NAYY 4x150 SE | 106 | 108 | 0.1862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3394-1_2_3_line_115 | NAYY 4x150 SE | 107 | 117 | 0.16698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3394-1_2_3_line_116 | NAYY 4x150 SE | 108 | 111 | 0.092851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3394-1_2_3_line_117 | NAYY 4x150 SE | 109 | 110 | 0.010933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3394-1_2_3_line_118 | NAYY 4x150 SE | 109 | 111 | 0.35639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3394-1_2_3_line_119 | NAYY 4x150 SE | 111 | 112 | 0.16568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3394-1_2_3_line_120 | NAYY 4x150 SE | 112 | 113 | 0.0014932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3394-1_2_3_line_121 | NAYY 4x150 SE | 113 | 114 | 0.088143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3394-1_2_3_line_122 | NAYY 4x150 SE | 114 | 115 | 0.11108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3394-1_2_3_line_123 | NAYY 4x150 SE | 114 | 116 | 0.17293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3394-1_2_3_line_124 | NAYY 4x150 SE | 117 | 123 | 0.031599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3394-1_2_3_line_125 | NAYY 4x150 SE | 118 | 119 | 0.28677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3394-1_2_3_line_126 | NAYY 4x150 SE | 118 | 120 | 0.7249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3394-1_2_3_line_127 | NAYY 4x150 SE | 119 | 121 | 0.088311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3394-1_2_3_line_128 | NAYY 4x150 SE | 119 | 122 | 0.22254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3394-1_2_3_line_129 | NAYY 4x150 SE | 121 | 133 | 0.021312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3394-1_2_3_line_130 | NAYY 4x150 SE | 123 | 124 | 0.0049504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3394-1_2_3_line_131 | NAYY 4x150 SE | 124 | 125 | 0.042697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3394-1_2_3_line_132 | NAYY 4x150 SE | 125 | 126 | 0.050722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3394-1_2_3_line_133 | NAYY 4x150 SE | 126 | 127 | 0.050451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3394-1_2_3_line_134 | NAYY 4x150 SE | 127 | 128 | 0.082014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3394-1_2_3_line_135 | NAYY 4x150 SE | 128 | 129 | 0.03058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3394-1_2_3_line_136 | NAYY 4x150 SE | 129 | 130 | 0.12574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3394-1_2_3_line_137 | NAYY 4x150 SE | 129 | 131 | 0.028207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3394-1_2_3_line_138 | NAYY 4x150 SE | 130 | 132 | 0.0026687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3394-1_2_3_line_139 | NAYY 4x150 SE | 131 | 133 | 0.016171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3394-1_2_3_line_140 | NAYY 4x150 SE | 132 | 134 | 0.019164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3394-1_2_3_line_141 | NAYY 4x150 SE | 134 | 135 | 0.01978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3394-1_2_3_line_142 | NAYY 4x150 SE | 135 | 148 | 0.019666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3394-1_2_3_line_143 | NAYY 4x150 SE | 136 | 137 | 0.0061259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3394-1_2_3_line_144 | NAYY 4x150 SE | 136 | 138 | 0.024846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3394-1_2_3_line_145 | NAYY 4x150 SE | 137 | 139 | 0.015344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3394-1_2_3_line_146 | NAYY 4x150 SE | 138 | 140 | 0.1175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3394-1_2_3_line_147 | NAYY 4x150 SE | 139 | 141 | 0.019256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3394-1_2_3_line_148 | NAYY 4x150 SE | 140 | 142 | 0.19734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3394-1_2_3_line_149 | NAYY 4x150 SE | 141 | 143 | 0.013523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_3394-1_2_3_line_150 | NAYY 4x150 SE | 142 | 144 | 0.035095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_3394-1_2_3_line_151 | NAYY 4x150 SE | 143 | 145 | 0.032992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_3394-1_2_3_line_152 | NAYY 4x150 SE | 145 | 146 | 0.019207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_3394-1_2_3_line_153 | NAYY 4x150 SE | 146 | 147 | 0.013461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_3394-1_2_3_line_154 | NAYY 4x150 SE | 147 | 148 | 0.0016507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_3394-1_2_3_line_155 | NAYY 4x150 SE | 151 | 152 | 0.068745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_3394-1_2_3_line_156 | NAYY 4x150 SE | 151 | 153 | 0.0043823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
157 | LV_3394-1_2_3_line_157 | NAYY 4x150 SE | 153 | 155 | 0.011697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
158 | LV_3394-1_2_3_line_158 | NAYY 4x150 SE | 155 | 156 | 0.035853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
159 | LV_3394-1_2_3_line_159 | NAYY 4x150 SE | 156 | 160 | 0.0099627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
160 | LV_3394-1_2_3_line_160 | NAYY 4x150 SE | 156 | 161 | 0.013495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_3394-1_2_3_line_161 | NAYY 4x150 SE | 156 | 158 | 0.018855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_3394-1_2_3_line_162 | NAYY 4x150 SE | 157 | 158 | 0.024441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_3394-1_2_3_line_163 | NAYY 4x150 SE | 157 | 159 | 0.014991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_3394-1_2_3_line_164 | NAYY 4x150 SE | 160 | 162 | 0.0091442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
165 | LV_3394-1_2_3_line_165 | NAYY 4x150 SE | 161 | 163 | 0.017308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_3394-1_2_3_line_166 | NAYY 4x150 SE | 162 | 164 | 0.019751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_3394-1_2_3_line_167 | NAYY 4x150 SE | 162 | 165 | 0.01222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
168 | LV_3394-1_2_3_line_168 | NAYY 4x150 SE | 163 | 166 | 0.0062269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_3394-1_2_3_line_169 | NAYY 4x150 SE | 165 | 167 | 0.0074563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
170 | LV_3394-1_2_3_line_170 | NAYY 4x150 SE | 166 | 168 | 0.010287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
171 | LV_3394-1_2_3_line_171 | NAYY 4x150 SE | 167 | 171 | 0.0091468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
172 | LV_3394-1_2_3_line_172 | NAYY 4x150 SE | 168 | 182 | 0.020376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
173 | LV_3394-1_2_3_line_173 | NAYY 4x150 SE | 168 | 180 | 0.013455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
174 | LV_3394-1_2_3_line_174 | NAYY 4x150 SE | 169 | 170 | 0.025164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
175 | LV_3394-1_2_3_line_175 | NAYY 4x150 SE | 170 | 172 | 0.029776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
176 | LV_3394-1_2_3_line_176 | NAYY 4x150 SE | 171 | 173 | 0.016152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
177 | LV_3394-1_2_3_line_177 | NAYY 4x150 SE | 172 | 192 | 0.043437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
178 | LV_3394-1_2_3_line_178 | NAYY 4x150 SE | 173 | 184 | 0.014704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
179 | LV_3394-1_2_3_line_179 | NAYY 4x150 SE | 174 | 175 | 0.0019956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
180 | LV_3394-1_2_3_line_180 | NAYY 4x150 SE | 175 | 176 | 0.024104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
181 | LV_3394-1_2_3_line_181 | NAYY 4x150 SE | 176 | 177 | 0.0058624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
182 | LV_3394-1_2_3_line_182 | NAYY 4x150 SE | 178 | 179 | 0.0037663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
183 | LV_3394-1_2_3_line_183 | NAYY 4x150 SE | 178 | 180 | 0.052158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
184 | LV_3394-1_2_3_line_184 | NAYY 4x150 SE | 179 | 181 | 0.0073594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
185 | LV_3394-1_2_3_line_185 | NAYY 4x150 SE | 183 | 194 | 0.0063874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
186 | LV_3394-1_2_3_line_186 | NAYY 4x150 SE | 184 | 185 | 0.037505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
187 | LV_3394-1_2_3_line_187 | NAYY 4x150 SE | 184 | 186 | 0.012561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
188 | LV_3394-1_2_3_line_188 | NAYY 4x150 SE | 185 | 187 | 0.022975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
189 | LV_3394-1_2_3_line_189 | NAYY 4x150 SE | 186 | 188 | 0.036049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
190 | LV_3394-1_2_3_line_190 | NAYY 4x150 SE | 187 | 189 | 0.00024713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
191 | LV_3394-1_2_3_line_191 | NAYY 4x150 SE | 188 | 190 | 0.015121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
192 | LV_3394-1_2_3_line_192 | NAYY 4x150 SE | 190 | 191 | 0.012503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
193 | LV_3394-1_2_3_line_193 | NAYY 4x150 SE | 192 | 193 | 0.014689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
194 | LV_3394-1_2_3_line_194 | NAYY 4x150 SE | 194 | 195 | 0.022095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3394-1_2_3_trafo_114 | 0.25 MVA 20/0.4 kV | 196 | 79 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39
0 | 2720756.9553 | 1243610.1835 | 2720743.5381 | 1243596.4299 | 2720728.3894 | 1243567.7533 | 2720677.0987 | 1243506.9593 | 2720672.9034 | 1243498.3184
1 | 2720764.5228 | 1243645.5312 | 2720760.9928 | 1243614.3223 | 2720756.9553 | 1243610.1835
2 | 2720668.9792 | 1243490.2358 | 2720672.9034 | 1243498.3184
3 | 2720764.5228 | 1243645.5312 | 2720779.5681 | 1243667.756 | 2720811.2493 | 1243702.7746 | 2720842.5211 | 1243735.2385 | 2720871.1859 | 1243755.006
4 | 2720728.4014 | 1243705.2682 | 2720737.3375 | 1243698.5778 | 2720762.124 | 1243647.4952 | 2720764.5228 | 1243645.5312
5 | 2720668.9792 | 1243490.2358 | 2720640.4542 | 1243469.8055 | 2720628.6656 | 1243458.3896 | 2720623.3093 | 1243446.304 | 2720616.2578 | 1243425.0096 | 2720610.8667 | 1243412.0337 | 2720600.5234 | 1243396.4549 | 2720596.9055 | 1243390.0682
6 | 2720894.5547 | 1243770.906 | 2720890.9695 | 1243765.0614 | 2720874.2427 | 1243757.114 | 2720871.1859 | 1243755.006
7 | 2720596.9055 | 1243390.0682 | 2720585.8975 | 1243370.6362 | 2720576.894 | 1243362.4131 | 2720568.0275 | 1243358.9745 | 2720568.0275 | 1243358.9745
8 | 2720894.5547 | 1243770.906 | 2720894.2773 | 1243784.5117
9 | 2720510.3555 | 1243392.1305 | 2720510.3555 | 1243392.1305 | 2720541.1241 | 1243364.7216 | 2720547.3737 | 1243360.4005 | 2720549.122 | 1243359.1906 | 2720557.3373 | 1243357.8452 | 2720568.0275 | 1243358.9745
10 | 2720488.42 | 1243409.6447 | 2720510.3555 | 1243392.1305
11 | 2721281.36 | 1244294.8046 | 2721248.6715 | 1244230.238 | 2721240.6746 | 1244213.9276 | 2721224.6006 | 1244185.2307 | 2721210.7806 | 1244170.8808 | 2721198.5919 | 1244155.8637 | 2721189.127 | 1244143.6824 | 2721186.2679 | 1244141.9391
12 | 2721281.36 | 1244294.8046 | 2721305.6686 | 1244341.8187 | 2721312.5982 | 1244347.0982 | 2721362.9678 | 1244394.9684 | 2721375.9709 | 1244412.994 | 2721383.766 | 1244440.2318 | 2721392.4593 | 1244458.3026 | 2721404.7398 | 1244473.2108 | 2721430.1432 | 1244490.3117 | 2721479.723 | 1244514.6471 | 2721484.8488 | 1244520.5126 | 2721486.1117 | 1244526.7548 | 2721483.0139 | 1244532.2181 | 2721460.2004 | 1244537.4109 | 2721405.7904 | 1244538.9096 | 2721393.7306 | 1244541.654 | 2721374.6455 | 1244578.5055
13 | 2721253.3429 | 1244301.949 | 2721265.8893 | 1244304.6299 | 2721273.5351 | 1244304.0969 | 2721280.072 | 1244301.2281 | 2721281.36 | 1244294.8046
14 | 2721374.6455 | 1244578.5055 | 2721320.2991 | 1244511.182 | 2721292.1041 | 1244491.6002 | 2721257.0511 | 1244478.0167 | 2721119.2437 | 1244433.4794
15 | 2721253.3429 | 1244301.949 | 2721172.9758 | 1244261.4566
16 | 2721084.9424 | 1244422.3938 | 2721119.2437 | 1244433.4794
17 | 2721163.6013 | 1244256.7334 | 2721172.9758 | 1244261.4566
18 | 2720484.2623 | 1243412.9644 | 2720488.42 | 1243409.6447
19 | 2720467.2193 | 1243426.5722 | 2720484.2623 | 1243412.9644
20 | 2720467.2193 | 1243426.5722 | 2720462.6558 | 1243419.7294 | 2720458.2239 | 1243412.7336 | 2720459.2234 | 1243400.3769 | 2720463.6114 | 1243391.3029 | 2720490.8258 | 1243365.7787 | 2720496.3793 | 1243357.0175 | 2720499.7746 | 1243345.4546 | 2720499.6118 | 1243339.6753
21 | 2720467.2193 | 1243426.5722 | 2720439.9463 | 1243452.7626 | 2720408.0496 | 1243480.6983
22 | 2720501.2369 | 1243270.155 | 2720498.6392 | 1243280.7889 | 2720498.6241 | 1243304.5972 | 2720499.6118 | 1243339.6753
23 | 2720266.3344 | 1243407.904 | 2720266.3344 | 1243407.904 | 2720286.3252 | 1243418.6514 | 2720315.5451 | 1243438.06 | 2720320.0526 | 1243448.4155 | 2720325.1969 | 1243467.6247 | 2720337.6211 | 1243480.5318 | 2720356.3638 | 1243490.9206 | 2720369.205 | 1243498.176 | 2720379.4549 | 1243500.497 | 2720388.8447 | 1243497.5183 | 2720408.0496 | 1243480.6983
24 | 2720388.5852 | 1243212.0535 | 2720415.5274 | 1243235.6976 | 2720444.2036 | 1243280.7837 | 2720447.8167 | 1243284.916 | 2720454.2482 | 1243287.2708 | 2720460.2702 | 1243285.2246 | 2720469.976 | 1243267.8294 | 2720514.3308 | 1243213.6628 | 2720521.634 | 1243209.9636 | 2720526.5958 | 1243214.3236 | 2720528.1328 | 1243218.6806 | 2720527.678 | 1243226.1776 | 2720522.0823 | 1243236.2613 | 2720509.1884 | 1243250.1776 | 2720502.8622 | 1243263.4713 | 2720501.2369 | 1243270.155
25 | 2720266.3344 | 1243407.904 | 2720252.4207 | 1243406.5431 | 2720202.3055 | 1243407.1726 | 2720197.6441 | 1243406.7543
26 | 2720388.5852 | 1243212.0535 | 2720382.836 | 1243206.9993 | 2720357.2126 | 1243183.927 | 2720333.6889 | 1243159.8411 | 2720324.2966 | 1243144.6602 | 2720322.7593 | 1243132.4856 | 2720327.8939 | 1243078.4226 | 2720328.6092 | 1243070.3748 | 2720323.4714 | 1243060.885 | 2720314.9268 | 1243055.3405 | 2720299.5125 | 1243047.4103 | 2720250.9037 | 1243046.68 | 2720230.926 | 1243043.7951 | 2720216.7119 | 1243038.1913 | 2720203.3578 | 1243028.5795 | 2720187.8374 | 1243001.9986 | 2720184.3403 | 1242974.5939 | 2720186.1746 | 1242946.7636 | 2720190.0385 | 1242923.6226 | 2720188.684 | 1242910.2508 | 2720183.3261 | 1242897.7986 | 2720176.8314 | 1242889.5825 | 2720164.0312 | 1242888.4334 | 2720155.9129 | 1242892.4279 | 2720124.5703 | 1242908.2176
27 | 2720388.5852 | 1243212.0535 | 2720392.8275 | 1243206.8018 | 2720413.573 | 1243206.845 | 2720418.8572 | 1243203.5273 | 2720416.5469 | 1243198.1537 | 2720413.845 | 1243195.816
28 | 2720179.6922 | 1243404.641 | 2720181.3335 | 1243405.2907 | 2720197.6441 | 1243406.7543
29 | 2720124.5703 | 1242908.2176 | 2720116.5949 | 1242914.8617 | 2720071.8687 | 1242930.3249 | 2720063.9591 | 1242930.3649 | 2720048.4763 | 1242926.4958
30 | 2720023.1051 | 1243260.2788 | 2720023.8259 | 1243304.5969 | 2720029.0913 | 1243318.6261 | 2720035.957 | 1243328.2953 | 2720049.3692 | 1243334.2716 | 2720109.5403 | 1243353.0492 | 2720121.2095 | 1243358.1008 | 2720126.6055 | 1243361.9354 | 2720135.59 | 1243369.6348 | 2720156.1792 | 1243392.2816 | 2720167.2106 | 1243399.7 | 2720179.6922 | 1243404.641
31 | 2720014.7457 | 1242911.4253 | 2720025.2488 | 1242919.0725 | 2720034.9057 | 1242923.1045 | 2720048.4763 | 1242926.4958
32 | 2720031.4312 | 1242867.2768 | 2720025.7534 | 1242859.0329 | 2720022.4716 | 1242851.2045 | 2720009.3424 | 1242812.885
33 | 2720031.4312 | 1242867.2768 | 2720025.5692 | 1242863.2771 | 2719999.8313 | 1242852.4477
34 | 2720009.3424 | 1242812.885 | 2720009.3424 | 1242812.885 | 2719997.837 | 1242746.9977 | 2719969.8401 | 1242716.9957 | 2719936.5798 | 1242690.7572 | 2719925.0767 | 1242679.66 | 2719921.6658 | 1242673.3414 | 2719918.8741 | 1242662.9542 | 2719921.5578 | 1242636.1131
35 | 2719995.6235 | 1242870.6368 | 2719995.0905 | 1242856.1882 | 2719999.8313 | 1242852.4477 | 2719999.8313 | 1242852.4477
36 | 2720004.6687 | 1242904.0883 | 2720014.7457 | 1242911.4253
37 | 2720239.5892 | 1242802.259 | 2720259.8223 | 1242805.6385 | 2720290.9759 | 1242818.2248 | 2720296.0552 | 1242821.887
38 | 2720239.5892 | 1242802.259 | 2720273.5894 | 1242797.5219 | 2720291.3609 | 1242800.4208
39 | 2720239.5892 | 1242802.259 | 2720240.2133 | 1242792.3635 | 2720251.5674 | 1242750.3698 | 2720277.9838 | 1242717.311 | 2720282.1136 | 1242703.4499 | 2720244.3423 | 1242639.0867 | 2720249.4072 | 1242632.8063 | 2720261.952 | 1242624.5759 | 2720272.1106 | 1242608.7353 | 2720374.1486 | 1242516.4943 | 2720405.2507 | 1242479.9763
40 | 2720239.5892 | 1242802.259 | 2720197.0258 | 1242792.8082
41 | 2720291.3609 | 1242800.4208 | 2720328.3049 | 1242806.4471
42 | 2720166.812 | 1242783.3396 | 2720187.7265 | 1242790.7433 | 2720197.0258 | 1242792.8082
43 | 2719921.5578 | 1242636.1131 | 2719922.5991 | 1242625.6986 | 2719922.807 | 1242616.9731
44 | 2720004.6687 | 1242904.0883 | 2719998.9479 | 1242896.0993 | 2719996.0084 | 1242881.0719 | 2719995.6235 | 1242870.6368
45 | 2720328.8673 | 1242806.5388 | 2720328.3049 | 1242806.4471
46 | 2720003.391 | 1242648.1615 | 2720079.9538 | 1242709.9169 | 2720099.7885 | 1242733.3599 | 2720115.3509 | 1242747.0974 | 2720146.6449 | 1242772.93 | 2720164.7017 | 1242782.5925 | 2720166.812 | 1242783.3396
47 | 2719922.807 | 1242616.9731 | 2719923.0538 | 1242606.6154
48 | 2719695.838 | 1243087.2499 | 2719695.0194 | 1243094.9705 | 2719694.8918 | 1243108.0343 | 2719694.8853 | 1243108.4883
49 | 2719694.746 | 1243118.2509 | 2719694.8853 | 1243108.4883
50 | 2719690.0215 | 1243111.8392 | 2719694.746 | 1243118.2509
51 | 2719703.3235 | 1243129.6779 | 2719694.746 | 1243118.2509
52 | 2719690.0215 | 1243111.8392 | 2719682.3311 | 1243101.4088 | 2719672.3196 | 1243093.2223 | 2719658.4749 | 1243088.0277 | 2719648.0286 | 1243084.9034 | 2719629.4091 | 1243079.9016 | 2719610.8222 | 1243078.1589 | 2719593.0307 | 1243077.0883 | 2719579.9163 | 1243079.9152 | 2719567.5416 | 1243085.426 | 2719544.7521 | 1243094.8747 | 2719534.6825 | 1243097.4406 | 2719525.2641 | 1243097.3286 | 2719511.9644 | 1243092.8459 | 2719486.9844 | 1243082.3119 | 2719476.7207 | 1243076.1224 | 2719467.0543 | 1243066.9312 | 2719460.9091 | 1243055.587 | 2719445.7556 | 1243025.6461 | 2719424.4199 | 1242988.4415 | 2719419.1482 | 1242978.7718
53 | 2719690.0215 | 1243111.8392 | 2719672.9435 | 1243125.6123
54 | 2719703.3235 | 1243129.6779 | 2719707.1883 | 1243134.8601
55 | 2719703.3235 | 1243129.6779 | 2719698.9509 | 1243146.6593 | 2719699.2636 | 1243155.6017
56 | 2719924.3684 | 1242589.0596 | 2719922.7211 | 1242596.488 | 2719923.0991 | 1242604.7136 | 2719923.0538 | 1242606.6154
57 | 2719924.3684 | 1242589.0596 | 2719924.1701 | 1242582.4167 | 2719930.741 | 1242578.3017 | 2719970.5162 | 1242566.974 | 2719980.5944 | 1242560.3056 | 2719983.8659 | 1242548.8511 | 2719983.9444 | 1242524.7883 | 2719980.1671 | 1242511.1673 | 2719970.1257 | 1242496.2075 | 2719953.1664 | 1242482.3199 | 2719947.3493 | 1242474.2067 | 2719945.4606 | 1242467.3962
58 | 2719924.3684 | 1242589.0596 | 2719928.4629 | 1242585.8841 | 2719933.7639 | 1242585.8579 | 2719942.1337 | 1242590.3752 | 2719944.2672 | 1242596.301 | 2719947.6833 | 1242603.1091 | 2719948.0003 | 1242603.501
59 | 2720069.7273 | 1242204.8362 | 2720074.3167 | 1242218.6849 | 2720070.6246 | 1242230.7313 | 2720053.8925 | 1242245.5606 | 2720046.8311 | 1242253.7134 | 2720041.346 | 1242264.3113 | 2720035.3126 | 1242311.7062 | 2720027.164 | 1242343.6901 | 2720024.0424 | 1242387.7079 | 2720017.2009 | 1242424.9781 | 2720009.3924 | 1242449.8853 | 2720003.7358 | 1242458.8784 | 2719995.1924 | 1242460.3179 | 2719960.0886 | 1242461.2201 | 2719951.6685 | 1242461.0498 | 2719945.4606 | 1242467.3962
60 | 2719945.8057 | 1242460.4308 | 2719945.4606 | 1242467.3962
61 | 2720003.391 | 1242648.1615 | 2719958.9035 | 1242616.9807 | 2719948.0003 | 1242603.501
62 | 2720003.391 | 1242648.1615 | 2720007.8994 | 1242643.9603 | 2720019.2764 | 1242642.9784 | 2720026.3495 | 1242634.2253 | 2720036.8455 | 1242596.8289 | 2720040.7497 | 1242584.3753 | 2720067.9236 | 1242564.2973 | 2720100.6831 | 1242549.1921 | 2720123.503 | 1242543.994 | 2720144.5341 | 1242546.8443 | 2720159.6275 | 1242542.702 | 2720188.7202 | 1242528.3348 | 2720199.9632 | 1242523.9033 | 2720209.0214 | 1242517.2145 | 2720211.1782 | 1242510.7862 | 2720209.0467 | 1242505.8946 | 2720203.4073 | 1242503.9565 | 2720197.9801 | 1242501.6224 | 2720192.251 | 1242494.0334 | 2720191.8028 | 1242476.2318 | 2720198.1005 | 1242465.8397 | 2720197.0393 | 1242458.134 | 2720189.4279 | 1242453.1313 | 2720178.3127 | 1242441.1741
63 | 2719945.8057 | 1242460.4308 | 2719960.297 | 1242450.9158 | 2719977.4206 | 1242436.5056 | 2719986.3809 | 1242424.5546 | 2719987.2671 | 1242411.028 | 2719981.0494 | 1242357.3134 | 2719987.0865 | 1242319.4263
64 | 2719655.0457 | 1242560.6915 | 2719647.2095 | 1242571.2951
65 | 2719695.3055 | 1242508.8355 | 2719687.5409 | 1242508.4119 | 2719680.7854 | 1242510.0659 | 2719674.4409 | 1242516.4544 | 2719666.2876 | 1242539.7871 | 2719655.7683 | 1242559.7137 | 2719655.0457 | 1242560.6915
66 | 2719647.2095 | 1242571.2951 | 2719647.2095 | 1242571.2951 | 2719638.2599 | 1242578.2649 | 2719628.2368 | 1242582.5998 | 2719620.1974 | 1242581.181 | 2719614.2846 | 1242578.5485 | 2719605.8509 | 1242571.5617 | 2719599.3457 | 1242559.6874 | 2719596.5164 | 1242553.3807 | 2719593.7527 | 1242529.9501 | 2719588.0186 | 1242514.6997 | 2719579.8939 | 1242502.1368 | 2719575.7691 | 1242494.8254 | 2719575.1367 | 1242487.5622 | 2719577.1354 | 1242474.6918 | 2719583.1056 | 1242443.364 | 2719586.3721 | 1242422.7461 | 2719584.7774 | 1242413.7065 | 2719579.3234 | 1242396.9383 | 2719572.2907 | 1242379.7046 | 2719564.0665 | 1242333.8121 | 2719564.8668 | 1242327.1227 | 2719568.1412 | 1242322.2402 | 2719573.0871 | 1242321.0833 | 2719577.6267 | 1242323.955 | 2719581.5577 | 1242330.3839 | 2719589.8376 | 1242347.2647 | 2719601.431 | 1242361.4434 | 2719609.7526 | 1242369.5066 | 2719613.9608 | 1242371.5598 | 2719619.5256 | 1242371.9612 | 2719624.0237 | 1242370.1392 | 2719626.9392 | 1242367.3068 | 2719629.5609 | 1242363.6677 | 2719631.0598 | 1242359.4611 | 2719631.0232 | 1242354.9011 | 2719629.3501 | 1242348.2507 | 2719619.4788 | 1242330.0478 | 2719609.1092 | 1242309.5552 | 2719608.6137 | 1242308.4707
67 | 2719695.3055 | 1242508.8355 | 2719701.5931 | 1242512.0094 | 2719706.6974 | 1242518.3621 | 2719710.7557 | 1242534.2015 | 2719719.8403 | 1242569.9921 | 2719723.9386 | 1242593.3557
68 | 2719566.4396 | 1242775.6252 | 2719570.0483 | 1242768.0249 | 2719569.0125 | 1242751.1456 | 2719569.383 | 1242735.7737 | 2719575.1349 | 1242721.6335 | 2719582.1649 | 1242703.727 | 2719582.835 | 1242689.9958 | 2719571.8007 | 1242649.2509 | 2719566.5668 | 1242634.7001 | 2719566.4404 | 1242631.2168 | 2719566.9469 | 1242627.8465 | 2719577.6801 | 1242613.0394 | 2719583.1555 | 1242611.4929 | 2719587.6961 | 1242612.4296 | 2719591.6468 | 1242614.8668 | 2719603.9172 | 1242628.4475 | 2719624.0301 | 1242649.0699 | 2719630.2728 | 1242661.5839 | 2719633.6316 | 1242670.8704 | 2719641.1556 | 1242679.4625 | 2719649.4466 | 1242683.7666 | 2719659.8866 | 1242684.6222 | 2719671.3993 | 1242682.1523 | 2719681.6548 | 1242674.9087 | 2719711.2154 | 1242644.7689 | 2719718.5009 | 1242632.9616 | 2719722.9318 | 1242619.1062 | 2719724.9124 | 1242598.9072 | 2719723.9386 | 1242593.3557
69 | 2719566.4396 | 1242775.6252 | 2719576.1436 | 1242802.4651 | 2719575.5147 | 1242814.5291 | 2719571.5095 | 1242839.1688 | 2719570.3109 | 1242851.3658
70 | 2719566.4396 | 1242775.6252 | 2719558.0344 | 1242761.989 | 2719544.8401 | 1242719.9884 | 2719529.8384 | 1242674.9935 | 2719499.835 | 1242641.9953 | 2719492.3733 | 1242624.8592
71 | 2719570.3109 | 1242851.3658 | 2719569.4752 | 1242859.8115 | 2719567.6246 | 1242868.5379
72 | 2719570.3109 | 1242851.3658 | 2719550.5722 | 1242837.0411
73 | 2719567.6246 | 1242868.5379 | 2719564.1611 | 1242884.8696 | 2719551.9799 | 1242909.2666 | 2719538.5617 | 1242929.0238 | 2719527.1899 | 1242940.2818 | 2719515.1541 | 1242948.4795 | 2719502.3152 | 1242954.8818 | 2719485.7435 | 1242959.2962 | 2719466.7003 | 1242962.9676
74 | 2719550.5722 | 1242837.0411 | 2719537.1036 | 1242827.2667
75 | 2719419.1482 | 1242978.7718 | 2719423.6772 | 1242975.0154 | 2719431.4888 | 1242970.8247 | 2719445.2186 | 1242967.1091 | 2719466.7003 | 1242962.9676
76 | 2719390.4895 | 1242738.5966 | 2719411.1913 | 1242764.1565 | 2719443.1356 | 1242774.7414 | 2719451.3141 | 1242783.8802 | 2719509.9326 | 1242811.0273 | 2719534.4072 | 1242825.3098 | 2719537.1036 | 1242827.2667
77 | 2719419.1482 | 1242978.7718 | 2719412.8353 | 1242974.9972 | 2719410.9522 | 1242973.6239
78 | 2719390.4895 | 1242738.5966 | 2719385.6911 | 1242737.6993 | 2719380.6332 | 1242733.9167 | 2719379.0887 | 1242728.7591 | 2719381.6273 | 1242714.2093 | 2719381.698 | 1242705.8149 | 2719371.7753 | 1242685.6542 | 2719349.8339 | 1242629.9891 | 2719323.1021 | 1242551.9649 | 2719317.6889 | 1242539.9016 | 2719307.0083 | 1242531.8247 | 2719304.7549 | 1242530.354
79 | 2719304.7549 | 1242530.354 | 2719293.91 | 1242523.2765 | 2719287.8057 | 1242519.7457
80 | 2719272.6975 | 1242511.0067 | 2719282.1764 | 1242499.1319
81 | 2719272.6975 | 1242511.0067 | 2719287.8057 | 1242519.7457
82 | 2720023.1051 | 1243260.2788 | 2720008.6818 | 1243269.884 | 2719982.5733 | 1243297.2565
83 | 2720023.1051 | 1243260.2788 | 2720020.6208 | 1243222.7752 | 2720010.0324 | 1243201.2877 | 2719996.7956 | 1243183.6387 | 2719988.0903 | 1243176.6903 | 2719967.1077 | 1243170.8056 | 2719930.4339 | 1243162.0681 | 2719915.631 | 1243158.7917
84 | 2719912.0648 | 1243158.0023 | 2719915.631 | 1243158.7917
85 | 2719879.8828 | 1243160.9791 | 2719889.3142 | 1243156.6994 | 2719899.9121 | 1243155.3124 | 2719912.0648 | 1243158.0023
86 | 2719879.8828 | 1243160.9791 | 2719871.9987 | 1243168.4221
87 | 2719871.9987 | 1243168.4221 | 2719864.6683 | 1243175.3424
88 | 2719594.503 | 1243307.709 | 2719596.6375 | 1243308.2418
89 | 2719594.503 | 1243307.709 | 2719607.0198 | 1243284.2641 | 2719638.332 | 1243297.1615 | 2719665.3499 | 1243308.6244
90 | 2719694.0196 | 1243314.1542 | 2719678.916 | 1243314.7945 | 2719669.3741 | 1243310.3317 | 2719665.3499 | 1243308.6244
91 | 2719620.2887 | 1243407.9118 | 2719630.6047 | 1243391.2393 | 2719656.466 | 1243365.8953 | 2719667.6812 | 1243353.3777 | 2719680.5995 | 1243332.521 | 2719688.3825 | 1243321.8691
92 | 2719641.3099 | 1243547.1066 | 2719634.1524 | 1243547.3848 | 2719614.6602 | 1243543.3662 | 2719607.0368 | 1243541.2553 | 2719602.3967 | 1243535.1678 | 2719599.8626 | 1243504.1354 | 2719598.3686 | 1243473.6356 | 2719601.6056 | 1243458.9553 | 2719610.5447 | 1243448.6937 | 2719615.3537 | 1243438.1708 | 2719620.2887 | 1243407.9118
93 | 2719694.0196 | 1243314.1542 | 2719688.3825 | 1243321.8691
94 | 2719651.6634 | 1243577.6407 | 2719645.7903 | 1243562.9768 | 2719641.3099 | 1243547.1066
95 | 2719676.1073 | 1243271.1573 | 2719677.6842 | 1243279.1846 | 2719688.097 | 1243295.5638 | 2719693.9029 | 1243306.0785 | 2719694.0196 | 1243314.1542
96 | 2719651.6634 | 1243577.6407 | 2719626.3849 | 1243610.4916 | 2719621.2325 | 1243614.4355 | 2719615.169 | 1243613.7015 | 2719606.0108 | 1243605.2321
97 | 2719651.6634 | 1243577.6407 | 2719658.2858 | 1243586.2703 | 2719660.3501 | 1243587.7465 | 2719667.1319 | 1243592.5984 | 2719676.344 | 1243593.1513
98 | 2719676.1073 | 1243271.1573 | 2719682.2873 | 1243276.9566
99 | 2719673.937 | 1243264.0632 | 2719676.1073 | 1243271.1573
100 | 2719676.344 | 1243593.1513 | 2719681.1313 | 1243593.437 | 2719691.2595 | 1243589.0599 | 2719707.5788 | 1243570.4848 | 2719727.2809 | 1243555.114 | 2719745.4808 | 1243542.6264 | 2719765.3134 | 1243532.4071 | 2719790.7385 | 1243523.4129 | 2719814.3994 | 1243518.2975 | 2719833.692 | 1243507.5003 | 2719861.0209 | 1243487.3689 | 2719875.1864 | 1243480.3826 | 2719887.576 | 1243477.8419 | 2719903.7186 | 1243483.7508 | 2719919.6758 | 1243494.7131
101 | 2719676.344 | 1243593.1513 | 2719675.7128 | 1243602.324 | 2719666.085 | 1243621.9906 | 2719657.427 | 1243629.5667 | 2719633.6196 | 1243640.4735 | 2719617.2825 | 1243650.9639 | 2719601.413 | 1243667.8803 | 2719596.5551 | 1243675.9669 | 2719596.1554 | 1243688.6582 | 2719597.0239 | 1243696.5712 | 2719599.8837 | 1243699.8426 | 2719606.416 | 1243703.1882 | 2719611.8755 | 1243701.2522 | 2719615.6243 | 1243696.8019 | 2719630.6064 | 1243673.2844 | 2719635.3434 | 1243671.1893 | 2719640.8876 | 1243672.1797 | 2719643.0483 | 1243674.1248 | 2719644.1106 | 1243679.5508 | 2719642.562 | 1243683.6118 | 2719631.1008 | 1243699.7385 | 2719629.2938 | 1243709.488 | 2719627.3037 | 1243716.1864
102 | 2719757.9874 | 1243316.0651 | 2719758.4776 | 1243309.0283 | 2719754.7295 | 1243298.455 | 2719752.1439 | 1243293.4727
103 | 2719739.0696 | 1243263.5304 | 2719744.8033 | 1243279.3277 | 2719752.1439 | 1243293.4727
104 | 2719713.8109 | 1243305.6353 | 2719692.7354 | 1243286.7611 | 2719682.2873 | 1243276.9566
105 | 2719696.0637 | 1243238.3659 | 2719673.937 | 1243264.0632
106 | 2719673.937 | 1243264.0632 | 2719665.3512 | 1243262.0439 | 2719651.4608 | 1243252.8839
107 | 2719919.6758 | 1243494.7131 | 2719929.7198 | 1243501.6133 | 2719992.1512 | 1243548.7257 | 2720032.9147 | 1243593.5763 | 2720066.0447 | 1243632.7525
108 | 2719613.4297 | 1243733.6903 | 2719616.3134 | 1243728.2196 | 2719623.8827 | 1243723.257 | 2719626.6172 | 1243718.497 | 2719627.3037 | 1243716.1864
109 | 2719739.0696 | 1243263.5304 | 2719738.7848 | 1243262.7456
110 | 2719613.4297 | 1243733.6903 | 2719612.5505 | 1243735.3583
111 | 2719497.0671 | 1243849.562 | 2719504.4354 | 1243847.8089 | 2719523.8692 | 1243835.9239 | 2719528.1049 | 1243829.4371 | 2719529.5728 | 1243821.8715 | 2719527.0622 | 1243815.5379 | 2719523.4959 | 1243810.9401 | 2719523.1549 | 1243806.1069 | 2719525.1179 | 1243803.233 | 2719528.405 | 1243799.9298 | 2719536.3846 | 1243796.7323 | 2719545.959 | 1243794.301 | 2719555.4747 | 1243794.782 | 2719563.1884 | 1243797.2729 | 2719570.0019 | 1243800.9132 | 2719572.475 | 1243801.9861 | 2719579.2256 | 1243801.2549 | 2719584.5739 | 1243797.7042 | 2719591.2474 | 1243779.4346 | 2719592.736 | 1243770.8464 | 2719594.3258 | 1243764.74 | 2719597.3108 | 1243762.1759 | 2719599.8755 | 1243760.5818 | 2719603.244 | 1243758.4924 | 2719608.0832 | 1243743.8333 | 2719612.5505 | 1243735.3583
112 | 2720180.5265 | 1243760.2473 | 2720153.9162 | 1243731.4956 | 2720095.2884 | 1243667.3331 | 2720066.0447 | 1243632.7525
113 | 2720180.5265 | 1243760.2473 | 2720190.9867 | 1243771.5478
114 | 2720180.5265 | 1243760.2473 | 2720170.2997 | 1243767.246 | 2720162.7713 | 1243768.3055 | 2720123.3723 | 1243761.4354 | 2720104.6114 | 1243756.8184 | 2720079.7067 | 1243744.9934 | 2720059.2523 | 1243733.6589 | 2720027.6556 | 1243721.8988 | 2720006.7422 | 1243714.383
115 | 2720190.9867 | 1243771.5478 | 2720194.7304 | 1243775.5922 | 2720225.4907 | 1243825.2123 | 2720255.6193 | 1243860.4855 | 2720288.7916 | 1243888.4256 | 2720299.2402 | 1243896.7034
116 | 2719916.6788 | 1243706.7979 | 2719926.8787 | 1243701.8667 | 2719949.1755 | 1243702.1176 | 2719973.166 | 1243709.075 | 2719997.259 | 1243710.9749 | 2720006.7422 | 1243714.383
117 | 2719676.7205 | 1243899.5689 | 2719681.7785 | 1243889.8761
118 | 2719916.6788 | 1243706.7979 | 2719865.0928 | 1243688.6961 | 2719840.7508 | 1243689.0158 | 2719805.6216 | 1243701.6391 | 2719793.6589 | 1243711.5058 | 2719789.347 | 1243724.3627 | 2719780.2749 | 1243741.9609 | 2719769.7411 | 1243751.4561 | 2719753.4753 | 1243753.5518 | 2719745.1628 | 1243753.3839 | 2719738.3933 | 1243757.295 | 2719732.453 | 1243770.3081 | 2719724.59 | 1243798.0503 | 2719687.6828 | 1243878.5614 | 2719681.7785 | 1243889.8761
119 | 2719916.6788 | 1243706.7979 | 2719885.5145 | 1243721.8585 | 2719870.6493 | 1243734.691 | 2719854.8276 | 1243755.1996 | 2719842.3832 | 1243778.8012 | 2719836.4259 | 1243812.8425 | 2719834.9684 | 1243824.734 | 2719832.2244 | 1243836.7279
120 | 2719832.2244 | 1243836.7279 | 2719831.8914 | 1243838.1835
121 | 2719840.8589 | 1243924.5137 | 2719835.6335 | 1243892.0589 | 2719829.3501 | 1243871.9264 | 2719828.293 | 1243853.9123 | 2719831.8914 | 1243838.1835
122 | 2719840.8589 | 1243924.5137 | 2719842.7901 | 1243929.201 | 2719848.9058 | 1243927.7122 | 2719856.3362 | 1243921.3904 | 2719869.7442 | 1243920.0379 | 2719933.3938 | 1243920.9249 | 2719945.1776 | 1243925.9984
123 | 2719830.0994 | 1244095.9055 | 2719837.9139 | 1244070.1976 | 2719840.1104 | 1244041.9406 | 2719844.4555 | 1243967.233 | 2719840.8589 | 1243924.5137
124 | 2720299.2402 | 1243896.7034 | 2720324.0082 | 1243916.3256
125 | 2720530.6601 | 1244184.2919 | 2720305.0137 | 1244361.274
126 | 2720305.0137 | 1244361.274 | 2719756.9855 | 1244835.7759
127 | 2720530.6601 | 1244184.2919 | 2720534.7836 | 1244181.1397 | 2720563.4714 | 1244185.971 | 2720566.7699 | 1244183.6139 | 2720568.4649 | 1244179.8118 | 2720554.8899 | 1244149.6219 | 2720548.3425 | 1244142.6052 | 2720546.182 | 1244140.3628
128 | 2720596.6482 | 1244349.1593 | 2720620.7219 | 1244351.8732 | 2720625.8413 | 1244349.5531 | 2720626.1233 | 1244345.7223 | 2720619.9808 | 1244338.5136 | 2720603.8639 | 1244303.6235 | 2720595.4187 | 1244290.3185 | 2720562.8357 | 1244237.301 | 2720542.4353 | 1244203.7362 | 2720530.7531 | 1244189.7539 | 2720530.6601 | 1244184.2919
129 | 2720546.182 | 1244140.3628 | 2720533.4473 | 1244127.1453 | 2720531.6622 | 1244124.7867
130 | 2720327.8885 | 1243919.3996 | 2720324.0082 | 1243916.3256
131 | 2720327.8885 | 1243919.3996 | 2720338.9378 | 1243928.1533 | 2720357.6059 | 1243948.1042 | 2720358.4019 | 1243949.1039
132 | 2720358.4019 | 1243949.1039 | 2720370.7275 | 1243964.5841 | 2720382.8265 | 1243993.0536
133 | 2720410.8214 | 1244033.9332 | 2720394.3212 | 1244018.1852 | 2720386.7878 | 1244002.3748 | 2720382.8265 | 1243993.0536
134 | 2720410.8214 | 1244033.9332 | 2720410.8214 | 1244033.9332 | 2720433.7655 | 1244044.3075 | 2720470.3272 | 1244063.0988 | 2720483.3725 | 1244071.8799
135 | 2720508.7407 | 1244088.956 | 2720483.3725 | 1244071.8799
136 | 2720508.7407 | 1244088.956 | 2720557.7126 | 1244115.2728 | 2720588.1861 | 1244129.7041 | 2720617.1129 | 1244151.8424
137 | 2720508.7407 | 1244088.956 | 2720507.188 | 1244092.4496 | 2720521.9035 | 1244111.8927
138 | 2720619.228 | 1244153.4696 | 2720618.6376 | 1244153.0092 | 2720617.1129 | 1244151.8424
139 | 2720531.6622 | 1244124.7867 | 2720521.9035 | 1244111.8927
140 | 2720619.228 | 1244153.4696 | 2720634.3402 | 1244165.2538
141 | 2720634.3402 | 1244165.2538 | 2720649.9388 | 1244177.4173
142 | 2720665.4471 | 1244189.5104 | 2720649.9388 | 1244177.4173
143 | 2720755.3319 | 1244270.7594 | 2720754.2331 | 1244269.4313 | 2720751.363 | 1244266.0934
144 | 2720755.3319 | 1244270.7594 | 2720771.1699 | 1244289.9026
145 | 2720751.363 | 1244266.0934 | 2720741.359 | 1244254.4589
146 | 2720863.1966 | 1244360.0703 | 2720815.079 | 1244334.6467 | 2720793.0821 | 1244317.1954 | 2720778.7046 | 1244299.0097 | 2720771.1699 | 1244289.9026
147 | 2720728.0116 | 1244240.6433 | 2720733.9704 | 1244245.8659 | 2720741.359 | 1244254.4589
148 | 2720863.1966 | 1244360.0703 | 2720902.3543 | 1244380.7632 | 2720932.0076 | 1244384.1593 | 2720966.7196 | 1244387.1027 | 2720998.5368 | 1244394.4688 | 2721051.5478 | 1244411.6012
149 | 2720728.0116 | 1244240.6433 | 2720717.8421 | 1244231.7301
150 | 2721051.5478 | 1244411.6012 | 2721084.9424 | 1244422.3938
151 | 2720717.8421 | 1244231.7301 | 2720703.7434 | 1244219.3732 | 2720692.5102 | 1244210.6137
152 | 2720692.5102 | 1244210.6137 | 2720677.3641 | 1244198.8031
153 | 2720666.7488 | 1244190.5255 | 2720677.3641 | 1244198.8031
154 | 2720665.4471 | 1244189.5104 | 2720666.7488 | 1244190.5255
155 | 2719631.2169 | 1243218.8866 | 2719645.4795 | 1243222.0879 | 2719656.8957 | 1243221.3508 | 2719677.4056 | 1243232.3068 | 2719696.0637 | 1243238.3659
156 | 2719696.0637 | 1243238.3659 | 2719699.7667 | 1243236.0223
157 | 2719699.7667 | 1243236.0223 | 2719709.6503 | 1243229.7671
158 | 2719734.7471 | 1243204.863 | 2719722.9738 | 1243220.6608 | 2719717.3311 | 1243224.906 | 2719709.6503 | 1243229.7671
159 | 2719734.7471 | 1243204.863 | 2719742.734 | 1243198.9077
160 | 2719734.7471 | 1243204.863 | 2719724.9203 | 1243195.6139
161 | 2719734.7471 | 1243204.863 | 2719734.9651 | 1243223.717
162 | 2719735.587 | 1243248.121 | 2719735.2261 | 1243246.2848 | 2719734.9651 | 1243223.717
163 | 2719735.587 | 1243248.121 | 2719738.0782 | 1243260.7988 | 2719738.7848 | 1243262.7456
164 | 2719750.7613 | 1243194.7111 | 2719745.8699 | 1243196.5695 | 2719742.734 | 1243198.9077
165 | 2719711.4911 | 1243184.8064 | 2719717.6746 | 1243188.7941 | 2719724.9203 | 1243195.6139
166 | 2719750.7613 | 1243194.7111 | 2719743.7202 | 1243183.9601 | 2719739.6082 | 1243178.4198
167 | 2719750.7613 | 1243194.7111 | 2719757.76 | 1243194.8302 | 2719762.9765 | 1243195.0239
168 | 2719706.258 | 1243181.4316 | 2719711.4911 | 1243184.8064
169 | 2719770.4277 | 1243195.3006 | 2719762.9765 | 1243195.0239
170 | 2719697.6129 | 1243175.8565 | 2719706.258 | 1243181.4316
171 | 2719779.571 | 1243195.5048 | 2719775.4914 | 1243195.4886 | 2719770.4277 | 1243195.3006
172 | 2719697.6129 | 1243175.8565 | 2719699.4638 | 1243161.3262 | 2719699.2636 | 1243155.6017
173 | 2719697.6129 | 1243175.8565 | 2719684.1655 | 1243175.4173
174 | 2719707.1883 | 1243134.8601 | 2719721.3815 | 1243153.8622 | 2719722.2434 | 1243155.0234
175 | 2719707.1883 | 1243134.8601 | 2719713.5014 | 1243117.2618 | 2719716.617 | 1243113.4882 | 2719721.6068 | 1243112.3768 | 2719722.624 | 1243112.7222
176 | 2719795.7225 | 1243195.5689 | 2719779.571 | 1243195.5048
177 | 2719722.624 | 1243112.7222 | 2719750.7124 | 1243122.2612 | 2719763.2804 | 1243127.8957
178 | 2719810.4261 | 1243195.6273 | 2719795.7225 | 1243195.5689
179 | 2719648.0642 | 1243145.6769 | 2719649.6176 | 1243144.4241
180 | 2719649.6176 | 1243144.4241 | 2719668.3802 | 1243129.2925
181 | 2719672.9435 | 1243125.6123 | 2719668.3802 | 1243129.2925
182 | 2719633.945 | 1243180.3541 | 2719633.945 | 1243180.3541 | 2719631.3785 | 1243183.1106
183 | 2719633.945 | 1243180.3541 | 2719643.2577 | 1243174.0811 | 2719684.1655 | 1243175.4173
184 | 2719626.3637 | 1243188.4969 | 2719631.3785 | 1243183.1106
185 | 2719405.7915 | 1242969.8603 | 2719410.9522 | 1242973.6239
186 | 2719810.4261 | 1243195.6273 | 2719838.3051 | 1243193.9778 | 2719847.2904 | 1243190.8233 | 2719847.3314 | 1243190.7876
187 | 2719810.4261 | 1243195.6273 | 2719808.6241 | 1243205.1099 | 2719807.0713 | 1243207.5696
188 | 2719847.3314 | 1243190.7876 | 2719860.1741 | 1243179.5853 | 2719864.4886 | 1243175.5121
189 | 2719807.0713 | 1243207.5696 | 2719793.8934 | 1243228.443 | 2719791.3032 | 1243239.5078
190 | 2719864.4886 | 1243175.5121 | 2719864.6683 | 1243175.3424
191 | 2719789.5172 | 1243254.3196 | 2719788.9369 | 1243249.616 | 2719791.3032 | 1243239.5078
192 | 2719791.0483 | 1243266.7284 | 2719789.5172 | 1243254.3196
193 | 2719763.2804 | 1243127.8957 | 2719768.1932 | 1243130.0982 | 2719776.0769 | 1243135.0404
194 | 2719405.7915 | 1242969.8603 | 2719387.9398 | 1242956.8411

## bus_geodata
| x | y | coords
0 | 2720756.9553 | 1243610.1835
1 | 2720672.9034 | 1243498.3184
2 | 2720764.5228 | 1243645.5312
3 | 2720668.9792 | 1243490.2358
4 | 2720871.1859 | 1243755.006
5 | 2720728.4014 | 1243705.2682
6 | 2720596.9055 | 1243390.0682
7 | 2720894.5547 | 1243770.906
8 | 2720568.0275 | 1243358.9745
9 | 2720894.2773 | 1243784.5117
10 | 2720510.3555 | 1243392.1305
11 | 2721186.2679 | 1244141.9391
12 | 2721281.36 | 1244294.8046
13 | 2721374.6455 | 1244578.5055
14 | 2721253.3429 | 1244301.949
15 | 2721119.2437 | 1244433.4794
16 | 2721172.9758 | 1244261.4566
17 | 2720488.42 | 1243409.6447
18 | 2720484.2623 | 1243412.9644
19 | 2720467.2193 | 1243426.5722
20 | 2720499.6118 | 1243339.6753
21 | 2720408.0496 | 1243480.6983
22 | 2720501.2369 | 1243270.155
23 | 2720266.3344 | 1243407.904
24 | 2720388.5852 | 1243212.0535
25 | 2720197.6441 | 1243406.7543
26 | 2720124.5703 | 1242908.2176
27 | 2720413.845 | 1243195.816
28 | 2720179.6922 | 1243404.641
29 | 2720048.4763 | 1242926.4958
30 | 2720031.4312 | 1242867.2768
31 | 2720009.3424 | 1242812.885
32 | 2719999.8313 | 1242852.4477
33 | 2720014.7457 | 1242911.4253
34 | 2720239.5892 | 1242802.259
35 | 2720296.0552 | 1242821.887
36 | 2720291.3609 | 1242800.4208
37 | 2720405.2507 | 1242479.9763
38 | 2720197.0258 | 1242792.8082
39 | 2719921.5578 | 1242636.1131
40 | 2719995.6235 | 1242870.6368
41 | 2720004.6687 | 1242904.0883
42 | 2720328.3049 | 1242806.4471
43 | 2720166.812 | 1242783.3396
44 | 2719922.807 | 1242616.9731
45 | 2719695.838 | 1243087.2499
46 | 2719694.8853 | 1243108.4883
47 | 2719694.746 | 1243118.2509
48 | 2719690.0215 | 1243111.8392
49 | 2719703.3235 | 1243129.6779
50 | 2719923.0538 | 1242606.6154
51 | 2719924.3684 | 1242589.0596
52 | 2719945.4606 | 1242467.3962
53 | 2719948.0003 | 1242603.501
54 | 2720328.8673 | 1242806.5388
55 | 2720003.391 | 1242648.1615
56 | 2720178.3127 | 1242441.1741
57 | 2720069.7273 | 1242204.8362
58 | 2719945.8057 | 1242460.4308
59 | 2719987.0865 | 1242319.4263
60 | 2719655.0457 | 1242560.6915
61 | 2719647.2095 | 1242571.2951
62 | 2719695.3055 | 1242508.8355
63 | 2719608.6137 | 1242308.4707
64 | 2719723.9386 | 1242593.3557
65 | 2719566.4396 | 1242775.6252
66 | 2719570.3109 | 1242851.3658
67 | 2719492.3733 | 1242624.8592
68 | 2719567.6246 | 1242868.5379
69 | 2719550.5722 | 1242837.0411
70 | 2719466.7003 | 1242962.9676
71 | 2719537.1036 | 1242827.2667
72 | 2719419.1482 | 1242978.7718
73 | 2719390.4895 | 1242738.5966
74 | 2719304.7549 | 1242530.354
75 | 2719272.6975 | 1242511.0067
76 | 2719282.1764 | 1242499.1319
77 | 2719287.8057 | 1242519.7457
78 | 2720023.1051 | 1243260.2788
79 | 2719982.5733 | 1243297.2565
80 | 2719915.631 | 1243158.7917
81 | 2719912.0648 | 1243158.0023
82 | 2719879.8828 | 1243160.9791
83 | 2719871.9987 | 1243168.4221
84 | 2719596.6375 | 1243308.2418
85 | 2719594.503 | 1243307.709
86 | 2719665.3499 | 1243308.6244
87 | 2719620.2887 | 1243407.9118
88 | 2719688.3825 | 1243321.8691
89 | 2719641.3099 | 1243547.1066
90 | 2719694.0196 | 1243314.1542
91 | 2719651.6634 | 1243577.6407
92 | 2719676.1073 | 1243271.1573
93 | 2719606.0108 | 1243605.2321
94 | 2719676.344 | 1243593.1513
95 | 2719757.9874 | 1243316.0651
96 | 2719752.1439 | 1243293.4727
97 | 2719682.2873 | 1243276.9566
98 | 2719673.937 | 1243264.0632
99 | 2719919.6758 | 1243494.7131
100 | 2719627.3037 | 1243716.1864
101 | 2719739.0696 | 1243263.5304
102 | 2719613.4297 | 1243733.6903
103 | 2719612.5505 | 1243735.3583
104 | 2719497.0671 | 1243849.562
105 | 2720066.0447 | 1243632.7525
106 | 2720180.5265 | 1243760.2473
107 | 2720190.9867 | 1243771.5478
108 | 2720006.7422 | 1243714.383
109 | 2719681.7785 | 1243889.8761
110 | 2719676.7205 | 1243899.5689
111 | 2719916.6788 | 1243706.7979
112 | 2719832.2244 | 1243836.7279
113 | 2719831.8914 | 1243838.1835
114 | 2719840.8589 | 1243924.5137
115 | 2719945.1776 | 1243925.9984
116 | 2719830.0994 | 1244095.9055
117 | 2720299.2402 | 1243896.7034
118 | 2720305.0137 | 1244361.274
119 | 2720530.6601 | 1244184.2919
120 | 2719756.9855 | 1244835.7759
121 | 2720546.182 | 1244140.3628
122 | 2720596.6482 | 1244349.1593
123 | 2720324.0082 | 1243916.3256
124 | 2720327.8885 | 1243919.3996
125 | 2720358.4019 | 1243949.1039
126 | 2720382.8265 | 1243993.0536
127 | 2720410.8214 | 1244033.9332
128 | 2720483.3725 | 1244071.8799
129 | 2720508.7407 | 1244088.956
130 | 2720617.1129 | 1244151.8424
131 | 2720521.9035 | 1244111.8927
132 | 2720619.228 | 1244153.4696
133 | 2720531.6622 | 1244124.7867
134 | 2720634.3402 | 1244165.2538
135 | 2720649.9388 | 1244177.4173
136 | 2720755.3319 | 1244270.7594
137 | 2720751.363 | 1244266.0934
138 | 2720771.1699 | 1244289.9026
139 | 2720741.359 | 1244254.4589
140 | 2720863.1966 | 1244360.0703
141 | 2720728.0116 | 1244240.6433
142 | 2721051.5478 | 1244411.6012
143 | 2720717.8421 | 1244231.7301
144 | 2721084.9424 | 1244422.3938
145 | 2720692.5102 | 1244210.6137
146 | 2720677.3641 | 1244198.8031
147 | 2720666.7488 | 1244190.5255
148 | 2720665.4471 | 1244189.5104
149 | 2721163.6013 | 1244256.7334
150 | 2719651.4608 | 1243252.8839
151 | 2719696.0637 | 1243238.3659
152 | 2719631.2169 | 1243218.8866
153 | 2719699.7667 | 1243236.0223
154 | 2719713.8109 | 1243305.6353
155 | 2719709.6503 | 1243229.7671
156 | 2719734.7471 | 1243204.863
157 | 2719735.587 | 1243248.121
158 | 2719734.9651 | 1243223.717
159 | 2719738.7848 | 1243262.7456
160 | 2719742.734 | 1243198.9077
161 | 2719724.9203 | 1243195.6139
162 | 2719750.7613 | 1243194.7111
163 | 2719711.4911 | 1243184.8064
164 | 2719739.6082 | 1243178.4198
165 | 2719762.9765 | 1243195.0239
166 | 2719706.258 | 1243181.4316
167 | 2719770.4277 | 1243195.3006
168 | 2719697.6129 | 1243175.8565
169 | 2719722.2434 | 1243155.0234
170 | 2719707.1883 | 1243134.8601
171 | 2719779.571 | 1243195.5048
172 | 2719722.624 | 1243112.7222
173 | 2719795.7225 | 1243195.5689
174 | 2719648.0642 | 1243145.6769
175 | 2719649.6176 | 1243144.4241
176 | 2719668.3802 | 1243129.2925
177 | 2719672.9435 | 1243125.6123
178 | 2719633.945 | 1243180.3541
179 | 2719631.3785 | 1243183.1106
180 | 2719684.1655 | 1243175.4173
181 | 2719626.3637 | 1243188.4969
182 | 2719699.2636 | 1243155.6017
183 | 2719410.9522 | 1242973.6239
184 | 2719810.4261 | 1243195.6273
185 | 2719847.3314 | 1243190.7876
186 | 2719807.0713 | 1243207.5696
187 | 2719864.4886 | 1243175.5121
188 | 2719791.3032 | 1243239.5078
189 | 2719864.6683 | 1243175.3424
190 | 2719789.5172 | 1243254.3196
191 | 2719791.0483 | 1243266.7284
192 | 2719763.2804 | 1243127.8957
193 | 2719776.0769 | 1243135.0404
194 | 2719405.7915 | 1242969.8603
195 | 2719387.9398 | 1242956.8411
196 | 2720023.1051 | 1243260.2788

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1