## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3395-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3395-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3395-10_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3395-10_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3395-10_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_3395-10_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_3395-10_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_3395-10_0_4_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_3395-10_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_3395-10_0_4_node_76 | 0.4 | n |  | TRUE
10 | bus_LV_3395-10_0_4_node_72 | 0.4 | n |  | TRUE
11 | bus_LV_3395-10_0_4_node_78 | 0.4 | n |  | TRUE
12 | bus_LV_3395-10_0_4_node_73 | 0.4 | n |  | TRUE
13 | bus_LV_3395-10_0_4_node_70 | 0.4 | n |  | TRUE
14 | bus_LV_3395-10_0_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_3395-10_0_4_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_3395-10_0_4_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_3395-10_0_4_node_95 | 0.4 | n |  | TRUE
18 | bus_LV_3395-10_0_4_node_97 | 0.4 | n |  | TRUE
19 | bus_LV_3395-10_0_4_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_3395-10_0_4_node_98 | 0.4 | n |  | TRUE
21 | bus_LV_3395-10_0_4_node_96 | 0.4 | n |  | TRUE
22 | bus_LV_3395-10_0_4_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_3395-10_0_4_node_75 | 0.4 | n |  | TRUE
24 | bus_LV_3395-10_0_4_node_115 | 0.4 | n |  | TRUE
25 | bus_LV_3395-10_0_4_node_114 | 0.4 | n |  | TRUE
26 | bus_LV_3395-10_0_4_node_79 | 0.4 | n |  | TRUE
27 | bus_LV_3395-10_0_4_node_154 | 0.4 | n |  | TRUE
28 | bus_LV_3395-10_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_3395-10_0_4_node_8 | 0.4 | n |  | TRUE
30 | bus_LV_3395-10_0_4_node_9 | 0.4 | n |  | TRUE
31 | bus_LV_3395-10_0_4_node_10 | 0.4 | n |  | TRUE
32 | bus_LV_3395-10_0_4_node_11 | 0.4 | n |  | TRUE
33 | bus_LV_3395-10_0_4_node_12 | 0.4 | n |  | TRUE
34 | bus_LV_3395-10_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_3395-10_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_3395-10_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_3395-10_0_4_node_14 | 0.4 | n |  | TRUE
38 | bus_LV_3395-10_0_4_node_15 | 0.4 | n |  | TRUE
39 | bus_LV_3395-10_0_4_node_16 | 0.4 | n |  | TRUE
40 | bus_LV_3395-10_0_4_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_3395-10_0_4_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_3395-10_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_3395-10_0_4_node_124 | 0.4 | n |  | TRUE
44 | bus_LV_3395-10_0_4_node_125 | 0.4 | n |  | TRUE
45 | bus_LV_3395-10_0_4_node_123 | 0.4 | n |  | TRUE
46 | bus_LV_3395-10_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_3395-10_0_4_node_146 | 0.4 | n |  | TRUE
48 | bus_LV_3395-10_0_4_node_132 | 0.4 | n |  | TRUE
49 | bus_LV_3395-10_0_4_node_144 | 0.4 | n |  | TRUE
50 | bus_LV_3395-10_0_4_node_122 | 0.4 | n |  | TRUE
51 | bus_LV_3395-10_0_4_node_19 | 0.4 | n |  | TRUE
52 | bus_LV_3395-10_0_4_node_20 | 0.4 | n |  | TRUE
53 | bus_LV_3395-10_0_4_node_21 | 0.4 | n |  | TRUE
54 | bus_LV_3395-10_0_4_node_22 | 0.4 | n |  | TRUE
55 | bus_LV_3395-10_0_4_node_23 | 0.4 | n |  | TRUE
56 | bus_LV_3395-10_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_3395-10_0_4_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_3395-10_0_4_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_3395-10_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_3395-10_0_4_node_35 | 0.4 | n |  | TRUE
61 | bus_LV_3395-10_0_4_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_3395-10_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_3395-10_0_4_node_38 | 0.4 | n |  | TRUE
64 | bus_LV_3395-10_0_4_node_29 | 0.4 | n |  | TRUE
65 | bus_LV_3395-10_0_4_node_30 | 0.4 | n |  | TRUE
66 | bus_LV_3395-10_0_4_node_147 | 0.4 | n |  | TRUE
67 | bus_LV_3395-10_0_4_node_31 | 0.4 | n |  | TRUE
68 | bus_LV_3395-10_0_4_node_151 | 0.4 | n |  | TRUE
69 | bus_LV_3395-10_0_4_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_3395-10_0_4_node_32 | 0.4 | n |  | TRUE
71 | bus_LV_3395-10_0_4_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_3395-10_0_4_node_33 | 0.4 | n |  | TRUE
73 | bus_LV_3395-10_0_4_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_3395-10_0_4_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_3395-10_0_4_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_3395-10_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_3395-10_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_3395-10_0_4_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_3395-10_0_4_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_3395-10_0_4_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_3395-10_0_4_node_56 | 0.4 | n |  | TRUE
82 | bus_LV_3395-10_0_4_node_148 | 0.4 | n |  | TRUE
83 | bus_LV_3395-10_0_4_node_120 | 0.4 | n |  | TRUE
84 | bus_LV_3395-10_0_4_node_149 | 0.4 | n |  | TRUE
85 | bus_LV_3395-10_0_4_node_117 | 0.4 | n |  | TRUE
86 | bus_LV_3395-10_0_4_node_152 | 0.4 | n |  | TRUE
87 | bus_LV_3395-10_0_4_node_127 | 0.4 | n |  | TRUE
88 | bus_LV_3395-10_0_4_node_62 | 0.4 | n |  | TRUE
89 | bus_LV_3395-10_0_4_node_119 | 0.4 | n |  | TRUE
90 | bus_LV_3395-10_0_4_node_118 | 0.4 | n |  | TRUE
91 | bus_LV_3395-10_0_4_node_126 | 0.4 | n |  | TRUE
92 | bus_LV_3395-10_0_4_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_3395-10_0_4_node_130 | 0.4 | n |  | TRUE
94 | bus_LV_3395-10_0_4_node_138 | 0.4 | n |  | TRUE
95 | bus_LV_3395-10_0_4_node_139 | 0.4 | n |  | TRUE
96 | bus_LV_3395-10_0_4_node_121 | 0.4 | n |  | TRUE
97 | bus_LV_3395-10_0_4_node_141 | 0.4 | n |  | TRUE
98 | bus_LV_3395-10_0_4_node_140 | 0.4 | n |  | TRUE
99 | bus_LV_3395-10_0_4_node_142 | 0.4 | n |  | TRUE
100 | bus_LV_3395-10_0_4_node_150 | 0.4 | n |  | TRUE
101 | bus_LV_3395-10_0_4_node_57 | 0.4 | n |  | TRUE
102 | bus_LV_3395-10_0_4_node_59 | 0.4 | n |  | TRUE
103 | bus_LV_3395-10_0_4_node_64 | 0.4 | n |  | TRUE
104 | bus_LV_3395-10_0_4_node_65 | 0.4 | n |  | TRUE
105 | bus_LV_3395-10_0_4_node_60 | 0.4 | n |  | TRUE
106 | bus_LV_3395-10_0_4_node_69 | 0.4 | n |  | TRUE
107 | bus_LV_3395-10_0_4_node_66 | 0.4 | n |  | TRUE
108 | bus_LV_3395-10_0_4_node_108 | 0.4 | n |  | TRUE
109 | bus_LV_3395-10_0_4_node_67 | 0.4 | n |  | TRUE
110 | bus_LV_3395-10_0_4_node_116 | 0.4 | n |  | TRUE
111 | bus_LV_3395-10_0_4_node_136 | 0.4 | n |  | TRUE
112 | bus_LV_3395-10_0_4_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_3395-10_0_4_node_68 | 0.4 | n |  | TRUE
114 | bus_LV_3395-10_0_4_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_3395-10_0_4_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_3395-10_0_4_node_77 | 0.4 | n |  | TRUE
117 | bus_LV_3395-10_0_4_node_153 | 0.4 | n |  | TRUE
118 | bus_LV_3395-10_0_4_node_84 | 0.4 | n |  | TRUE
119 | bus_LV_3395-10_0_4_node_93 | 0.4 | n |  | TRUE
120 | bus_LV_3395-10_0_4_node_99 | 0.4 | n |  | TRUE
121 | bus_LV_3395-10_0_4_node_92 | 0.4 | n |  | TRUE
122 | bus_LV_3395-10_0_4_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_3395-10_0_4_node_82 | 0.4 | n |  | TRUE
124 | bus_LV_3395-10_0_4_node_83 | 0.4 | n |  | TRUE
125 | bus_LV_3395-10_0_4_node_81 | 0.4 | n |  | TRUE
126 | bus_LV_3395-10_0_4_node_80 | 0.4 | n |  | TRUE
127 | bus_LV_3395-10_0_4_node_100 | 0.4 | n |  | TRUE
128 | bus_LV_3395-10_0_4_node_101 | 0.4 | n |  | TRUE
129 | bus_LV_3395-10_0_4_node_85 | 0.4 | n |  | TRUE
130 | bus_LV_3395-10_0_4_node_86 | 0.4 | n |  | TRUE
131 | bus_LV_3395-10_0_4_node_87 | 0.4 | n |  | TRUE
132 | bus_LV_3395-10_0_4_node_88 | 0.4 | n |  | TRUE
133 | bus_LV_3395-10_0_4_node_94 | 0.4 | n |  | TRUE
134 | bus_LV_3395-10_0_4_node_89 | 0.4 | n |  | TRUE
135 | bus_LV_3395-10_0_4_node_90 | 0.4 | n |  | TRUE
136 | bus_LV_3395-10_0_4_node_91 | 0.4 | n |  | TRUE
137 | bus_LV_3395-10_0_4_node_103 | 0.4 | n |  | TRUE
138 | bus_LV_3395-10_0_4_node_104 | 0.4 | n |  | TRUE
139 | bus_LV_3395-10_0_4_node_107 | 0.4 | n |  | TRUE
140 | bus_LV_3395-10_0_4_node_109 | 0.4 | n |  | TRUE
141 | bus_LV_3395-10_0_4_node_105 | 0.4 | n |  | TRUE
142 | bus_LV_3395-10_0_4_node_111 | 0.4 | n |  | TRUE
143 | bus_LV_3395-10_0_4_node_113 | 0.4 | n |  | TRUE
144 | bus_LV_3395-10_0_4_node_137 | 0.4 | n |  | TRUE
145 | bus_LV_3395-10_0_4_node_135 | 0.4 | n |  | TRUE
146 | bus_LV_3395-10_0_4_node_128 | 0.4 | n |  | TRUE
147 | bus_LV_3395-10_0_4_node_145 | 0.4 | n |  | TRUE
148 | bus_LV_3395-10_0_4_node_143 | 0.4 | n |  | TRUE
149 | bus_LV_3395-10_0_4_node_129 | 0.4 | n |  | TRUE
150 | bus_LV_3395-10_0_4_node_131 | 0.4 | n |  | TRUE
151 | bus_LV_3395-10_0_4_node_133 | 0.4 | n |  | TRUE
152 | bus_LV_3395-10_0_4_node_134 | 0.4 | n |  | TRUE
153 | bus_MV_154_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3395-10_0_4_load_0 | 0 | 0.0016802 | 0.0004211 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3395-10_0_4_load_1 | 1 | 0.0015829 | 0.00039671 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3395-10_0_4_load_3 | 3 | 0.0019383 | 0.00048578 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3395-10_0_4_load_7 | 5 | 0.0024464 | 0.00061311 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3395-10_0_4_load_4 | 6 | 0.0014781 | 0.00037045 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3395-10_0_4_load_76 | 9 | 0.0052421 | 0.0013138 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3395-10_0_4_load_78 | 11 | 0.0015053 | 0.00037727 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3395-10_0_4_load_70 | 13 | 0.0012391 | 0.00031054 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3395-10_0_4_load_95 | 17 | 0.00075121 | 0.00018827 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3395-10_0_4_load_97 | 18 | 0.0016166 | 0.00040515 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3395-10_0_4_load_96 | 21 | 0.0026712 | 0.00066946 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3395-10_0_4_load_114 | 25 | 0.0089908 | 0.0022533 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3395-10_0_4_load_79 | 26 | 0.0042864 | 0.0010743 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3395-10_0_4_load_154 | 27 | 0.0028008 | 0.00070194 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3395-10_0_4_load_28 | 28 | 0.00058978 | 0.00014781 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3395-10_0_4_load_8 | 29 | 0.001156 | 0.00028972 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3395-10_0_4_load_9 | 30 | 0.0010675 | 0.00026753 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3395-10_0_4_load_24 | 34 | 0.0013459 | 0.00033731 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3395-10_0_4_load_50 | 35 | 0.0034082 | 0.00085418 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3395-10_0_4_load_25 | 36 | 0.00088316 | 0.00022134 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3395-10_0_4_load_14 | 37 | 0.00071018 | 0.00017799 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3395-10_0_4_load_42 | 42 | 0.00078721 | 0.00019729 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3395-10_0_4_load_125 | 44 | 0.0009831 | 0.00024639 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3395-10_0_4_load_123 | 45 | 0.00061154 | 0.00015327 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3395-10_0_4_load_41 | 46 | 0.0012269 | 0.00030748 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3395-10_0_4_load_146 | 47 | 0.0046425 | 0.0011635 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3395-10_0_4_load_132 | 48 | 0.0010636 | 0.00026656 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3395-10_0_4_load_122 | 50 | 0.00065968 | 0.00016533 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3395-10_0_4_load_19 | 51 | 0.00082642 | 0.00020712 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3395-10_0_4_load_20 | 52 | 0.00043183 | 0.00010823 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3395-10_0_4_load_23 | 55 | 0.0015285 | 0.00038308 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3395-10_0_4_load_34 | 57 | 0.00071384 | 0.0001789 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3395-10_0_4_load_46 | 58 | 0.0012915 | 0.00032369 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3395-10_0_4_load_47 | 59 | 0.0024411 | 0.00061181 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3395-10_0_4_load_44 | 61 | 0.0010873 | 0.0002725 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3395-10_0_4_load_37 | 62 | 0.0048047 | 0.0012042 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3395-10_0_4_load_29 | 64 | 0.00031217 | 7.8237e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3395-10_0_4_load_147 | 66 | 0.00012617 | 3.1621e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3395-10_0_4_load_31 | 67 | 0.0011405 | 0.00028583 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3395-10_0_4_load_151 | 68 | 0.00032712 | 8.1983e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3395-10_0_4_load_40 | 71 | 0.0011925 | 0.00029886 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3395-10_0_4_load_49 | 73 | 0.0026335 | 0.00066002 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3395-10_0_4_load_43 | 74 | 0.00093901 | 0.00023534 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3395-10_0_4_load_45 | 75 | 0.00084579 | 0.00021198 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3395-10_0_4_load_51 | 76 | 0.0016874 | 0.0004229 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3395-10_0_4_load_56 | 81 | 0.0036232 | 0.00090807 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3395-10_0_4_load_148 | 82 | 0.00088422 | 0.00022161 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3395-10_0_4_load_152 | 86 | 0.00067477 | 0.00016911 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3395-10_0_4_load_126 | 91 | 0.0075004 | 0.0018798 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3395-10_0_4_load_138 | 94 | 0.0016868 | 0.00042275 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3395-10_0_4_load_139 | 95 | 0.0025555 | 0.00064046 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3395-10_0_4_load_141 | 97 | 0.00065602 | 0.00016441 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3395-10_0_4_load_140 | 98 | 0.0018275 | 0.00045803 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3395-10_0_4_load_142 | 99 | 0.0049718 | 0.001246 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3395-10_0_4_load_150 | 100 | 0.0021233 | 0.00053214 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3395-10_0_4_load_57 | 101 | 0.0058796 | 0.0014736 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3395-10_0_4_load_65 | 104 | 0.00018662 | 4.6771e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3395-10_0_4_load_60 | 105 | 0.0017222 | 0.00043162 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3395-10_0_4_load_69 | 106 | 0.00024922 | 6.2459e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3395-10_0_4_load_66 | 107 | 0.012204 | 0.0030586 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3395-10_0_4_load_68 | 113 | 0.00048938 | 0.00012265 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3395-10_0_4_load_106 | 114 | 0.00052102 | 0.00013058 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3395-10_0_4_load_153 | 117 | 0.0023306 | 0.00058411 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3395-10_0_4_load_99 | 120 | 0.0017886 | 0.00044826 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3395-10_0_4_load_92 | 121 | 0.0013372 | 0.00033514 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3395-10_0_4_load_112 | 122 | 0.0006195 | 0.00015526 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3395-10_0_4_load_83 | 124 | 0.0037495 | 0.00093971 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3395-10_0_4_load_81 | 125 | 0.0020774 | 0.00052064 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3395-10_0_4_load_80 | 126 | 0.005449 | 0.0013656 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3395-10_0_4_load_100 | 127 | 0.00092392 | 0.00023156 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3395-10_0_4_load_101 | 128 | 0.0029539 | 0.00074031 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3395-10_0_4_load_85 | 129 | 0.0051755 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3395-10_0_4_load_87 | 131 | 0.00064665 | 0.00016206 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3395-10_0_4_load_88 | 132 | 0.0002457 | 6.1578e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3395-10_0_4_load_94 | 133 | 0.0037941 | 0.0009509 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3395-10_0_4_load_89 | 134 | 0.00057766 | 0.00014478 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3395-10_0_4_load_90 | 135 | 0.0015785 | 0.00039561 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3395-10_0_4_load_91 | 136 | 0.00086826 | 0.00021761 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3395-10_0_4_load_103 | 137 | 0.00097059 | 0.00024325 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3395-10_0_4_load_104 | 138 | 0.00052408 | 0.00013135 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3395-10_0_4_load_107 | 139 | 0.00019405 | 4.8634e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3395-10_0_4_load_109 | 140 | 0.00041599 | 0.00010426 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3395-10_0_4_load_105 | 141 | 0.0015773 | 0.00039531 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3395-10_0_4_load_111 | 142 | 0.0028823 | 0.00072238 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3395-10_0_4_load_113 | 143 | 0.0026729 | 0.00066988 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3395-10_0_4_load_137 | 144 | 0.0054121 | 0.0013564 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3395-10_0_4_load_135 | 145 | 0.0030514 | 0.00076475 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3395-10_0_4_load_128 | 146 | 0.0010109 | 0.00025337 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3395-10_0_4_load_145 | 147 | 0.00064204 | 0.00016091 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3395-10_0_4_load_143 | 148 | 0.0038769 | 0.00097163 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3395-10_0_4_load_129 | 149 | 0.0016291 | 0.0004083 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3395-10_0_4_load_131 | 150 | 0.00096662 | 0.00024226 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3395-10_0_4_load_133 | 151 | 0.0015967 | 0.00040016 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3395-10_0_4_load_134 | 152 | 0.0013146 | 0.00032947 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3395-10_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.034708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3395-10_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.067191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3395-10_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.028358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3395-10_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.2703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_3395-10_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.021905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3395-10_0_4_line_5 | NAYY 4x150 SE | 4 | 12 | 0.32364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3395-10_0_4_line_6 | NAYY 4x150 SE | 4 | 13 | 0.030465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_3395-10_0_4_line_7 | NAYY 4x150 SE | 5 | 14 | 0.038616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3395-10_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.08854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3395-10_0_4_line_9 | NAYY 4x150 SE | 7 | 15 | 0.005713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3395-10_0_4_line_10 | NAYY 4x150 SE | 8 | 9 | 0.017608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_3395-10_0_4_line_11 | NAYY 4x150 SE | 8 | 10 | 0.11401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_3395-10_0_4_line_12 | NAYY 4x150 SE | 8 | 11 | 0.013347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3395-10_0_4_line_13 | NAYY 4x150 SE | 9 | 16 | 0.013263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_3395-10_0_4_line_14 | NAYY 4x150 SE | 10 | 17 | 0.019882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3395-10_0_4_line_15 | NAYY 4x150 SE | 10 | 18 | 0.020247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_3395-10_0_4_line_16 | NAYY 4x150 SE | 11 | 26 | 0.0016175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3395-10_0_4_line_17 | NAYY 4x150 SE | 12 | 27 | 0.00811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3395-10_0_4_line_18 | NAYY 4x150 SE | 13 | 16 | 0.0044578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_3395-10_0_4_line_19 | NAYY 4x150 SE | 14 | 15 | 0.02675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3395-10_0_4_line_20 | NAYY 4x150 SE | 14 | 28 | 0.033626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3395-10_0_4_line_21 | NAYY 4x150 SE | 15 | 62 | 0.02226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3395-10_0_4_line_22 | NAYY 4x150 SE | 16 | 116 | 0.01326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3395-10_0_4_line_23 | NAYY 4x150 SE | 17 | 119 | 0.0078793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3395-10_0_4_line_24 | NAYY 4x150 SE | 18 | 21 | 0.020524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_3395-10_0_4_line_25 | NAYY 4x150 SE | 19 | 20 | 0.006722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3395-10_0_4_line_26 | NAYY 4x150 SE | 19 | 21 | 0.018982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_3395-10_0_4_line_27 | NAYY 4x150 SE | 19 | 22 | 0.10701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_3395-10_0_4_line_28 | NAYY 4x150 SE | 20 | 120 | 0.018252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3395-10_0_4_line_29 | NAYY 4x150 SE | 20 | 121 | 0.032672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3395-10_0_4_line_30 | NAYY 4x150 SE | 22 | 23 | 0.038684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_3395-10_0_4_line_31 | NAYY 4x150 SE | 23 | 24 | 0.058563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_3395-10_0_4_line_32 | NAYY 4x150 SE | 23 | 25 | 0.014169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3395-10_0_4_line_33 | NAYY 4x150 SE | 24 | 90 | 0.062233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_3395-10_0_4_line_34 | NAYY 4x150 SE | 25 | 122 | 0.046048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3395-10_0_4_line_35 | NAYY 4x150 SE | 26 | 126 | 0.0091036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3395-10_0_4_line_36 | NAYY 4x150 SE | 29 | 30 | 0.031961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3395-10_0_4_line_37 | NAYY 4x150 SE | 29 | 31 | 0.025963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3395-10_0_4_line_38 | NAYY 4x150 SE | 30 | 32 | 0.026347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3395-10_0_4_line_39 | NAYY 4x150 SE | 31 | 33 | 0.046692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3395-10_0_4_line_40 | NAYY 4x150 SE | 32 | 34 | 0.082853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3395-10_0_4_line_41 | NAYY 4x150 SE | 33 | 35 | 0.010626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3395-10_0_4_line_42 | NAYY 4x150 SE | 34 | 36 | 0.23314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3395-10_0_4_line_43 | NAYY 4x150 SE | 36 | 40 | 0.01554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3395-10_0_4_line_44 | NAYY 4x150 SE | 37 | 38 | 0.016344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3395-10_0_4_line_45 | NAYY 4x150 SE | 38 | 39 | 0.039517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3395-10_0_4_line_46 | NAYY 4x150 SE | 38 | 40 | 0.012965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3395-10_0_4_line_47 | NAYY 4x150 SE | 39 | 41 | 0.023067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3395-10_0_4_line_48 | NAYY 4x150 SE | 40 | 42 | 0.084754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3395-10_0_4_line_49 | NAYY 4x150 SE | 41 | 43 | 0.027402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3395-10_0_4_line_50 | NAYY 4x150 SE | 41 | 44 | 0.018824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3395-10_0_4_line_51 | NAYY 4x150 SE | 41 | 45 | 0.0094854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3395-10_0_4_line_52 | NAYY 4x150 SE | 42 | 46 | 0.01989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3395-10_0_4_line_53 | NAYY 4x150 SE | 43 | 47 | 0.008775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3395-10_0_4_line_54 | NAYY 4x150 SE | 43 | 48 | 0.016346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_3395-10_0_4_line_55 | NAYY 4x150 SE | 44 | 49 | 0.012461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3395-10_0_4_line_56 | NAYY 4x150 SE | 45 | 50 | 0.0011312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3395-10_0_4_line_57 | NAYY 4x150 SE | 48 | 93 | 0.006758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_3395-10_0_4_line_58 | NAYY 4x150 SE | 49 | 147 | 0.012217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3395-10_0_4_line_59 | NAYY 4x150 SE | 51 | 52 | 0.20218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3395-10_0_4_line_60 | NAYY 4x150 SE | 51 | 53 | 0.095086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3395-10_0_4_line_61 | NAYY 4x150 SE | 53 | 54 | 0.008422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3395-10_0_4_line_62 | NAYY 4x150 SE | 53 | 55 | 0.0093061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3395-10_0_4_line_63 | NAYY 4x150 SE | 54 | 56 | 0.006993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3395-10_0_4_line_64 | NAYY 4x150 SE | 54 | 57 | 0.035491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3395-10_0_4_line_65 | NAYY 4x150 SE | 55 | 58 | 0.0072158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3395-10_0_4_line_66 | NAYY 4x150 SE | 56 | 59 | 0.010265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3395-10_0_4_line_67 | NAYY 4x150 SE | 57 | 60 | 0.1218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3395-10_0_4_line_68 | NAYY 4x150 SE | 58 | 61 | 0.052454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3395-10_0_4_line_69 | NAYY 4x150 SE | 60 | 70 | 0.00507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3395-10_0_4_line_70 | NAYY 4x150 SE | 61 | 74 | 0.034795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3395-10_0_4_line_71 | NAYY 4x150 SE | 62 | 63 | 0.021853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3395-10_0_4_line_72 | NAYY 4x150 SE | 63 | 71 | 0.0162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3395-10_0_4_line_73 | NAYY 4x150 SE | 63 | 72 | 0.003962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3395-10_0_4_line_74 | NAYY 4x150 SE | 64 | 65 | 0.03898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3395-10_0_4_line_75 | NAYY 4x150 SE | 64 | 66 | 0.19859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3395-10_0_4_line_76 | NAYY 4x150 SE | 65 | 67 | 0.020691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3395-10_0_4_line_77 | NAYY 4x150 SE | 66 | 68 | 0.11535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3395-10_0_4_line_78 | NAYY 4x150 SE | 67 | 69 | 0.017509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3395-10_0_4_line_79 | NAYY 4x150 SE | 69 | 72 | 0.038473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3395-10_0_4_line_80 | NAYY 4x150 SE | 70 | 71 | 0.033452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3395-10_0_4_line_81 | NAYY 4x150 SE | 72 | 73 | 0.022526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3395-10_0_4_line_82 | NAYY 4x150 SE | 74 | 75 | 0.018241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3395-10_0_4_line_83 | NAYY 4x150 SE | 76 | 77 | 0.248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3395-10_0_4_line_84 | NAYY 4x150 SE | 77 | 78 | 0.21896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3395-10_0_4_line_85 | NAYY 4x150 SE | 77 | 79 | 0.15293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_3395-10_0_4_line_86 | NAYY 4x150 SE | 77 | 80 | 0.23598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_3395-10_0_4_line_87 | NAYY 4x150 SE | 78 | 81 | 0.020633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3395-10_0_4_line_88 | NAYY 4x150 SE | 79 | 82 | 0.077267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3395-10_0_4_line_89 | NAYY 4x150 SE | 79 | 83 | 0.24858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_3395-10_0_4_line_90 | NAYY 4x150 SE | 80 | 84 | 0.36392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_3395-10_0_4_line_91 | NAYY 4x150 SE | 83 | 96 | 0.04184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_3395-10_0_4_line_92 | NAYY 4x150 SE | 83 | 95 | 0.01115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
93 | LV_3395-10_0_4_line_93 | NAYY 4x150 SE | 83 | 85 | 0.012347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_3395-10_0_4_line_94 | NAYY 4x150 SE | 84 | 100 | 0.007002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_3395-10_0_4_line_95 | NAYY 4x150 SE | 85 | 86 | 0.009442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_3395-10_0_4_line_96 | NAYY 4x150 SE | 85 | 87 | 0.31611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
97 | LV_3395-10_0_4_line_97 | NAYY 4x150 SE | 87 | 99 | 0.020734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3395-10_0_4_line_98 | NAYY 4x150 SE | 88 | 89 | 0.044612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
99 | LV_3395-10_0_4_line_99 | NAYY 4x150 SE | 88 | 90 | 0.058054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
100 | LV_3395-10_0_4_line_100 | NAYY 4x150 SE | 88 | 91 | 0.040158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3395-10_0_4_line_101 | NAYY 4x150 SE | 88 | 92 | 0.052048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
102 | LV_3395-10_0_4_line_102 | NAYY 4x150 SE | 89 | 95 | 0.0024765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
103 | LV_3395-10_0_4_line_103 | NAYY 4x150 SE | 90 | 93 | 0.040051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
104 | LV_3395-10_0_4_line_104 | NAYY 4x150 SE | 90 | 94 | 0.058775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3395-10_0_4_line_105 | NAYY 4x150 SE | 92 | 107 | 0.056533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
106 | LV_3395-10_0_4_line_106 | NAYY 4x150 SE | 93 | 146 | 0.032146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3395-10_0_4_line_107 | NAYY 4x150 SE | 94 | 110 | 0.040202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3395-10_0_4_line_108 | NAYY 4x150 SE | 96 | 97 | 0.015215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3395-10_0_4_line_109 | NAYY 4x150 SE | 96 | 98 | 0.0072814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3395-10_0_4_line_110 | NAYY 4x150 SE | 99 | 148 | 0.0070286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_3395-10_0_4_line_111 | NAYY 4x150 SE | 101 | 102 | 0.023802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3395-10_0_4_line_112 | NAYY 4x150 SE | 102 | 103 | 0.003947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_3395-10_0_4_line_113 | NAYY 4x150 SE | 102 | 104 | 0.01686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3395-10_0_4_line_114 | NAYY 4x150 SE | 103 | 108 | 0.033047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3395-10_0_4_line_115 | NAYY 4x150 SE | 104 | 106 | 0.0030838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3395-10_0_4_line_116 | NAYY 4x150 SE | 105 | 106 | 0.014892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3395-10_0_4_line_117 | NAYY 4x150 SE | 107 | 109 | 0.018949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3395-10_0_4_line_118 | NAYY 4x150 SE | 108 | 112 | 0.028923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3395-10_0_4_line_119 | NAYY 4x150 SE | 108 | 113 | 0.03814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3395-10_0_4_line_120 | NAYY 4x150 SE | 109 | 113 | 0.01308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3395-10_0_4_line_121 | NAYY 4x150 SE | 110 | 111 | 0.024624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3395-10_0_4_line_122 | NAYY 4x150 SE | 111 | 144 | 0.026483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3395-10_0_4_line_123 | NAYY 4x150 SE | 111 | 145 | 0.051411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3395-10_0_4_line_124 | NAYY 4x150 SE | 112 | 140 | 0.0022764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3395-10_0_4_line_125 | NAYY 4x150 SE | 114 | 115 | 0.0092035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3395-10_0_4_line_126 | NAYY 4x150 SE | 115 | 139 | 0.0126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3395-10_0_4_line_127 | NAYY 4x150 SE | 115 | 128 | 0.018133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3395-10_0_4_line_128 | NAYY 4x150 SE | 116 | 117 | 0.008429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3395-10_0_4_line_129 | NAYY 4x150 SE | 116 | 118 | 0.048794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3395-10_0_4_line_130 | NAYY 4x150 SE | 118 | 123 | 0.06666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3395-10_0_4_line_131 | NAYY 4x150 SE | 119 | 133 | 0.006745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3395-10_0_4_line_132 | NAYY 4x150 SE | 119 | 131 | 0.033116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3395-10_0_4_line_133 | NAYY 4x150 SE | 120 | 137 | 0.018029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3395-10_0_4_line_134 | NAYY 4x150 SE | 121 | 135 | 0.019911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3395-10_0_4_line_135 | NAYY 4x150 SE | 122 | 142 | 0.045596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3395-10_0_4_line_136 | NAYY 4x150 SE | 123 | 124 | 0.002343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3395-10_0_4_line_137 | NAYY 4x150 SE | 123 | 125 | 0.0024864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3395-10_0_4_line_138 | NAYY 4x150 SE | 127 | 128 | 0.037061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3395-10_0_4_line_139 | NAYY 4x150 SE | 129 | 130 | 0.017078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3395-10_0_4_line_140 | NAYY 4x150 SE | 130 | 131 | 0.0046893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3395-10_0_4_line_141 | NAYY 4x150 SE | 130 | 132 | 0.023612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3395-10_0_4_line_142 | NAYY 4x150 SE | 134 | 135 | 0.018924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3395-10_0_4_line_143 | NAYY 4x150 SE | 134 | 136 | 0.00013509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3395-10_0_4_line_144 | NAYY 4x150 SE | 137 | 138 | 0.0076206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3395-10_0_4_line_145 | NAYY 4x150 SE | 138 | 141 | 0.0077519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3395-10_0_4_line_146 | NAYY 4x150 SE | 139 | 140 | 0.012319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3395-10_0_4_line_147 | NAYY 4x150 SE | 142 | 143 | 0.03254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3395-10_0_4_line_148 | NAYY 4x150 SE | 146 | 149 | 0.0029734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3395-10_0_4_line_149 | NAYY 4x150 SE | 149 | 150 | 0.014253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_3395-10_0_4_line_150 | NAYY 4x150 SE | 150 | 151 | 0.02476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_3395-10_0_4_line_151 | NAYY 4x150 SE | 151 | 152 | 0.025809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3395-10_0_4_trafo_97 | 0.25 MVA 20/0.4 kV | 153 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34
0 | 2724271.4529 | 1244457.2604 | 2724292.2326 | 1244429.4605
1 | 2724230.7418 | 1244510.712 | 2724259.6981 | 1244472.9864 | 2724271.4529 | 1244457.2604
2 | 2724309.2108 | 1244406.7464 | 2724292.2326 | 1244429.4605
3 | 2724230.7418 | 1244510.712 | 2724227.8743 | 1244514.444 | 2724192.9884 | 1244554.5142 | 2724186.8981 | 1244562.3378 | 2724182.0574 | 1244570.777 | 2724179.2138 | 1244579.5027 | 2724178.3074 | 1244585.2441 | 2724177.8364 | 1244594.3753 | 2724178.3195 | 1244607.3965 | 2724181.3985 | 1244631.815 | 2724188.0851 | 1244669.4869 | 2724183.4617 | 1244670.8023 | 2724179.6 | 1244672.2005 | 2724177.5611 | 1244673.5478 | 2724176.7625 | 1244674.8656 | 2724172.317 | 1244689.6962 | 2724169.6479 | 1244701.2835 | 2724167.809 | 1244710.7642 | 2724166.8635 | 1244719.8187 | 2724166.511 | 1244731.2321 | 2724166.8625 | 1244742.2377 | 2724167.7785 | 1244749.0293 | 2724163.3376 | 1244749.5702
4 | 2724322.1417 | 1244389.0747 | 2724320.5875 | 1244391.5263 | 2724309.2108 | 1244406.7464
5 | 2724163.3376 | 1244749.5702 | 2724167.7785 | 1244749.0293 | 2724166.8625 | 1244742.2377 | 2724166.511 | 1244731.2321 | 2724166.8635 | 1244719.8187 | 2724167.809 | 1244710.7642 | 2724169.6479 | 1244701.2835 | 2724172.317 | 1244689.6962 | 2724176.7625 | 1244674.8656 | 2724177.5611 | 1244673.5478 | 2724179.6 | 1244672.2005 | 2724183.4617 | 1244670.8023 | 2724188.0851 | 1244669.4869 | 2724192.8154 | 1244692.65 | 2724194.7842 | 1244701.1429 | 2724197.1645 | 1244709.4775 | 2724202.1649 | 1244708.2034 | 2724205.3924 | 1244706.7697 | 2724207.1806 | 1244704.0382 | 2724207.8709 | 1244700.3161 | 2724206.8834 | 1244695.8584 | 2724196.2893 | 1244658.1713 | 2724195.2539 | 1244648.4191 | 2724195.6456 | 1244640.187 | 2724197.5812 | 1244630.7862 | 2724202.3301 | 1244620.955 | 2724209.7196 | 1244609.5668 | 2724229.8175 | 1244585.8341 | 2724237.5317 | 1244575.9095 | 2724241.9865 | 1244568.5743 | 2724229.0271 | 1244562.9537 | 2724223.4887 | 1244571.8564 | 2724222.1273 | 1244571.8946
6 | 2724163.3376 | 1244749.5702 | 2724159.9633 | 1244750.0777 | 2724154.7697 | 1244751.1922 | 2724149.2769 | 1244753.6015 | 2724136.2957 | 1244762.5075
7 | 2724336.821 | 1244353.8679 | 2724335.6893 | 1244360.9724 | 2724332.3671 | 1244371.9565 | 2724327.2875 | 1244380.9577 | 2724322.1417 | 1244389.0747
8 | 2724330.8514 | 1244331.4126 | 2724331.598 | 1244333.6635 | 2724332.3032 | 1244340.4062 | 2724332.6286 | 1244346.5182 | 2724331.8242 | 1244355.6758 | 2724330.8766 | 1244360.8492 | 2724329.6899 | 1244366.2511 | 2724327.353 | 1244371.7068 | 2724326.3815 | 1244374.0551 | 2724324.5505 | 1244377.3751 | 2724321.6884 | 1244382.286 | 2724316.4812 | 1244389.4385 | 2724301.8722 | 1244409.8385 | 2724301.0505 | 1244410.9649
9 | 2724330.8514 | 1244331.4126 | 2724334.7714 | 1244327.2468
10 | 2724138.3589 | 1244794.53 | 2724138.2882 | 1244776.9225
11 | 2724138.3589 | 1244794.53 | 2724155.3736 | 1244795.6203 | 2724158.7608 | 1244798.1044 | 2724162.2148 | 1244798.1212 | 2724163.9598 | 1244797.813 | 2724164.002 | 1244831.5203 | 2724164.1816 | 1244839.9089 | 2724164.6309 | 1244848.7703 | 2724165.4509 | 1244856.8943 | 2724165.4731 | 1244864.1343 | 2724164.887 | 1244869.7379 | 2724162.6228 | 1244885.0924
12 | 2724138.3589 | 1244794.53 | 2724137.2042 | 1244807.8266
13 | 2724132.6198 | 1244765.0293 | 2724138.2847 | 1244776.0572 | 2724138.2882 | 1244776.9225
14 | 2724162.6228 | 1244885.0924 | 2724156.2997 | 1244884.9266 | 2724142.7734 | 1244885.8332
15 | 2724162.6228 | 1244885.0924 | 2724162.2974 | 1244888.722 | 2724161.9121 | 1244898.4556 | 2724161.8701 | 1244905.3169
16 | 2724137.2042 | 1244807.8266 | 2724137.0643 | 1244809.438
17 | 2724222.1273 | 1244571.8946 | 2724218.2438 | 1244579.0193
18 | 2724132.6198 | 1244765.0293 | 2724136.2957 | 1244762.5075
19 | 2724334.7714 | 1244327.2468 | 2724336.8152 | 1244343.6925 | 2724336.821 | 1244353.8679
20 | 2724336.821 | 1244353.8679 | 2724345.0023 | 1244353.0497 | 2724355.1617 | 1244349.8266 | 2724366.7197 | 1244350.5584 | 2724369.8451 | 1244350.0615
21 | 2724334.7714 | 1244327.2468 | 2724330.7906 | 1244305.3455
22 | 2724132.6198 | 1244765.0293 | 2724121.6683 | 1244772.551
23 | 2724134.8949 | 1244885.9462 | 2724142.7734 | 1244885.8332
24 | 2724161.7447 | 1244925.8404 | 2724161.8701 | 1244905.3169
25 | 2724154.9006 | 1244945.2263 | 2724159.7228 | 1244944.8714 | 2724161.6286 | 1244944.8223
26 | 2724161.6286 | 1244944.8223 | 2724161.7447 | 1244925.8404
27 | 2724161.1636 | 1245051.8145 | 2724161.6286 | 1244944.8223
28 | 2724154.9006 | 1244945.2263 | 2724152.3077 | 1244949.2087 | 2724143.9324 | 1244956.8066 | 2724142.2853 | 1244958.2522
29 | 2724154.9006 | 1244945.2263 | 2724147.6175 | 1244938.5682 | 2724142.6561 | 1244935.4618 | 2724134.6339 | 1244934.86 | 2724125.7357 | 1244935.2322
30 | 2724161.1636 | 1245051.8145 | 2724166.0941 | 1245052.0624 | 2724166.0565 | 1245071.1778 | 2724165.9087 | 1245085.8094
31 | 2724194.3659 | 1245117.5654 | 2724165.7217 | 1245115.6642 | 2724165.8221 | 1245099.686 | 2724165.9087 | 1245085.8094
32 | 2724165.9087 | 1245085.8094 | 2724180.0388 | 1245086.8575
33 | 2724181.1434 | 1245178.3069 | 2724182.2136 | 1245168.3541 | 2724189.7235 | 1245137.1181 | 2724194.3659 | 1245117.5654
34 | 2724226.0404 | 1245087.0506 | 2724224.9728 | 1245087.1248 | 2724193.0692 | 1245087.8241 | 2724180.0388 | 1245086.8575
35 | 2724134.3512 | 1244818.0661 | 2724136.8946 | 1244811.3915 | 2724137.0643 | 1244809.438
36 | 2724308.8227 | 1244735.3233 | 2724304.1963 | 1244703.6985
37 | 2724284.9819 | 1244696.2276 | 2724303.0547 | 1244695.8949 | 2724304.1963 | 1244703.6985
38 | 2724293.2934 | 1244754.062 | 2724305.512 | 1244745.2438 | 2724309.4874 | 1244739.867 | 2724308.8227 | 1244735.3233
39 | 2724284.9819 | 1244696.2276 | 2724299.5137 | 1244680.9191 | 2724311.0675 | 1244675.3342 | 2724323.3748 | 1244671.6668
40 | 2724293.2934 | 1244754.062 | 2724306.4991 | 1244787.5671 | 2724322.2551 | 1244831.6764
41 | 2724323.3748 | 1244671.6668 | 2724327.9891 | 1244681.2383
42 | 2724308.2679 | 1245063.1913 | 2724311.9909 | 1245042.1762 | 2724312.4577 | 1245008.0236 | 2724313.4513 | 1244988.0386 | 2724315.7805 | 1244965.2792 | 2724317.9051 | 1244920.5635 | 2724326.4512 | 1244861.5925 | 2724326.0739 | 1244847.506 | 2724323.4127 | 1244834.9173 | 2724322.2551 | 1244831.6764
43 | 2724305.9069 | 1245078.5463 | 2724306.8896 | 1245070.9715 | 2724308.2679 | 1245063.1913
44 | 2724297.6769 | 1245088.5824 | 2724303.8968 | 1245103.6962
45 | 2724297.6769 | 1245088.5824 | 2724273.8038 | 1245120.1201
46 | 2724305.9069 | 1245078.5463 | 2724297.6769 | 1245088.5824
47 | 2724258.9515 | 1245137.7906 | 2724268.0187 | 1245127.4718 | 2724273.8038 | 1245120.1201
48 | 2724305.9069 | 1245078.5463 | 2724344.6204 | 1245031.0284 | 2724348.5603 | 1245026.9742 | 2724353.6424 | 1245022.8772 | 2724358.6696 | 1245019.9579 | 2724363.8902 | 1245018.3315
49 | 2724258.9515 | 1245137.7906 | 2724246.4775 | 1245150.5402 | 2724239.6617 | 1245157.3032
50 | 2724258.9515 | 1245137.7906 | 2724263.2097 | 1245143.0621 | 2724269.2864 | 1245153.4651
51 | 2724258.9515 | 1245137.7906 | 2724252.8257 | 1245130.5486
52 | 2724383.2881 | 1245020.2965 | 2724378.6701 | 1245018.8429 | 2724372.1985 | 1245017.4727 | 2724366.5289 | 1245017.5095 | 2724363.8902 | 1245018.3315
53 | 2724238.7487 | 1245148.5767 | 2724239.6617 | 1245157.3032
54 | 2724239.6617 | 1245157.3032 | 2724233.4218 | 1245162.5548 | 2724226.685 | 1245166.2724 | 2724226.239 | 1245166.4897
55 | 2724275.7076 | 1245164.1418 | 2724273.2058 | 1245160.1749 | 2724269.2864 | 1245153.4651
56 | 2724252.0952 | 1245129.6849 | 2724252.8257 | 1245130.5486
57 | 2724220.1636 | 1245169.4496 | 2724226.239 | 1245166.4897
58 | 2724275.7076 | 1245164.1418 | 2724282.2266 | 1245174.4739
59 | 2724453.0424 | 1244343.4682 | 2724444.0177 | 1244359.7537 | 2724426.0394 | 1244385.0648 | 2724410.5002 | 1244402.943 | 2724405.9509 | 1244410.4428 | 2724403.1401 | 1244416.1443 | 2724400.6759 | 1244424.4218 | 2724397.1497 | 1244445.488 | 2724396.7697 | 1244452.7862 | 2724397.9017 | 1244458.2813 | 2724400.796 | 1244462.6457 | 2724405.3908 | 1244465.9448 | 2724411.4952 | 1244467.9078 | 2724418.0137 | 1244468.5117 | 2724426.0836 | 1244467.5913 | 2724433.2299 | 1244465.2948 | 2724444.4601 | 1244459.67 | 2724450.567 | 1244458.2747 | 2724457.5147 | 1244458.5985 | 2724462.7624 | 1244460.3211
60 | 2724469.6927 | 1244251.9453 | 2724471.8039 | 1244260.4857 | 2724472.6181 | 1244267.0751 | 2724472.7985 | 1244275.764 | 2724472.0687 | 1244284.9565 | 2724469.8482 | 1244295.6634 | 2724464.4707 | 1244315.2339 | 2724459.9298 | 1244328.4498 | 2724454.4283 | 1244340.9673 | 2724453.0424 | 1244343.4682
61 | 2724469.6927 | 1244251.9453 | 2724468.0436 | 1244248.0407 | 2724465.5209 | 1244244.6961
62 | 2724469.6927 | 1244251.9453 | 2724467.3576 | 1244260.9537
63 | 2724470.759 | 1244240.0465 | 2724465.5209 | 1244244.6961
64 | 2724465.5209 | 1244244.6961 | 2724460.5979 | 1244241.1787 | 2724444.7907 | 1244231.8281 | 2724434.8324 | 1244226.9826
65 | 2724465.5469 | 1244267.9386 | 2724467.3576 | 1244260.9537
66 | 2724470.759 | 1244240.0465 | 2724480.5597 | 1244236.9939
67 | 2724317.4904 | 1244229.9355 | 2724321.5898 | 1244229.1096 | 2724384.4976 | 1244215.5388 | 2724396.8196 | 1244213.7401 | 2724406.1173 | 1244214.1243 | 2724414.4093 | 1244217.0451 | 2724434.8324 | 1244226.9826
68 | 2724465.5469 | 1244267.9386 | 2724462.3903 | 1244281.1057 | 2724438.3292 | 1244311.689
69 | 2724317.4904 | 1244229.9355 | 2724318.3911 | 1244234.9253
70 | 2724413.1232 | 1244322.9617 | 2724424.0481 | 1244311.0269 | 2724434.0652 | 1244317.1088 | 2724438.3292 | 1244311.689
71 | 2724326.8826 | 1244283.8447 | 2724330.7906 | 1244305.3455
72 | 2724326.8826 | 1244283.8447 | 2724324.1887 | 1244267.8705
73 | 2724326.8826 | 1244283.8447 | 2724322.9346 | 1244284.2957
74 | 2724277.3542 | 1244243.4061 | 2724255.2832 | 1244246.8801 | 2724238.6496 | 1244246.5315
75 | 2724238.6496 | 1244246.5315 | 2724105.1662 | 1244099.4902
76 | 2724277.3542 | 1244243.4061 | 2724281.4372 | 1244256.7029 | 2724282.8127 | 1244263.3437
77 | 2724105.1662 | 1244099.4902 | 2724000.0389 | 1244052.0084
78 | 2724285.3955 | 1244280.6394 | 2724284.3822 | 1244270.921 | 2724282.8127 | 1244263.3437
79 | 2724322.9346 | 1244284.2957 | 2724309.1653 | 1244285.9085 | 2724302.3301 | 1244282.3734 | 2724285.3955 | 1244280.6394
80 | 2724318.3911 | 1244234.9253 | 2724323.0772 | 1244261.2791 | 2724324.1887 | 1244267.8705
81 | 2724322.9346 | 1244284.2957 | 2724325.8458 | 1244300.8374 | 2724326.8077 | 1244306.4857
82 | 2724400.8068 | 1244336.4166 | 2724413.1232 | 1244322.9617
83 | 2723852.2078 | 1244945.6661 | 2723849.1836 | 1244942.4447 | 2723846.6046 | 1244929.8579 | 2723845.0572 | 1244858.4874 | 2723840.0225 | 1244789.0568 | 2723831.7148 | 1244730.467 | 2723825.5028 | 1244700.5481
84 | 2723946.8722 | 1244786.2191 | 2723947.5184 | 1244790.3806 | 2723957.0821 | 1244831.1372 | 2723959.5094 | 1244843.0202 | 2723959.3472 | 1244854.0262 | 2723956.8987 | 1244864.4839 | 2723944.8968 | 1244889.3653 | 2723937.6005 | 1244899.9552 | 2723928.5595 | 1244905.4154 | 2723880.2529 | 1244923.1103 | 2723864.478 | 1244931.4324 | 2723855.8757 | 1244939.7821 | 2723852.2078 | 1244945.6661
85 | 2723852.2078 | 1244945.6661 | 2723849.8566 | 1244951.4775 | 2723849.4055 | 1244962.2105 | 2723850.2742 | 1244975.2619 | 2723850.7245 | 1244989.1609 | 2723851.0296 | 1244991.5582 | 2723851.7574 | 1244997.2449 | 2723852.1691 | 1245000.6897 | 2723852.7145 | 1245003.5257 | 2723852.9397 | 1245004.687 | 2723854.3924 | 1245012.2126 | 2723856.6838 | 1245024.0927 | 2723860.3632 | 1245037.1918 | 2723862.1681 | 1245041.9668 | 2723863.953 | 1245044.8065 | 2723866.2897 | 1245047.6466 | 2723869.1451 | 1245050.6199 | 2723873.6271 | 1245048.1002 | 2723876.446 | 1245046.669 | 2723878.0943 | 1245046.2808 | 2723879.8275 | 1245046.1725 | 2723883.1966 | 1245046.2651 | 2723887.4963 | 1245046.6775 | 2723889.6823 | 1245047.3237 | 2723900.5148 | 1245050.5193 | 2723910.6937 | 1245053.5234
86 | 2723732.3231 | 1244939.7817 | 2723779.7159 | 1244937.2237 | 2723799.7703 | 1244936.4304 | 2723802.6686 | 1244956.1743 | 2723807.4703 | 1244975.9802 | 2723812.1549 | 1244985.1079 | 2723817.8168 | 1244993.3998 | 2723825.5875 | 1245001.3354 | 2723844.4875 | 1245015.2639 | 2723848.7409 | 1245009.9371 | 2723852.9397 | 1245004.687 | 2723852.7145 | 1245003.5257 | 2723852.1691 | 1245000.6897 | 2723851.7574 | 1244997.2449 | 2723851.0296 | 1244991.5582 | 2723850.7245 | 1244989.1609 | 2723850.2742 | 1244975.2619 | 2723849.4055 | 1244962.2105 | 2723849.8566 | 1244951.4775 | 2723852.2078 | 1244945.6661
87 | 2723946.8722 | 1244786.2191 | 2723944.376 | 1244770.0422 | 2723944.1348 | 1244765.7841
88 | 2723910.6937 | 1245053.5234 | 2723915.6571 | 1245037.7359 | 2723924.8615 | 1245014.6864 | 2723942.7389 | 1244983.5223
89 | 2723910.6937 | 1245053.5234 | 2723926.875 | 1245058.2876 | 2723928.6027 | 1245058.8019 | 2723936.0043 | 1245103.172 | 2723936.2701 | 1245104.5565 | 2723935.2812 | 1245109.9182 | 2723938.4058 | 1245111.5849 | 2723954.1784 | 1245119.9771 | 2723955.9938 | 1245121.7165 | 2723956.7589 | 1245123.4451 | 2723957.3102 | 1245125.6362 | 2723958.3552 | 1245127.3484 | 2723960.3476 | 1245128.9358 | 2723963.3117 | 1245129.2425 | 2723965.7285 | 1245130.4162 | 2723981.7967 | 1245143.4631 | 2723980.2529 | 1245152.2271 | 2723980.0841 | 1245153.7916 | 2724001.6888 | 1245163.7628 | 2724004.565 | 1245167.1813 | 2724007.1265 | 1245169.0253 | 2724010.6372 | 1245171.3785 | 2724012.1952 | 1245172.7789 | 2724012.4491 | 1245174.0075 | 2724016.7399 | 1245175.5652 | 2724020.9952 | 1245176.2881 | 2724022.7361 | 1245176.1689 | 2724028.6618 | 1245183.0319 | 2724029.6762 | 1245185.1216 | 2724030.7598 | 1245189.3256 | 2724036.0989 | 1245189.9044 | 2724047.2337 | 1245189.8371 | 2724056.2876 | 1245189.1592 | 2724063.5345 | 1245188.1433 | 2724073.8223 | 1245187.013
90 | 2723696.4517 | 1244678.9126 | 2723691.7701 | 1244677.5917 | 2723692.4373 | 1244683.6552 | 2723700.0356 | 1244717.9871 | 2723708.9066 | 1244742.4039 | 2723718.6242 | 1244769.7074 | 2723732.4702 | 1244795.8628 | 2723751.4489 | 1244819.1006 | 2723777.356 | 1244840.6593 | 2723790.7208 | 1244856.1735 | 2723795.6506 | 1244867.3192 | 2723798.9639 | 1244892.165 | 2723799.7703 | 1244936.4304 | 2723779.7159 | 1244937.2237 | 2723732.3231 | 1244939.7817
91 | 2724053.0476 | 1245165.2045 | 2724055.3055 | 1245181.9103 | 2724056.2876 | 1245189.1592 | 2724063.5345 | 1245188.1433 | 2724073.8223 | 1245187.013
92 | 2724073.8223 | 1245187.013 | 2724084.9059 | 1245185.7982
93 | 2724073.2703 | 1245196.0536 | 2724072.8092 | 1245192.085 | 2724075.9373 | 1245191.7724 | 2724073.8223 | 1245187.013
94 | 2723696.4517 | 1244678.9126 | 2723703.2603 | 1244677.1976
95 | 2724073.2703 | 1245196.0536 | 2724082.7049 | 1245195.2391
96 | 2724047.9015 | 1245270.9644 | 2724044.1409 | 1245271.8866 | 2724026.4342 | 1245276.8428 | 2724004.2232 | 1245283.2283 | 2723992.7025 | 1245283.6879 | 2723983.5899 | 1245281.3954 | 2723977.0685 | 1245281.3369 | 2723973.5235 | 1245282.4304 | 2723959.7849 | 1245255.5871 | 2723953.4726 | 1245242.6331 | 2723951.4506 | 1245238.4874 | 2723950.1366 | 1245235.9022 | 2723940.1565 | 1245216.1769 | 2723938.3675 | 1245212.8144 | 2723936.9001 | 1245208.8916 | 2723936.6615 | 1245206.2065 | 2723936.6878 | 1245200.6134 | 2723938.631 | 1245195.5164 | 2723943.7068 | 1245189.1726 | 2723948.3491 | 1245185.1217 | 2723951.5253 | 1245183.2309 | 2723957.4952 | 1245179.6749 | 2723962.217 | 1245179.0508 | 2723967.1773 | 1245179.6772 | 2723969.2605 | 1245180.1767 | 2723993.217 | 1245188.6401 | 2724007.4397 | 1245193.4304 | 2724022.6596 | 1245197.1629 | 2724041.87 | 1245198.3767 | 2724055.5521 | 1245197.5732 | 2724066.1679 | 1245196.6611 | 2724073.2703 | 1245196.0536
97 | 2724047.9015 | 1245270.9644 | 2724051.5585 | 1245275.7116 | 2724057.1675 | 1245289.3447
98 | 2724131.9067 | 1245181.29 | 2724124.0179 | 1245181.9143 | 2724092.0503 | 1245184.9703 | 2724087.3676 | 1245185.5284
99 | 2724181.1434 | 1245178.3069 | 2724169.4843 | 1245179.9531 | 2724166.4091 | 1245179.5439 | 2724163.1835 | 1245178.3754 | 2724159.8738 | 1245176.1709 | 2724155.8669 | 1245180.5463 | 2724151.5263 | 1245183.5358 | 2724146.9506 | 1245185.1192 | 2724139.7473 | 1245186.2138 | 2724132.8583 | 1245186.7368 | 2724131.9067 | 1245181.29
100 | 2724131.9067 | 1245181.29 | 2724136.9081 | 1245179.9491 | 2724141.3596 | 1245177.4401 | 2724147.0809 | 1245173.8457 | 2724150.6224 | 1245170.7616 | 2724154.1507 | 1245167.2213 | 2724157.2976 | 1245164.2069 | 2724159.1051 | 1245160.1857 | 2724159.6804 | 1245156.5391 | 2724159.7396 | 1245155.5803
101 | 2724124.3821 | 1245130.2336 | 2724127.1914 | 1245139.011 | 2724128.0346 | 1245166.2406 | 2724128.6868 | 1245170.8248 | 2724130.1716 | 1245176.4385 | 2724131.9067 | 1245181.29
102 | 2724087.3676 | 1245185.5284 | 2724084.9059 | 1245185.7982
103 | 2724181.1434 | 1245178.3069 | 2724200.2125 | 1245175.4481 | 2724207.7764 | 1245173.7383 | 2724214.469 | 1245171.7657 | 2724220.1636 | 1245169.4496
104 | 2724181.1434 | 1245178.3069 | 2724184.1201 | 1245185.5865 | 2724186.6792 | 1245191.8676 | 2724192.1795 | 1245205.3164 | 2724192.4288 | 1245207.1232 | 2724196.0142 | 1245216.3727 | 2724200.1158 | 1245227.3124 | 2724200.2407 | 1245230.729 | 2724199.189 | 1245233.2718
105 | 2724124.3821 | 1245130.2336 | 2724120.1955 | 1245129.4787 | 2724117.3965 | 1245128.5082 | 2724114.5329 | 1245126.6578 | 2724107.1566 | 1245121.21 | 2724083.5689 | 1245100.1765 | 2724080.0611 | 1245096.429
106 | 2724220.1636 | 1245169.4496 | 2724232.277 | 1245196.2594 | 2724233.3345 | 1245198.7722
107 | 2724163.1987 | 1245249.4472 | 2724195.7978 | 1245237.5195 | 2724198.7678 | 1245234.2901 | 2724199.189 | 1245233.2718
108 | 2724053.0476 | 1245165.2045 | 2724048.7524 | 1245163.1351 | 2724053.3705 | 1245153.7459
109 | 2724053.0476 | 1245165.2045 | 2724060.1935 | 1245166.6023
110 | 2724057.1675 | 1245289.3447 | 2724059.8418 | 1245295.8447
111 | 2724082.2645 | 1245021.3156 | 2724084.1396 | 1245022.3668 | 2724087.0716 | 1245024.9303 | 2724098.7838 | 1245038.2779
112 | 2724078.3761 | 1245021.8347 | 2724080.3979 | 1245021.2987 | 2724082.2645 | 1245021.3156
113 | 2724082.2645 | 1245021.3156 | 2724094.7123 | 1245009.9446
114 | 2724078.3761 | 1245021.8347 | 2724053.2615 | 1245043.3944
115 | 2724094.7123 | 1245009.9446 | 2724096.9892 | 1245007.8647
116 | 2724107.8181 | 1245016.5498 | 2724099.7239 | 1245007.9917 | 2724097.6762 | 1245007.2371 | 2724096.9892 | 1245007.8647
117 | 2724067.1119 | 1245082.5951 | 2724080.0611 | 1245096.429
118 | 2724047.0174 | 1245015.2622 | 2724047.7187 | 1245019.3136 | 2724052.6357 | 1245036.0974 | 2724053.2615 | 1245043.3944
119 | 2724053.2615 | 1245043.3944 | 2724045.2337 | 1245050.288 | 2724044.6978 | 1245051.7002 | 2724044.5548 | 1245053.4765 | 2724044.9711 | 1245055.9762 | 2724046.3421 | 1245059.0853 | 2724049.1154 | 1245063.0911 | 2724051.6898 | 1245066.1253 | 2724058.1715 | 1245073.0473
120 | 2724067.1119 | 1245082.5951 | 2724058.1715 | 1245073.0473
121 | 2724163.1987 | 1245249.4472 | 2724168.568 | 1245273.48
122 | 2724168.568 | 1245273.48 | 2724174.1777 | 1245293.2476 | 2724175.7507 | 1245298.9743
123 | 2724168.568 | 1245273.48 | 2724206.9583 | 1245278.0543 | 2724219.1507 | 1245274.3264
124 | 2724047.0174 | 1245015.2622 | 2724046.6303 | 1245013.0189
125 | 2724049.1892 | 1244988.4182 | 2724052.864 | 1244989.7962 | 2724057.7743 | 1244991.7338
126 | 2724049.1892 | 1244988.4182 | 2724047.2095 | 1245000.8621
127 | 2724049.1892 | 1244988.4182 | 2724047.4182 | 1244976.2486 | 2724047.7654 | 1244970.424
128 | 2724121.6683 | 1244772.551 | 2724125.7696 | 1244779.9209
129 | 2724085.0011 | 1244804.6556 | 2724097.1988 | 1244792.8452 | 2724117.435 | 1244775.4538 | 2724119.5364 | 1244774.0077 | 2724121.6683 | 1244772.551
130 | 2724085.0011 | 1244804.6556 | 2724097.1988 | 1244792.8452 | 2724099.2441 | 1244808.8794 | 2724102.9387 | 1244809.6796 | 2724103.8268 | 1244819.2507 | 2724108.3468 | 1244819.2564 | 2724109.7448 | 1244834.7988
131 | 2724134.8949 | 1244885.9462 | 2724134.5521 | 1244879.2111
132 | 2724134.8949 | 1244885.9462 | 2724129.4219 | 1244888.8564 | 2724119.1682 | 1244893.746 | 2724110.9726 | 1244898.5341 | 2724105.1721 | 1244900.3067
133 | 2724142.2853 | 1244958.2522 | 2724128.7348 | 1244970.1448
134 | 2724125.7357 | 1244935.2322 | 2724105.8417 | 1244936.0644
135 | 2724239.2691 | 1245051.0061 | 2724241.1705 | 1245073.0632 | 2724240.559 | 1245077.3541 | 2724238.5937 | 1245082.0502 | 2724234.996 | 1245085.2887 | 2724230.3774 | 1245086.7488 | 2724226.0404 | 1245087.0506
136 | 2724109.7448 | 1244834.7988 | 2724107.4722 | 1244835.3962
137 | 2724109.7448 | 1244834.7988 | 2724109.904 | 1244837.2801
138 | 2724051.5788 | 1244933.5922 | 2724048.8276 | 1244952.6024 | 2724047.7654 | 1244970.424
139 | 2724100.6875 | 1244901.6772 | 2724099.8655 | 1244884.6189
140 | 2724100.6875 | 1244901.6772 | 2724105.1721 | 1244900.3067
141 | 2724077.3259 | 1244905.5474 | 2724100.6875 | 1244901.6772
142 | 2724086.9339 | 1244936.8553 | 2724105.8417 | 1244936.0644
143 | 2724086.7989 | 1244936.861 | 2724086.9339 | 1244936.8553
144 | 2724128.7348 | 1244970.1448 | 2724123.0073 | 1244975.1716
145 | 2724117.1811 | 1244980.2851 | 2724123.0073 | 1244975.1716
146 | 2724046.6303 | 1245013.0189 | 2724045.9254 | 1245008.934 | 2724047.2095 | 1245000.8621
147 | 2724236.7119 | 1245018.568 | 2724237.5529 | 1245031.0963 | 2724239.2691 | 1245051.0061
148 | 2724233.3345 | 1245198.7722 | 2724234.4878 | 1245201.5128
149 | 2724239.9926 | 1245214.6595 | 2724238.3679 | 1245210.7326 | 2724234.4878 | 1245201.5128
150 | 2724239.9926 | 1245214.6595 | 2724244.1229 | 1245224.6428 | 2724249.9194 | 1245237.3379
151 | 2724260.2349 | 1245260.9955 | 2724251.5156 | 1245240.8336 | 2724249.9194 | 1245237.3379

## bus_geodata
| x | y | coords
0 | 2724271.4529 | 1244457.2604
1 | 2724292.2326 | 1244429.4605
2 | 2724230.7418 | 1244510.712
3 | 2724309.2108 | 1244406.7464
4 | 2724163.3376 | 1244749.5702
5 | 2724322.1417 | 1244389.0747
6 | 2724301.0505 | 1244410.9649
7 | 2724330.8514 | 1244331.4126
8 | 2724138.3589 | 1244794.53
9 | 2724138.2882 | 1244776.9225
10 | 2724162.6228 | 1244885.0924
11 | 2724137.2042 | 1244807.8266
12 | 2724222.1273 | 1244571.8946
13 | 2724136.2957 | 1244762.5075
14 | 2724336.821 | 1244353.8679
15 | 2724334.7714 | 1244327.2468
16 | 2724132.6198 | 1244765.0293
17 | 2724142.7734 | 1244885.8332
18 | 2724161.8701 | 1244905.3169
19 | 2724161.6286 | 1244944.8223
20 | 2724154.9006 | 1244945.2263
21 | 2724161.7447 | 1244925.8404
22 | 2724161.1636 | 1245051.8145
23 | 2724165.9087 | 1245085.8094
24 | 2724194.3659 | 1245117.5654
25 | 2724180.0388 | 1245086.8575
26 | 2724137.0643 | 1244809.438
27 | 2724218.2438 | 1244579.0193
28 | 2724369.8451 | 1244350.0615
29 | 2724304.1963 | 1244703.6985
30 | 2724308.8227 | 1244735.3233
31 | 2724284.9819 | 1244696.2276
32 | 2724293.2934 | 1244754.062
33 | 2724323.3748 | 1244671.6668
34 | 2724322.2551 | 1244831.6764
35 | 2724327.9891 | 1244681.2383
36 | 2724308.2679 | 1245063.1913
37 | 2724303.8968 | 1245103.6962
38 | 2724297.6769 | 1245088.5824
39 | 2724273.8038 | 1245120.1201
40 | 2724305.9069 | 1245078.5463
41 | 2724258.9515 | 1245137.7906
42 | 2724363.8902 | 1245018.3315
43 | 2724239.6617 | 1245157.3032
44 | 2724269.2864 | 1245153.4651
45 | 2724252.8257 | 1245130.5486
46 | 2724383.2881 | 1245020.2965
47 | 2724238.7487 | 1245148.5767
48 | 2724226.239 | 1245166.4897
49 | 2724275.7076 | 1245164.1418
50 | 2724252.0952 | 1245129.6849
51 | 2724453.0424 | 1244343.4682
52 | 2724462.7624 | 1244460.3211
53 | 2724469.6927 | 1244251.9453
54 | 2724465.5209 | 1244244.6961
55 | 2724467.3576 | 1244260.9537
56 | 2724470.759 | 1244240.0465
57 | 2724434.8324 | 1244226.9826
58 | 2724465.5469 | 1244267.9386
59 | 2724480.5597 | 1244236.9939
60 | 2724317.4904 | 1244229.9355
61 | 2724438.3292 | 1244311.689
62 | 2724330.7906 | 1244305.3455
63 | 2724326.8826 | 1244283.8447
64 | 2724238.6496 | 1244246.5315
65 | 2724277.3542 | 1244243.4061
66 | 2724105.1662 | 1244099.4902
67 | 2724282.8127 | 1244263.3437
68 | 2724000.0389 | 1244052.0084
69 | 2724285.3955 | 1244280.6394
70 | 2724318.3911 | 1244234.9253
71 | 2724324.1887 | 1244267.8705
72 | 2724322.9346 | 1244284.2957
73 | 2724326.8077 | 1244306.4857
74 | 2724413.1232 | 1244322.9617
75 | 2724400.8068 | 1244336.4166
76 | 2723825.5028 | 1244700.5481
77 | 2723852.2078 | 1244945.6661
78 | 2723946.8722 | 1244786.2191
79 | 2723910.6937 | 1245053.5234
80 | 2723732.3231 | 1244939.7816
81 | 2723944.1348 | 1244765.7841
82 | 2723942.7389 | 1244983.5223
83 | 2724073.8223 | 1245187.013
84 | 2723696.4517 | 1244678.9126
85 | 2724073.2703 | 1245196.0536
86 | 2724082.7049 | 1245195.2391
87 | 2724047.9015 | 1245270.9644
88 | 2724131.9067 | 1245181.29
89 | 2724087.3676 | 1245185.5284
90 | 2724181.1434 | 1245178.3069
91 | 2724159.7396 | 1245155.5803
92 | 2724124.3821 | 1245130.2336
93 | 2724220.1636 | 1245169.4496
94 | 2724199.189 | 1245233.2718
95 | 2724084.9059 | 1245185.7982
96 | 2724053.0476 | 1245165.2045
97 | 2724053.3705 | 1245153.7459
98 | 2724060.1935 | 1245166.6023
99 | 2724057.1675 | 1245289.3447
100 | 2723703.2603 | 1244677.1976
101 | 2724098.7838 | 1245038.2779
102 | 2724082.2645 | 1245021.3156
103 | 2724078.3761 | 1245021.8347
104 | 2724094.7123 | 1245009.9446
105 | 2724107.8181 | 1245016.5498
106 | 2724096.9892 | 1245007.8647
107 | 2724080.0611 | 1245096.429
108 | 2724053.2615 | 1245043.3944
109 | 2724067.1119 | 1245082.5951
110 | 2724163.1987 | 1245249.4472
111 | 2724168.568 | 1245273.48
112 | 2724047.0174 | 1245015.2622
113 | 2724058.1715 | 1245073.0473
114 | 2724057.7743 | 1244991.7338
115 | 2724049.1892 | 1244988.4182
116 | 2724121.6683 | 1244772.551
117 | 2724125.7696 | 1244779.9209
118 | 2724085.0011 | 1244804.6556
119 | 2724134.8949 | 1244885.9462
120 | 2724142.2853 | 1244958.2522
121 | 2724125.7357 | 1244935.2322
122 | 2724226.0404 | 1245087.0506
123 | 2724109.7448 | 1244834.7988
124 | 2724107.4722 | 1244835.3962
125 | 2724109.904 | 1244837.2801
126 | 2724134.3512 | 1244818.0661
127 | 2724051.5788 | 1244933.5922
128 | 2724047.7654 | 1244970.424
129 | 2724099.8655 | 1244884.6189
130 | 2724100.6875 | 1244901.6772
131 | 2724105.1721 | 1244900.3067
132 | 2724077.3259 | 1244905.5474
133 | 2724134.5521 | 1244879.2111
134 | 2724086.9339 | 1244936.8553
135 | 2724105.8417 | 1244936.0644
136 | 2724086.7989 | 1244936.861
137 | 2724128.7348 | 1244970.1448
138 | 2724123.0073 | 1244975.1716
139 | 2724047.2095 | 1245000.8621
140 | 2724046.6303 | 1245013.0189
141 | 2724117.1811 | 1244980.2851
142 | 2724239.2691 | 1245051.0061
143 | 2724236.7119 | 1245018.568
144 | 2724175.7507 | 1245298.9743
145 | 2724219.1507 | 1245274.3264
146 | 2724233.3345 | 1245198.7722
147 | 2724282.2266 | 1245174.4739
148 | 2724059.8418 | 1245295.8447
149 | 2724234.4878 | 1245201.5128
150 | 2724239.9926 | 1245214.6595
151 | 2724249.9194 | 1245237.3379
152 | 2724260.2349 | 1245260.9955
153 | 2724162.6228 | 1244885.0924

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1