## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3544-17_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3544-17_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3544-17_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3544-17_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3544-17_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3544-17_0_2_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_3544-17_0_2_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_3544-17_0_2_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_3544-17_0_2_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_3544-17_0_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_3544-17_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_3544-17_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_3544-17_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_3544-17_0_2_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_3544-17_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_3544-17_0_2_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_3544-17_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_3544-17_0_2_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_3544-17_0_2_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_3544-17_0_2_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_3544-17_0_2_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_3544-17_0_2_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_3544-17_0_2_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_3544-17_0_2_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_3544-17_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_3544-17_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_3544-17_0_2_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_3544-17_0_2_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_3544-17_0_2_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_3544-17_0_2_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_3544-17_0_2_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_3544-17_0_2_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_3544-17_0_2_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_3544-17_0_2_node_32 | 0.4 | n |  | TRUE
34 | bus_MV_158_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3544-17_0_2_load_0 | 0 | 0.0021901 | 0.00054889 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3544-17_0_2_load_4 | 4 | 0.0053114 | 0.0013312 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3544-17_0_2_load_24 | 5 | 0.0039339 | 0.00098594 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3544-17_0_2_load_18 | 6 | 0.0031208 | 0.00078215 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3544-17_0_2_load_12 | 7 | 0.0038305 | 0.00096 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3544-17_0_2_load_16 | 8 | 0.0027203 | 0.00068178 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3544-17_0_2_load_5 | 10 | 0.0017846 | 0.00044726 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3544-17_0_2_load_6 | 11 | 0.0092833 | 0.0023266 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3544-17_0_2_load_7 | 12 | 0.013765 | 0.0034498 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3544-17_0_2_load_10 | 13 | 0.0034365 | 0.00086126 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3544-17_0_2_load_8 | 14 | 0.00167 | 0.00041854 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3544-17_0_2_load_9 | 15 | 0.0031289 | 0.00078419 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3544-17_0_2_load_11 | 16 | 0.0028683 | 0.00071887 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3544-17_0_2_load_21 | 17 | 0.003103 | 0.00077769 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3544-17_0_2_load_22 | 18 | 0.0011788 | 0.00029543 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3544-17_0_2_load_23 | 19 | 0.0045502 | 0.0011404 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3544-17_0_2_load_27 | 20 | 0.010971 | 0.0027495 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3544-17_0_2_load_14 | 21 | 0.0021318 | 0.00053427 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3544-17_0_2_load_15 | 22 | 0.0025557 | 0.00064052 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3544-17_0_2_load_17 | 23 | 0.0014461 | 0.00036241 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3544-17_0_2_load_19 | 24 | 0.0013926 | 0.00034902 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3544-17_0_2_load_20 | 25 | 0.0011633 | 0.00029154 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3544-17_0_2_load_28 | 28 | 0.015581 | 0.003905 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3544-17_0_2_load_31 | 29 | 0.0067591 | 0.001694 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3544-17_0_2_load_34 | 30 | 0.0055739 | 0.0013969 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3544-17_0_2_load_30 | 31 | 0.0066563 | 0.0016682 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3544-17_0_2_load_29 | 32 | 0.0074798 | 0.0018746 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3544-17_0_2_load_32 | 33 | 0.018161 | 0.0045516 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3544-17_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0091062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3544-17_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.006789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3544-17_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.002856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3544-17_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3544-17_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.012045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3544-17_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.016301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3544-17_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0079837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3544-17_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.012686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3544-17_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.00919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3544-17_0_2_line_9 | NAYY 4x150 SE | 8 | 21 | 0.0026809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3544-17_0_2_line_10 | NAYY 4x150 SE | 9 | 19 | 0.0004003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3544-17_0_2_line_11 | NAYY 4x150 SE | 9 | 18 | 0.012235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3544-17_0_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.074379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3544-17_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.011233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3544-17_0_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.021345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3544-17_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.0078811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3544-17_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.00041463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3544-17_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.014249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3544-17_0_2_line_18 | NAYY 4x150 SE | 16 | 17 | 0.015749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3544-17_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.010084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3544-17_0_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.002201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3544-17_0_2_line_21 | NAYY 4x150 SE | 20 | 28 | 0.015404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3544-17_0_2_line_22 | NAYY 4x150 SE | 21 | 22 | 0.0016562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3544-17_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.014988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3544-17_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.002605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3544-17_0_2_line_25 | NAYY 4x150 SE | 25 | 26 | 0.011083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3544-17_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.01789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3544-17_0_2_line_27 | NAYY 4x150 SE | 27 | 29 | 0.012489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3544-17_0_2_line_28 | NAYY 4x150 SE | 27 | 30 | 0.0081785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3544-17_0_2_line_29 | NAYY 4x150 SE | 28 | 32 | 0.0089002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3544-17_0_2_line_30 | NAYY 4x150 SE | 29 | 31 | 0.0034547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3544-17_0_2_line_31 | NAYY 4x150 SE | 30 | 32 | 0.0011715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3544-17_0_2_line_32 | NAYY 4x150 SE | 31 | 33 | 0.0051748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3544-17_0_2_trafo_28 | 0.25 MVA 20/0.4 kV | 34 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2776591.1389 | 1166825.9896 | 2776585.6331 | 1166818.7364
1 | 2776581.5283 | 1166813.3289 | 2776585.6331 | 1166818.7364
2 | 2776593.2712 | 1166824.0838 | 2776591.1389 | 1166825.9896
3 | 2776581.5283 | 1166813.3289 | 2776589.3856 | 1166803.4785
4 | 2776593.2712 | 1166824.0838 | 2776602.6119 | 1166816.4792
5 | 2776593.2712 | 1166824.0838 | 2776604.6426 | 1166835.7634
6 | 2776594.3641 | 1166797.2372 | 2776589.3856 | 1166803.4785
7 | 2776613.492 | 1166844.8528 | 2776613.492 | 1166844.8528 | 2776604.6426 | 1166835.7634
8 | 2776600.0948 | 1166790.0528 | 2776594.3641 | 1166797.2372
9 | 2776613.492 | 1166844.8528 | 2776615.3281 | 1166845.9855 | 2776615.8516 | 1166845.9885
10 | 2776600.0948 | 1166790.0528 | 2776600.4833 | 1166790.1493
11 | 2776600.0948 | 1166790.0528 | 2776588.2461 | 1166787.0017
12 | 2776562.2943 | 1166716.4184 | 2776568.7404 | 1166715.3848 | 2776603.9157 | 1166715.3627 | 2776607.3842 | 1166715.6982 | 2776610.0382 | 1166716.3768 | 2776612.3113 | 1166717.5002 | 2776613.9599 | 1166719.0167 | 2776615.2969 | 1166720.9689 | 2776616.1415 | 1166723.2514 | 2776616.4392 | 1166725.896 | 2776616.1242 | 1166728.7894 | 2776615.3185 | 1166730.6563 | 2776614.2127 | 1166732.3031 | 2776611.5699 | 1166734.8945 | 2776608.5645 | 1166736.8507
13 | 2776608.5645 | 1166736.8507 | 2776604.8835 | 1166739.2465 | 2776598.8812 | 1166742.5286
14 | 2776580.1535 | 1166752.7689 | 2776598.8812 | 1166742.5286
15 | 2776580.1535 | 1166752.7689 | 2776576.8198 | 1166754.5918 | 2776573.7304 | 1166757.259 | 2776573.7304 | 1166757.259
16 | 2776573.7304 | 1166757.259 | 2776573.4932 | 1166757.5991
17 | 2776573.4932 | 1166757.5991 | 2776571.9146 | 1166759.8636 | 2776571.0134 | 1166762.3728 | 2776570.6691 | 1166765.7436 | 2776570.8311 | 1166771.1756
18 | 2776578.7767 | 1166783.6028 | 2776576.4077 | 1166782.4165 | 2776574.3457 | 1166780.8878 | 2776572.9839 | 1166779.2574 | 2776572.1432 | 1166777.3643 | 2776571.4075 | 1166774.7625 | 2776570.8311 | 1166771.1756 | 2776570.8311 | 1166771.1756
19 | 2776578.7767 | 1166783.6028 | 2776580.7491 | 1166784.5905 | 2776587.0768 | 1166786.7006 | 2776588.2461 | 1166787.0017
20 | 2776602.6194 | 1166790.68 | 2776600.4833 | 1166790.1493
21 | 2776602.6194 | 1166790.68 | 2776605.2745 | 1166791.3396 | 2776610.7955 | 1166791.7021 | 2776616.3916 | 1166791.3329 | 2776617.9084 | 1166791.1543
22 | 2776615.8516 | 1166845.9885 | 2776617.2049 | 1166845.9963 | 2776617.4829 | 1166845.8763
23 | 2776625.4715 | 1166833.7627 | 2776622.0989 | 1166841.6249 | 2776620.8163 | 1166843.5557 | 2776618.9664 | 1166845.2362 | 2776617.4829 | 1166845.8763
24 | 2776629.798 | 1166811.8231 | 2776628.0908 | 1166809.8553
25 | 2776620.8279 | 1166801.4837 | 2776628.0908 | 1166809.8553
26 | 2776635.878 | 1166791.7504 | 2776620.8279 | 1166801.4837
27 | 2776635.878 | 1166791.7504 | 2776636.3458 | 1166790.1738 | 2776637.2569 | 1166788.6324 | 2776639.4722 | 1166786.2509 | 2776643.7778 | 1166782.3623
28 | 2776635.878 | 1166791.7504 | 2776630.0262 | 1166790.1324 | 2776627.919 | 1166790.1205
29 | 2776626.7476 | 1166790.1139 | 2776626.7476 | 1166790.1139 | 2776617.9084 | 1166791.1543
30 | 2776646.3199 | 1166780.023 | 2776644.1709 | 1166782.0073 | 2776643.7778 | 1166782.3623
31 | 2776626.7476 | 1166790.1139 | 2776627.919 | 1166790.1205
32 | 2776646.3199 | 1166780.023 | 2776650.1218 | 1166776.5123

## bus_geodata
| x | y | coords
0 | 2776585.6331 | 1166818.7364
1 | 2776591.1389 | 1166825.9896
2 | 2776581.5283 | 1166813.3289
3 | 2776593.2712 | 1166824.0838
4 | 2776589.3856 | 1166803.4785
5 | 2776602.6119 | 1166816.4792
6 | 2776604.6426 | 1166835.7634
7 | 2776594.3641 | 1166797.2372
8 | 2776613.492 | 1166844.8528
9 | 2776600.0948 | 1166790.0528
10 | 2776562.2943 | 1166716.4184
11 | 2776608.5645 | 1166736.8507
12 | 2776598.8812 | 1166742.5286
13 | 2776580.1535 | 1166752.7689
14 | 2776573.7304 | 1166757.259
15 | 2776573.4932 | 1166757.5991
16 | 2776570.8311 | 1166771.1756
17 | 2776578.7767 | 1166783.6028
18 | 2776588.2461 | 1166787.0017
19 | 2776600.4833 | 1166790.1493
20 | 2776602.6194 | 1166790.68
21 | 2776615.8516 | 1166845.9885
22 | 2776617.4829 | 1166845.8763
23 | 2776625.4715 | 1166833.7627
24 | 2776629.798 | 1166811.8231
25 | 2776628.0908 | 1166809.8553
26 | 2776620.8279 | 1166801.4837
27 | 2776635.878 | 1166791.7504
28 | 2776617.9084 | 1166791.1543
29 | 2776643.7778 | 1166782.3623
30 | 2776627.919 | 1166790.1205
31 | 2776646.3199 | 1166780.023
32 | 2776626.7476 | 1166790.1139
33 | 2776650.1218 | 1166776.5123
34 | 2776600.0948 | 1166790.0528

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1