## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3582-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3582-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3582-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3582-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3582-4_0_2_node_58 | 0.4 | n |  | TRUE
5 | bus_LV_3582-4_0_2_node_61 | 0.4 | n |  | TRUE
6 | bus_LV_3582-4_0_2_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_3582-4_0_2_node_60 | 0.4 | n |  | TRUE
8 | bus_LV_3582-4_0_2_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_3582-4_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_3582-4_0_2_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_3582-4_0_2_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_3582-4_0_2_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_3582-4_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_3582-4_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_3582-4_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_3582-4_0_2_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_3582-4_0_2_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_3582-4_0_2_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_3582-4_0_2_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_3582-4_0_2_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_3582-4_0_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_3582-4_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_3582-4_0_2_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_3582-4_0_2_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_3582-4_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_3582-4_0_2_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_3582-4_0_2_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_3582-4_0_2_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_3582-4_0_2_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_3582-4_0_2_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_3582-4_0_2_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_3582-4_0_2_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_3582-4_0_2_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_3582-4_0_2_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_3582-4_0_2_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_3582-4_0_2_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_3582-4_0_2_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_3582-4_0_2_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_3582-4_0_2_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_3582-4_0_2_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_3582-4_0_2_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_3582-4_0_2_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_3582-4_0_2_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_3582-4_0_2_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_3582-4_0_2_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_3582-4_0_2_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_3582-4_0_2_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_3582-4_0_2_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_3582-4_0_2_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_3582-4_0_2_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_3582-4_0_2_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_3582-4_0_2_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_3582-4_0_2_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_3582-4_0_2_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_3582-4_0_2_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_3582-4_0_2_node_75 | 0.4 | n |  | TRUE
57 | bus_LV_3582-4_0_2_node_73 | 0.4 | n |  | TRUE
58 | bus_LV_3582-4_0_2_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_3582-4_0_2_node_68 | 0.4 | n |  | TRUE
60 | bus_LV_3582-4_0_2_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_3582-4_0_2_node_83 | 0.4 | n |  | TRUE
62 | bus_LV_3582-4_0_2_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_3582-4_0_2_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_3582-4_0_2_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_3582-4_0_2_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_3582-4_0_2_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_3582-4_0_2_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_3582-4_0_2_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_3582-4_0_2_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_3582-4_0_2_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_3582-4_0_2_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_3582-4_0_2_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_3582-4_0_2_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_3582-4_0_2_node_81 | 0.4 | n |  | TRUE
75 | bus_LV_3582-4_0_2_node_82 | 0.4 | n |  | TRUE
76 | bus_LV_3582-4_0_2_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_3582-4_0_2_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_3582-4_0_2_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_3582-4_0_2_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_3582-4_0_2_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_3582-4_0_2_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_3582-4_0_2_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_3582-4_0_2_node_79 | 0.4 | n |  | TRUE
84 | bus_MV_161_0_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3582-4_0_2_load_0 | 0 | 0.0010725 | 0.0002688 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3582-4_0_2_load_2 | 2 | 0.0018981 | 0.0004757 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3582-4_0_2_load_3 | 3 | 0.0019789 | 0.00049595 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3582-4_0_2_load_58 | 4 | 0.0019003 | 0.00047627 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3582-4_0_2_load_61 | 5 | 0.0022564 | 0.00056551 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3582-4_0_2_load_39 | 6 | 0.0019959 | 0.00050022 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3582-4_0_2_load_4 | 8 | 0.0030118 | 0.00075483 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3582-4_0_2_load_5 | 9 | 0.0024659 | 0.00061802 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3582-4_0_2_load_7 | 10 | 0.001313 | 0.00032908 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3582-4_0_2_load_11 | 11 | 0.0064773 | 0.0016234 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3582-4_0_2_load_12 | 12 | 0.0052877 | 0.0013252 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3582-4_0_2_load_8 | 13 | 0.0031328 | 0.00078514 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3582-4_0_2_load_9 | 14 | 0.0028091 | 0.00070403 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3582-4_0_2_load_10 | 15 | 0.0034368 | 0.00086135 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3582-4_0_2_load_13 | 16 | 0.0023039 | 0.00057741 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3582-4_0_2_load_30 | 17 | 0.0029549 | 0.00074058 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3582-4_0_2_load_41 | 19 | 0.0022953 | 0.00057526 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3582-4_0_2_load_42 | 20 | 0.003441 | 0.0008624 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3582-4_0_2_load_40 | 21 | 0.0031649 | 0.0007932 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3582-4_0_2_load_16 | 22 | 0.0020582 | 0.00051584 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3582-4_0_2_load_15 | 23 | 0.004659 | 0.0011677 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3582-4_0_2_load_14 | 24 | 0.0022707 | 0.00056909 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3582-4_0_2_load_17 | 25 | 0.0053915 | 0.0013512 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3582-4_0_2_load_27 | 26 | 0.0018522 | 0.0004642 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3582-4_0_2_load_28 | 27 | 0.0054714 | 0.0013713 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3582-4_0_2_load_21 | 29 | 0.0036698 | 0.00091973 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3582-4_0_2_load_22 | 30 | 0.0061477 | 0.0015408 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3582-4_0_2_load_23 | 32 | 0.004037 | 0.0010118 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3582-4_0_2_load_25 | 33 | 0.0033916 | 0.00085002 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3582-4_0_2_load_24 | 34 | 0.0023656 | 0.00059288 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3582-4_0_2_load_51 | 35 | 0.0018185 | 0.00045577 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3582-4_0_2_load_49 | 36 | 0.0029855 | 0.00074823 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3582-4_0_2_load_26 | 37 | 0.0038113 | 0.00095521 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3582-4_0_2_load_29 | 38 | 0.0022748 | 0.00057012 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3582-4_0_2_load_33 | 39 | 0.0026376 | 0.00066104 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3582-4_0_2_load_32 | 40 | 0.0025506 | 0.00063923 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3582-4_0_2_load_36 | 41 | 0.00077064 | 0.00019314 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3582-4_0_2_load_34 | 42 | 0.0023879 | 0.00059847 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3582-4_0_2_load_35 | 43 | 0.0012478 | 0.00031273 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3582-4_0_2_load_37 | 44 | 0.0027488 | 0.00068892 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3582-4_0_2_load_44 | 45 | 0.002603 | 0.00065236 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3582-4_0_2_load_45 | 46 | 0.0018436 | 0.00046205 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3582-4_0_2_load_43 | 47 | 0.0017759 | 0.00044507 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3582-4_0_2_load_38 | 48 | 0.0016806 | 0.00042121 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3582-4_0_2_load_46 | 49 | 0.001087 | 0.00027244 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3582-4_0_2_load_47 | 50 | 0.0028403 | 0.00071184 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3582-4_0_2_load_53 | 51 | 0.00088634 | 0.00022214 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3582-4_0_2_load_54 | 52 | 0.0010025 | 0.00025125 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3582-4_0_2_load_48 | 53 | 0.0080554 | 0.0020189 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3582-4_0_2_load_52 | 55 | 0.0051854 | 0.0012996 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3582-4_0_2_load_75 | 56 | 0.0026118 | 0.00065458 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3582-4_0_2_load_73 | 57 | 0.0058198 | 0.0014586 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3582-4_0_2_load_70 | 58 | 0.0014598 | 0.00036585 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3582-4_0_2_load_68 | 59 | 0.0026384 | 0.00066125 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3582-4_0_2_load_85 | 60 | 0.0019442 | 0.00048727 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3582-4_0_2_load_83 | 61 | 0.0037557 | 0.00094126 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3582-4_0_2_load_55 | 62 | 0.0014969 | 0.00037517 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3582-4_0_2_load_56 | 63 | 0.0027193 | 0.00068153 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3582-4_0_2_load_57 | 64 | 0.002273 | 0.00056968 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3582-4_0_2_load_59 | 65 | 0.00079393 | 0.00019898 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3582-4_0_2_load_62 | 66 | 0.0022707 | 0.00056909 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3582-4_0_2_load_63 | 67 | 0.0020555 | 0.00051515 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3582-4_0_2_load_64 | 68 | 0.0018132 | 0.00045443 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3582-4_0_2_load_65 | 69 | 0.0022852 | 0.00057272 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3582-4_0_2_load_71 | 70 | 0.00096237 | 0.00024119 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3582-4_0_2_load_66 | 72 | 0.0011098 | 0.00027814 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3582-4_0_2_load_67 | 73 | 0.0011076 | 0.00027759 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3582-4_0_2_load_81 | 74 | 0.0017839 | 0.00044708 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3582-4_0_2_load_82 | 75 | 0.002846 | 0.00071328 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3582-4_0_2_load_84 | 76 | 0.0019589 | 0.00049095 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3582-4_0_2_load_74 | 77 | 0.0064625 | 0.0016197 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3582-4_0_2_load_76 | 78 | 0.0061544 | 0.0015424 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3582-4_0_2_load_72 | 79 | 0.0015809 | 0.0003962 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3582-4_0_2_load_77 | 81 | 0.0024897 | 0.00062398 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3582-4_0_2_load_78 | 82 | 0.0022378 | 0.00056084 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3582-4_0_2_load_79 | 83 | 0.0019152 | 0.00048 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3582-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0047684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3582-4_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.028065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3582-4_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.037225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3582-4_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3582-4_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0014852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3582-4_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0074767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3582-4_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.013849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3582-4_0_2_line_7 | NAYY 4x150 SE | 6 | 48 | 0.018833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3582-4_0_2_line_8 | NAYY 4x150 SE | 7 | 66 | 0.0024803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_3582-4_0_2_line_9 | NAYY 4x150 SE | 7 | 65 | 0.025084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_3582-4_0_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.0078047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3582-4_0_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.0082549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3582-4_0_2_line_12 | NAYY 4x150 SE | 10 | 13 | 0.013289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3582-4_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.034065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3582-4_0_2_line_14 | NAYY 4x150 SE | 12 | 16 | 0.02294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3582-4_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.02554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3582-4_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.013562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3582-4_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0012806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3582-4_0_2_line_18 | NAYY 4x150 SE | 16 | 24 | 0.014353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3582-4_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0092725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3582-4_0_2_line_20 | NAYY 4x150 SE | 18 | 40 | 0.0098868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3582-4_0_2_line_21 | NAYY 4x150 SE | 18 | 39 | 0.011879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3582-4_0_2_line_22 | NAYY 4x150 SE | 19 | 20 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_3582-4_0_2_line_23 | NAYY 4x150 SE | 19 | 21 | 0.010942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_3582-4_0_2_line_24 | NAYY 4x150 SE | 20 | 47 | 0.0043373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_3582-4_0_2_line_25 | NAYY 4x150 SE | 21 | 38 | 0.049854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3582-4_0_2_line_26 | NAYY 4x150 SE | 21 | 37 | 0.014612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_3582-4_0_2_line_27 | NAYY 4x150 SE | 22 | 23 | 0.045152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3582-4_0_2_line_28 | NAYY 4x150 SE | 23 | 25 | 0.023024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3582-4_0_2_line_29 | NAYY 4x150 SE | 24 | 28 | 0.00182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3582-4_0_2_line_30 | NAYY 4x150 SE | 25 | 31 | 0.0082145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3582-4_0_2_line_31 | NAYY 4x150 SE | 26 | 27 | 0.0041949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3582-4_0_2_line_32 | NAYY 4x150 SE | 27 | 38 | 0.018406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3582-4_0_2_line_33 | NAYY 4x150 SE | 28 | 29 | 0.028749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_3582-4_0_2_line_34 | NAYY 4x150 SE | 28 | 30 | 0.013843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3582-4_0_2_line_35 | NAYY 4x150 SE | 28 | 31 | 0.073534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3582-4_0_2_line_36 | NAYY 4x150 SE | 29 | 32 | 0.016604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_3582-4_0_2_line_37 | NAYY 4x150 SE | 30 | 33 | 0.014642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3582-4_0_2_line_38 | NAYY 4x150 SE | 32 | 34 | 0.016487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_3582-4_0_2_line_39 | NAYY 4x150 SE | 34 | 35 | 0.0013272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_3582-4_0_2_line_40 | NAYY 4x150 SE | 35 | 36 | 0.0089703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_3582-4_0_2_line_41 | NAYY 4x150 SE | 36 | 53 | 0.012645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_3582-4_0_2_line_42 | NAYY 4x150 SE | 38 | 39 | 0.0087757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3582-4_0_2_line_43 | NAYY 4x150 SE | 40 | 41 | 0.0067313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3582-4_0_2_line_44 | NAYY 4x150 SE | 41 | 42 | 0.0057098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3582-4_0_2_line_45 | NAYY 4x150 SE | 42 | 43 | 0.011133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3582-4_0_2_line_46 | NAYY 4x150 SE | 43 | 44 | 0.0037651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3582-4_0_2_line_47 | NAYY 4x150 SE | 45 | 46 | 0.0052388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_3582-4_0_2_line_48 | NAYY 4x150 SE | 45 | 47 | 0.0053363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_3582-4_0_2_line_49 | NAYY 4x150 SE | 46 | 49 | 0.014982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_3582-4_0_2_line_50 | NAYY 4x150 SE | 49 | 50 | 0.0047173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_3582-4_0_2_line_51 | NAYY 4x150 SE | 50 | 51 | 0.0021385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_3582-4_0_2_line_52 | NAYY 4x150 SE | 51 | 52 | 0.0069748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_3582-4_0_2_line_53 | NAYY 4x150 SE | 52 | 62 | 0.0028903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_3582-4_0_2_line_54 | NAYY 4x150 SE | 53 | 54 | 0.0018422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_3582-4_0_2_line_55 | NAYY 4x150 SE | 54 | 55 | 0.015414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_3582-4_0_2_line_56 | NAYY 4x150 SE | 55 | 58 | 0.012441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_3582-4_0_2_line_57 | NAYY 4x150 SE | 56 | 57 | 0.034857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3582-4_0_2_line_58 | NAYY 4x150 SE | 57 | 60 | 0.053583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3582-4_0_2_line_59 | NAYY 4x150 SE | 57 | 79 | 0.0047847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3582-4_0_2_line_60 | NAYY 4x150 SE | 58 | 59 | 0.012541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_3582-4_0_2_line_61 | NAYY 4x150 SE | 59 | 72 | 0.001736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_3582-4_0_2_line_62 | NAYY 4x150 SE | 60 | 61 | 0.014918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3582-4_0_2_line_63 | NAYY 4x150 SE | 61 | 75 | 0.019658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3582-4_0_2_line_64 | NAYY 4x150 SE | 62 | 63 | 0.012688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
65 | LV_3582-4_0_2_line_65 | NAYY 4x150 SE | 63 | 64 | 0.0056948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
66 | LV_3582-4_0_2_line_66 | NAYY 4x150 SE | 64 | 65 | 0.009091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_3582-4_0_2_line_67 | NAYY 4x150 SE | 66 | 67 | 0.010679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_3582-4_0_2_line_68 | NAYY 4x150 SE | 67 | 68 | 0.020575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_3582-4_0_2_line_69 | NAYY 4x150 SE | 68 | 69 | 0.0054807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
70 | LV_3582-4_0_2_line_70 | NAYY 4x150 SE | 69 | 70 | 0.02018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_3582-4_0_2_line_71 | NAYY 4x150 SE | 70 | 71 | 0.0080029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
72 | LV_3582-4_0_2_line_72 | NAYY 4x150 SE | 71 | 74 | 0.027978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
73 | LV_3582-4_0_2_line_73 | NAYY 4x150 SE | 71 | 73 | 0.016821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
74 | LV_3582-4_0_2_line_74 | NAYY 4x150 SE | 72 | 73 | 0.013617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
75 | LV_3582-4_0_2_line_75 | NAYY 4x150 SE | 74 | 83 | 0.017965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3582-4_0_2_line_76 | NAYY 4x150 SE | 75 | 76 | 0.047577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3582-4_0_2_line_77 | NAYY 4x150 SE | 77 | 78 | 0.025568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3582-4_0_2_line_78 | NAYY 4x150 SE | 77 | 79 | 0.032838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3582-4_0_2_line_79 | NAYY 4x150 SE | 78 | 80 | 0.032638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3582-4_0_2_line_80 | NAYY 4x150 SE | 80 | 82 | 0.0046394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3582-4_0_2_line_81 | NAYY 4x150 SE | 81 | 82 | 0.0067979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3582-4_0_2_line_82 | NAYY 4x150 SE | 81 | 83 | 0.013395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3582-4_0_2_trafo_26 | 0.25 MVA 20/0.4 kV | 84 | 37 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2737143.7869 | 1183416.0848 | 2737148.5406 | 1183416.4591
1 | 2737143.7869 | 1183416.0848 | 2737115.8411 | 1183413.5025
2 | 2737143.7869 | 1183416.0848 | 2737145.4561 | 1183453.272
3 | 2737101.1578 | 1183412.1458 | 2737115.8411 | 1183413.5025
4 | 2737145.5227 | 1183454.7558 | 2737145.4561 | 1183453.272
5 | 2737093.7128 | 1183411.4578 | 2737093.7128 | 1183411.4578 | 2737101.1578 | 1183412.1458
6 | 2737146.1436 | 1183468.5904 | 2737145.5227 | 1183454.7558
7 | 2737075.3793 | 1183407.1506 | 2737093.7128 | 1183411.4578
8 | 2737146.1436 | 1183468.5904 | 2737146.2032 | 1183471.07
9 | 2737146.1436 | 1183468.5904 | 2737121.1189 | 1183466.8738
10 | 2736913.1275 | 1183484.6209 | 2736920.8258 | 1183483.337
11 | 2736920.8258 | 1183483.337 | 2736928.9682 | 1183481.979
12 | 2736928.9682 | 1183481.979 | 2736942.0757 | 1183479.793
13 | 2736917.8843 | 1183537.004 | 2736931.3073 | 1183535.8967 | 2736949.7288 | 1183538.2528 | 2736951.6746 | 1183538.8117
14 | 2736973.7235 | 1183545.1447 | 2736951.6746 | 1183538.8117
15 | 2736966.0749 | 1183471.856 | 2736953.7682 | 1183477.8429 | 2736942.0757 | 1183479.793
16 | 2736978.27 | 1183465.9235 | 2736966.0749 | 1183471.856
17 | 2736978.27 | 1183465.9235 | 2736979.4216 | 1183465.3633
18 | 2736973.7235 | 1183545.1447 | 2736987.5192 | 1183549.1072
19 | 2736987.7598 | 1183461.307 | 2736979.4216 | 1183465.3633
20 | 2736987.7598 | 1183461.307 | 2736989.8374 | 1183460.2981 | 2736994.6666 | 1183454.4593
21 | 2736987.7598 | 1183461.307 | 2736992.006 | 1183472.4014
22 | 2737043.687 | 1183481.6143 | 2737048.7212 | 1183473.4323 | 2737052.8687 | 1183471.1953
23 | 2737040.909 | 1183491.8425 | 2737041.1851 | 1183485.6805 | 2737043.687 | 1183481.6143
24 | 2737054.7539 | 1183467.3709 | 2737053.1909 | 1183471.0215 | 2737052.8687 | 1183471.1953
25 | 2737040.909 | 1183491.8425 | 2736992.2256 | 1183481.1021
26 | 2737040.909 | 1183491.8425 | 2737040.2549 | 1183506.4398
27 | 2736941.3649 | 1183615.1082 | 2736932.415 | 1183613.7155 | 2736911.7045 | 1183611.2738 | 2736896.4964 | 1183610.281
28 | 2736941.3649 | 1183615.1082 | 2736943.8077 | 1183615.4883 | 2736955.9735 | 1183617.857 | 2736963.9698 | 1183619.4693
29 | 2736989.2684 | 1183549.6097 | 2736987.5192 | 1183549.1072
30 | 2736972.0222 | 1183621.0929 | 2736963.9698 | 1183619.4693
31 | 2736973.0014 | 1183492.2145 | 2736976.8405 | 1183490.5238
32 | 2736992.2256 | 1183481.1021 | 2736988.3608 | 1183485.4505 | 2736976.8405 | 1183490.5238
33 | 2736989.2684 | 1183549.6097 | 2737017.9744 | 1183548.045
34 | 2736989.2684 | 1183549.6097 | 2736999.6347 | 1183540.4348
35 | 2736989.2684 | 1183549.6097 | 2736972.0222 | 1183621.0929
36 | 2737017.9744 | 1183548.045 | 2737034.5541 | 1183547.1412
37 | 2736999.6347 | 1183540.4348 | 2737010.5989 | 1183530.7309
38 | 2737051.0167 | 1183546.2439 | 2737034.5541 | 1183547.1412
39 | 2737051.0167 | 1183546.2439 | 2737052.3419 | 1183546.1716
40 | 2737061.2989 | 1183545.6834 | 2737052.3419 | 1183546.1716
41 | 2737073.9254 | 1183544.9951 | 2737061.2989 | 1183545.6834
42 | 2736992.006 | 1183472.4014 | 2736992.401 | 1183473.4335 | 2736992.2256 | 1183481.1021 | 2736992.2256 | 1183481.1021
43 | 2736994.6666 | 1183454.4593 | 2736998.4935 | 1183449.8324 | 2736998.7644 | 1183449.158
44 | 2737000.8926 | 1183443.8596 | 2736998.7644 | 1183449.158
45 | 2737000.8926 | 1183443.8596 | 2737003.6364 | 1183437.0289 | 2737005.7675 | 1183433.9167
46 | 2737005.7675 | 1183433.9167 | 2737007.8947 | 1183430.8101
47 | 2737056.8543 | 1183462.4653 | 2737062.0808 | 1183462.8239
48 | 2737056.8543 | 1183462.4653 | 2737056.8543 | 1183462.4653 | 2737054.7539 | 1183467.3709
49 | 2737062.0808 | 1183462.8239 | 2737077.0274 | 1183463.8492
50 | 2737077.0274 | 1183463.8492 | 2737081.7337 | 1183464.172
51 | 2737083.8672 | 1183464.3184 | 2737081.7337 | 1183464.172
52 | 2737090.8256 | 1183464.7957 | 2737083.8672 | 1183464.3184
53 | 2737090.8256 | 1183464.7957 | 2737093.7092 | 1183464.9935
54 | 2737075.7649 | 1183544.8949 | 2737073.9254 | 1183544.9951
55 | 2737075.7649 | 1183544.8949 | 2737091.0385 | 1183542.8206
56 | 2737091.0385 | 1183542.8206 | 2737103.3668 | 1183541.1463
57 | 2737074.6106 | 1183600.5355 | 2737093.3141 | 1183600.3614 | 2737109.3139 | 1183598.1415
58 | 2737109.3139 | 1183598.1415 | 2737098.9357 | 1183650.7098
59 | 2737114.0532 | 1183597.484 | 2737109.3139 | 1183598.1415
60 | 2737115.7939 | 1183539.4587 | 2737103.3668 | 1183541.1463
61 | 2737117.5142 | 1183539.225 | 2737115.7939 | 1183539.4587
62 | 2737113.4601 | 1183654.1121 | 2737098.9357 | 1183650.7098
63 | 2737132.6 | 1183658.5955 | 2737113.4601 | 1183654.1121
64 | 2737093.7092 | 1183464.9935 | 2737106.3679 | 1183465.8619
65 | 2737112.0493 | 1183466.2516 | 2737106.3679 | 1183465.8619
66 | 2737112.0493 | 1183466.2516 | 2737121.1189 | 1183466.8738
67 | 2737146.4597 | 1183481.7459 | 2737146.2032 | 1183471.07
68 | 2737146.4597 | 1183481.7459 | 2737146.954 | 1183502.3147
69 | 2737146.954 | 1183502.3147 | 2737147.0856 | 1183507.7938
70 | 2737147.5703 | 1183527.9679 | 2737147.0856 | 1183507.7938
71 | 2737147.7626 | 1183535.9685 | 2737147.5703 | 1183527.9679
72 | 2737147.7626 | 1183535.9685 | 2737141.8683 | 1183563.3183
73 | 2737147.7626 | 1183535.9685 | 2737134.0605 | 1183536.9779 | 2737131.0072 | 1183537.3926
74 | 2737117.5142 | 1183539.225 | 2737131.0072 | 1183537.3926
75 | 2737141.8683 | 1183563.3183 | 2737159.8313 | 1183563.5965
76 | 2737132.6 | 1183658.5955 | 2737150.7453 | 1183662.8459 | 2737164.9715 | 1183665.6181 | 2737179.247 | 1183667.8349
77 | 2737146.5798 | 1183592.9711 | 2737171.905 | 1183589.4574
78 | 2737114.0532 | 1183597.484 | 2737146.5798 | 1183592.9711
79 | 2737183.8166 | 1183567.4402 | 2737186.2349 | 1183571.5654 | 2737187.2086 | 1183576.069 | 2737187.0343 | 1183580.6796 | 2737185.3411 | 1183584.2436 | 2737181.4503 | 1183587.0568 | 2737176.2078 | 1183588.8604 | 2737171.905 | 1183589.4574
80 | 2737183.8166 | 1183567.4402 | 2737179.9101 | 1183564.9377
81 | 2737173.2249 | 1183563.804 | 2737174.4442 | 1183563.8229 | 2737179.9101 | 1183564.9377 | 2737179.9101 | 1183564.9377
82 | 2737173.2249 | 1183563.804 | 2737159.8313 | 1183563.5965

## bus_geodata
| x | y | coords
0 | 2737148.5406 | 1183416.4591
1 | 2737143.7869 | 1183416.0848
2 | 2737115.8411 | 1183413.5025
3 | 2737145.4561 | 1183453.272
4 | 2737101.1578 | 1183412.1458
5 | 2737145.5227 | 1183454.7558
6 | 2737093.7128 | 1183411.4578
7 | 2737146.1436 | 1183468.5904
8 | 2736913.1275 | 1183484.6209
9 | 2736920.8258 | 1183483.337
10 | 2736928.9682 | 1183481.979
11 | 2736917.8843 | 1183537.004
12 | 2736951.6746 | 1183538.8117
13 | 2736942.0757 | 1183479.793
14 | 2736966.0749 | 1183471.856
15 | 2736978.27 | 1183465.9235
16 | 2736973.7235 | 1183545.1447
17 | 2736979.4216 | 1183465.3633
18 | 2736987.7598 | 1183461.307
19 | 2737043.687 | 1183481.6143
20 | 2737052.8687 | 1183471.1953
21 | 2737040.909 | 1183491.8425
22 | 2736896.4964 | 1183610.281
23 | 2736941.3649 | 1183615.1082
24 | 2736987.5192 | 1183549.1072
25 | 2736963.9698 | 1183619.4693
26 | 2736973.0014 | 1183492.2145
27 | 2736976.8405 | 1183490.5238
28 | 2736989.2684 | 1183549.6097
29 | 2737017.9744 | 1183548.045
30 | 2736999.6347 | 1183540.4348
31 | 2736972.0222 | 1183621.0929
32 | 2737034.5541 | 1183547.1412
33 | 2737010.5989 | 1183530.7309
34 | 2737051.0167 | 1183546.2439
35 | 2737052.3419 | 1183546.1716
36 | 2737061.2989 | 1183545.6834
37 | 2737040.2549 | 1183506.4398
38 | 2736992.2256 | 1183481.1021
39 | 2736992.006 | 1183472.4014
40 | 2736994.6666 | 1183454.4593
41 | 2736998.7644 | 1183449.158
42 | 2737000.8926 | 1183443.8596
43 | 2737005.7675 | 1183433.9167
44 | 2737007.8947 | 1183430.8101
45 | 2737056.8543 | 1183462.4653
46 | 2737062.0808 | 1183462.8239
47 | 2737054.7539 | 1183467.3709
48 | 2737075.3793 | 1183407.1506
49 | 2737077.0274 | 1183463.8492
50 | 2737081.7337 | 1183464.172
51 | 2737083.8672 | 1183464.3184
52 | 2737090.8256 | 1183464.7957
53 | 2737073.9254 | 1183544.9951
54 | 2737075.7649 | 1183544.8949
55 | 2737091.0385 | 1183542.8206
56 | 2737074.6106 | 1183600.5355
57 | 2737109.3139 | 1183598.1415
58 | 2737103.3668 | 1183541.1463
59 | 2737115.7939 | 1183539.4587
60 | 2737098.9357 | 1183650.7098
61 | 2737113.4601 | 1183654.1121
62 | 2737093.7092 | 1183464.9935
63 | 2737106.3679 | 1183465.8619
64 | 2737112.0493 | 1183466.2516
65 | 2737121.1189 | 1183466.8738
66 | 2737146.2032 | 1183471.07
67 | 2737146.4597 | 1183481.7459
68 | 2737146.954 | 1183502.3147
69 | 2737147.0856 | 1183507.7938
70 | 2737147.5703 | 1183527.9679
71 | 2737147.7626 | 1183535.9685
72 | 2737117.5142 | 1183539.225
73 | 2737131.0072 | 1183537.3926
74 | 2737141.8683 | 1183563.3183
75 | 2737132.6 | 1183658.5955
76 | 2737179.247 | 1183667.8349
77 | 2737146.5798 | 1183592.9711
78 | 2737171.905 | 1183589.4574
79 | 2737114.0532 | 1183597.484
80 | 2737183.8166 | 1183567.4402
81 | 2737173.2249 | 1183563.804
82 | 2737179.9101 | 1183564.9377
83 | 2737159.8313 | 1183563.5965
84 | 2736989.2684 | 1183549.6097

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1