## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3619-15_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3619-15_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3619-15_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3619-15_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3619-15_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3619-15_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3619-15_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3619-15_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_3619-15_0_6_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_3619-15_0_6_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_3619-15_0_6_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_3619-15_0_6_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_3619-15_0_6_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_3619-15_0_6_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_3619-15_0_6_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_3619-15_0_6_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_3619-15_0_6_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_3619-15_0_6_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_3619-15_0_6_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_3619-15_0_6_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_3619-15_0_6_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_3619-15_0_6_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_3619-15_0_6_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_3619-15_0_6_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_3619-15_0_6_node_166 | 0.4 | n |  | TRUE
25 | bus_LV_3619-15_0_6_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_3619-15_0_6_node_165 | 0.4 | n |  | TRUE
27 | bus_LV_3619-15_0_6_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_3619-15_0_6_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_3619-15_0_6_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_3619-15_0_6_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_3619-15_0_6_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_3619-15_0_6_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_3619-15_0_6_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_3619-15_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_3619-15_0_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_3619-15_0_6_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_3619-15_0_6_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_3619-15_0_6_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_3619-15_0_6_node_116 | 0.4 | n |  | TRUE
40 | bus_LV_3619-15_0_6_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_3619-15_0_6_node_113 | 0.4 | n |  | TRUE
42 | bus_LV_3619-15_0_6_node_118 | 0.4 | n |  | TRUE
43 | bus_LV_3619-15_0_6_node_119 | 0.4 | n |  | TRUE
44 | bus_LV_3619-15_0_6_node_109 | 0.4 | n |  | TRUE
45 | bus_LV_3619-15_0_6_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_3619-15_0_6_node_149 | 0.4 | n |  | TRUE
47 | bus_LV_3619-15_0_6_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_3619-15_0_6_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_3619-15_0_6_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_3619-15_0_6_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_3619-15_0_6_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_3619-15_0_6_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_3619-15_0_6_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_3619-15_0_6_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_3619-15_0_6_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_3619-15_0_6_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_3619-15_0_6_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_3619-15_0_6_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_3619-15_0_6_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_3619-15_0_6_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_3619-15_0_6_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_3619-15_0_6_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_3619-15_0_6_node_137 | 0.4 | n |  | TRUE
64 | bus_LV_3619-15_0_6_node_136 | 0.4 | n |  | TRUE
65 | bus_LV_3619-15_0_6_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_3619-15_0_6_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_3619-15_0_6_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_3619-15_0_6_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_3619-15_0_6_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_3619-15_0_6_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_3619-15_0_6_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_3619-15_0_6_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_3619-15_0_6_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_3619-15_0_6_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_3619-15_0_6_node_86 | 0.4 | n |  | TRUE
76 | bus_LV_3619-15_0_6_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_3619-15_0_6_node_87 | 0.4 | n |  | TRUE
78 | bus_LV_3619-15_0_6_node_88 | 0.4 | n |  | TRUE
79 | bus_LV_3619-15_0_6_node_89 | 0.4 | n |  | TRUE
80 | bus_LV_3619-15_0_6_node_90 | 0.4 | n |  | TRUE
81 | bus_LV_3619-15_0_6_node_91 | 0.4 | n |  | TRUE
82 | bus_LV_3619-15_0_6_node_138 | 0.4 | n |  | TRUE
83 | bus_LV_3619-15_0_6_node_139 | 0.4 | n |  | TRUE
84 | bus_LV_3619-15_0_6_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_3619-15_0_6_node_82 | 0.4 | n |  | TRUE
86 | bus_LV_3619-15_0_6_node_148 | 0.4 | n |  | TRUE
87 | bus_LV_3619-15_0_6_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_3619-15_0_6_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_3619-15_0_6_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_3619-15_0_6_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_3619-15_0_6_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_3619-15_0_6_node_67 | 0.4 | n |  | TRUE
93 | bus_LV_3619-15_0_6_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_3619-15_0_6_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_3619-15_0_6_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_3619-15_0_6_node_71 | 0.4 | n |  | TRUE
97 | bus_LV_3619-15_0_6_node_159 | 0.4 | n |  | TRUE
98 | bus_LV_3619-15_0_6_node_72 | 0.4 | n |  | TRUE
99 | bus_LV_3619-15_0_6_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_3619-15_0_6_node_158 | 0.4 | n |  | TRUE
101 | bus_LV_3619-15_0_6_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_3619-15_0_6_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_3619-15_0_6_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_3619-15_0_6_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_3619-15_0_6_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_3619-15_0_6_node_83 | 0.4 | n |  | TRUE
107 | bus_LV_3619-15_0_6_node_167 | 0.4 | n |  | TRUE
108 | bus_LV_3619-15_0_6_node_168 | 0.4 | n |  | TRUE
109 | bus_LV_3619-15_0_6_node_143 | 0.4 | n |  | TRUE
110 | bus_LV_3619-15_0_6_node_145 | 0.4 | n |  | TRUE
111 | bus_LV_3619-15_0_6_node_146 | 0.4 | n |  | TRUE
112 | bus_LV_3619-15_0_6_node_147 | 0.4 | n |  | TRUE
113 | bus_LV_3619-15_0_6_node_92 | 0.4 | n |  | TRUE
114 | bus_LV_3619-15_0_6_node_93 | 0.4 | n |  | TRUE
115 | bus_LV_3619-15_0_6_node_94 | 0.4 | n |  | TRUE
116 | bus_LV_3619-15_0_6_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_3619-15_0_6_node_125 | 0.4 | n |  | TRUE
118 | bus_LV_3619-15_0_6_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_3619-15_0_6_node_126 | 0.4 | n |  | TRUE
120 | bus_LV_3619-15_0_6_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_3619-15_0_6_node_96 | 0.4 | n |  | TRUE
122 | bus_LV_3619-15_0_6_node_97 | 0.4 | n |  | TRUE
123 | bus_LV_3619-15_0_6_node_98 | 0.4 | n |  | TRUE
124 | bus_LV_3619-15_0_6_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_3619-15_0_6_node_101 | 0.4 | n |  | TRUE
126 | bus_LV_3619-15_0_6_node_99 | 0.4 | n |  | TRUE
127 | bus_LV_3619-15_0_6_node_102 | 0.4 | n |  | TRUE
128 | bus_LV_3619-15_0_6_node_103 | 0.4 | n |  | TRUE
129 | bus_LV_3619-15_0_6_node_105 | 0.4 | n |  | TRUE
130 | bus_LV_3619-15_0_6_node_104 | 0.4 | n |  | TRUE
131 | bus_LV_3619-15_0_6_node_106 | 0.4 | n |  | TRUE
132 | bus_LV_3619-15_0_6_node_107 | 0.4 | n |  | TRUE
133 | bus_LV_3619-15_0_6_node_108 | 0.4 | n |  | TRUE
134 | bus_LV_3619-15_0_6_node_110 | 0.4 | n |  | TRUE
135 | bus_LV_3619-15_0_6_node_111 | 0.4 | n |  | TRUE
136 | bus_LV_3619-15_0_6_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_3619-15_0_6_node_121 | 0.4 | n |  | TRUE
138 | bus_LV_3619-15_0_6_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_3619-15_0_6_node_122 | 0.4 | n |  | TRUE
140 | bus_LV_3619-15_0_6_node_123 | 0.4 | n |  | TRUE
141 | bus_LV_3619-15_0_6_node_124 | 0.4 | n |  | TRUE
142 | bus_LV_3619-15_0_6_node_127 | 0.4 | n |  | TRUE
143 | bus_LV_3619-15_0_6_node_128 | 0.4 | n |  | TRUE
144 | bus_LV_3619-15_0_6_node_131 | 0.4 | n |  | TRUE
145 | bus_LV_3619-15_0_6_node_129 | 0.4 | n |  | TRUE
146 | bus_LV_3619-15_0_6_node_130 | 0.4 | n |  | TRUE
147 | bus_LV_3619-15_0_6_node_132 | 0.4 | n |  | TRUE
148 | bus_LV_3619-15_0_6_node_133 | 0.4 | n |  | TRUE
149 | bus_LV_3619-15_0_6_node_134 | 0.4 | n |  | TRUE
150 | bus_LV_3619-15_0_6_node_135 | 0.4 | n |  | TRUE
151 | bus_LV_3619-15_0_6_node_141 | 0.4 | n |  | TRUE
152 | bus_LV_3619-15_0_6_node_142 | 0.4 | n |  | TRUE
153 | bus_LV_3619-15_0_6_node_150 | 0.4 | n |  | TRUE
154 | bus_LV_3619-15_0_6_node_152 | 0.4 | n |  | TRUE
155 | bus_LV_3619-15_0_6_node_154 | 0.4 | n |  | TRUE
156 | bus_LV_3619-15_0_6_node_169 | 0.4 | n |  | TRUE
157 | bus_LV_3619-15_0_6_node_164 | 0.4 | n |  | TRUE
158 | bus_LV_3619-15_0_6_node_156 | 0.4 | n |  | TRUE
159 | bus_LV_3619-15_0_6_node_153 | 0.4 | n |  | TRUE
160 | bus_LV_3619-15_0_6_node_161 | 0.4 | n |  | TRUE
161 | bus_LV_3619-15_0_6_node_155 | 0.4 | n |  | TRUE
162 | bus_LV_3619-15_0_6_node_163 | 0.4 | n |  | TRUE
163 | bus_LV_3619-15_0_6_node_162 | 0.4 | n |  | TRUE
164 | bus_LV_3619-15_0_6_node_160 | 0.4 | n |  | TRUE
165 | bus_LV_3619-15_0_6_node_157 | 0.4 | n |  | TRUE
166 | bus_MV_161_0_node_228 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3619-15_0_6_load_0 | 0 | 0.00092694 | 0.00023231 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3619-15_0_6_load_1 | 1 | 0.0013143 | 0.0003294 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3619-15_0_6_load_3 | 3 | 0.0018764 | 0.00047028 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3619-15_0_6_load_4 | 4 | 0.00081218 | 0.00020355 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3619-15_0_6_load_8 | 8 | 8.8952e-05 | 2.2293e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3619-15_0_6_load_9 | 9 | 0.00049143 | 0.00012316 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3619-15_0_6_load_10 | 10 | 0.0020615 | 0.00051666 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3619-15_0_6_load_11 | 11 | 0.00077408 | 0.000194 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3619-15_0_6_load_13 | 12 | 0.00021272 | 5.3313e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3619-15_0_6_load_18 | 14 | 0.001104 | 0.00027668 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3619-15_0_6_load_15 | 15 | 0.00014547 | 3.6459e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3619-15_0_6_load_16 | 16 | 0.00014958 | 3.7488e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3619-15_0_6_load_17 | 17 | 0.00011941 | 2.9927e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3619-15_0_6_load_19 | 18 | 0.0014855 | 0.0003723 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3619-15_0_6_load_27 | 19 | 0.0010027 | 0.00025129 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3619-15_0_6_load_29 | 20 | 0.0054001 | 0.0013534 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3619-15_0_6_load_28 | 21 | 0.010488 | 0.0026286 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3619-15_0_6_load_21 | 23 | 0.00023055 | 5.7782e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3619-15_0_6_load_166 | 24 | 0.00011409 | 2.8595e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3619-15_0_6_load_165 | 26 | 6.1577e-05 | 1.5433e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3619-15_0_6_load_20 | 27 | 0.00051706 | 0.00012959 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3619-15_0_6_load_35 | 29 | 0.0017646 | 0.00044225 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3619-15_0_6_load_36 | 30 | 0.0011154 | 0.00027953 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3619-15_0_6_load_37 | 31 | 0.0008145 | 0.00020413 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3619-15_0_6_load_23 | 32 | 0.010457 | 0.0026207 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3619-15_0_6_load_24 | 33 | 0.00024433 | 6.1236e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3619-15_0_6_load_25 | 34 | 0.0012707 | 0.00031847 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3619-15_0_6_load_62 | 37 | 0.00014301 | 3.5843e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3619-15_0_6_load_116 | 39 | 0.00033171 | 8.3135e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3619-15_0_6_load_117 | 40 | 0.0019031 | 0.00047697 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3619-15_0_6_load_113 | 41 | 0.001543 | 0.00038672 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3619-15_0_6_load_118 | 42 | 0.0061627 | 0.0015445 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3619-15_0_6_load_119 | 43 | 0.0014527 | 0.00036409 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3619-15_0_6_load_33 | 45 | 0.0008703 | 0.00021812 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3619-15_0_6_load_149 | 46 | 0.00047008 | 0.00011781 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3619-15_0_6_load_42 | 47 | 0.0016251 | 0.00040728 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3619-15_0_6_load_38 | 48 | 0.00042321 | 0.00010607 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3619-15_0_6_load_43 | 49 | 0.0011162 | 0.00027973 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3619-15_0_6_load_39 | 50 | 0.0022567 | 0.00056558 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3619-15_0_6_load_40 | 51 | 0.0058277 | 0.0014606 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3619-15_0_6_load_51 | 53 | 0.0022114 | 0.00055422 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3619-15_0_6_load_52 | 54 | 0.0011247 | 0.00028188 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3619-15_0_6_load_53 | 55 | 0.0013643 | 0.00034193 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3619-15_0_6_load_46 | 58 | 0.0018356 | 0.00046005 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3619-15_0_6_load_45 | 59 | 0.00061937 | 0.00015523 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3619-15_0_6_load_47 | 60 | 0.0012892 | 0.0003231 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3619-15_0_6_load_48 | 61 | 0.0027589 | 0.00069143 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3619-15_0_6_load_49 | 62 | 0.0027155 | 0.00068056 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3619-15_0_6_load_137 | 63 | 0.0035721 | 0.00089526 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3619-15_0_6_load_136 | 64 | 0.0034725 | 0.00087029 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3619-15_0_6_load_57 | 65 | 0.0012315 | 0.00030863 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3619-15_0_6_load_58 | 66 | 0.0014367 | 0.00036007 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3619-15_0_6_load_54 | 67 | 0.0012039 | 0.00030174 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3619-15_0_6_load_55 | 68 | 0.0011705 | 0.00029337 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3619-15_0_6_load_56 | 69 | 0.0010157 | 0.00025455 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3619-15_0_6_load_78 | 70 | 0.0012015 | 0.00030114 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3619-15_0_6_load_65 | 71 | 0.001694 | 0.00042457 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3619-15_0_6_load_59 | 72 | 0.0015374 | 0.00038531 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3619-15_0_6_load_60 | 73 | 0.0010898 | 0.00027312 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3619-15_0_6_load_61 | 74 | 0.0018054 | 0.00045248 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3619-15_0_6_load_88 | 78 | 9.4174e-05 | 2.3602e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3619-15_0_6_load_89 | 79 | 9.4169e-05 | 2.3601e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3619-15_0_6_load_90 | 80 | 8.7827e-05 | 2.2011e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3619-15_0_6_load_91 | 81 | 0.00014376 | 3.603e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3619-15_0_6_load_138 | 82 | 0.00087845 | 0.00022016 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3619-15_0_6_load_85 | 84 | 0.00063293 | 0.00015863 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3619-15_0_6_load_82 | 85 | 0.00098744 | 0.00024748 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3619-15_0_6_load_63 | 87 | 0.0016863 | 0.00042263 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3619-15_0_6_load_66 | 89 | 0.00082438 | 0.00020661 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3619-15_0_6_load_75 | 90 | 0.0011423 | 0.00028629 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3619-15_0_6_load_74 | 91 | 0.00057128 | 0.00014318 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3619-15_0_6_load_67 | 92 | 0.00042703 | 0.00010702 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3619-15_0_6_load_68 | 93 | 0.0010795 | 0.00027056 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3619-15_0_6_load_69 | 94 | 0.0011076 | 0.00027759 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3619-15_0_6_load_70 | 95 | 0.00084551 | 0.0002119 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3619-15_0_6_load_71 | 96 | 0.00098806 | 0.00024763 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3619-15_0_6_load_72 | 98 | 0.0013381 | 0.00033537 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3619-15_0_6_load_73 | 99 | 0.00075721 | 0.00018977 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3619-15_0_6_load_158 | 100 | 0.00096863 | 0.00024276 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3619-15_0_6_load_76 | 101 | 0.001101 | 0.00027593 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3619-15_0_6_load_77 | 102 | 0.00080347 | 0.00020137 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3619-15_0_6_load_83 | 106 | 0.00049025 | 0.00012287 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3619-15_0_6_load_167 | 107 | 0.0006581 | 0.00016494 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3619-15_0_6_load_168 | 108 | 0.00065523 | 0.00016422 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3619-15_0_6_load_143 | 109 | 9.6214e-05 | 2.4113e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3619-15_0_6_load_145 | 110 | 0.00012662 | 3.1735e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3619-15_0_6_load_146 | 111 | 0.00015304 | 3.8355e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3619-15_0_6_load_147 | 112 | 0.0001128 | 2.8272e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3619-15_0_6_load_92 | 113 | 0.0026385 | 0.00066127 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3619-15_0_6_load_93 | 114 | 0.0033564 | 0.0008412 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3619-15_0_6_load_94 | 115 | 0.0033944 | 0.00085071 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3619-15_0_6_load_125 | 117 | 0.0029789 | 0.00074658 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3619-15_0_6_load_115 | 118 | 0.0036002 | 0.00090231 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3619-15_0_6_load_126 | 119 | 0.0069802 | 0.0017494 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3619-15_0_6_load_114 | 120 | 0.0028896 | 0.00072421 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3619-15_0_6_load_96 | 121 | 0.00041187 | 0.00010322 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3619-15_0_6_load_97 | 122 | 0.00068423 | 0.00017148 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3619-15_0_6_load_100 | 124 | 0.00097913 | 0.00024539 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3619-15_0_6_load_101 | 125 | 0.00095382 | 0.00023905 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3619-15_0_6_load_102 | 127 | 0.00057981 | 0.00014531 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3619-15_0_6_load_103 | 128 | 0.00048229 | 0.00012087 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3619-15_0_6_load_104 | 130 | 0.00079158 | 0.00019839 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3619-15_0_6_load_106 | 131 | 0.00064233 | 0.00016098 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3619-15_0_6_load_107 | 132 | 0.0006148 | 0.00015408 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3619-15_0_6_load_108 | 133 | 0.00096246 | 0.00024121 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3619-15_0_6_load_110 | 134 | 0.00097106 | 0.00024337 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3619-15_0_6_load_111 | 135 | 0.00074571 | 0.00018689 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3619-15_0_6_load_112 | 136 | 0.00061644 | 0.00015449 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3619-15_0_6_load_121 | 137 | 0.0060837 | 0.0015247 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3619-15_0_6_load_120 | 138 | 0.0009857 | 0.00024704 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3619-15_0_6_load_122 | 139 | 0.0042253 | 0.001059 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3619-15_0_6_load_123 | 140 | 0.003823 | 0.00095813 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3619-15_0_6_load_124 | 141 | 0.0044452 | 0.0011141 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3619-15_0_6_load_128 | 143 | 0.0046007 | 0.001153 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3619-15_0_6_load_131 | 144 | 0.0077596 | 0.0019448 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3619-15_0_6_load_129 | 145 | 0.0031212 | 0.00078225 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3619-15_0_6_load_130 | 146 | 0.0031321 | 0.00078499 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3619-15_0_6_load_132 | 147 | 0.008904 | 0.0022315 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3619-15_0_6_load_133 | 148 | 0.0030924 | 0.00077503 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3619-15_0_6_load_134 | 149 | 0.0060488 | 0.001516 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3619-15_0_6_load_135 | 150 | 0.0044755 | 0.0011217 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3619-15_0_6_load_142 | 152 | 0.00047203 | 0.0001183 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3619-15_0_6_load_150 | 153 | 0.0014655 | 0.00036729 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_3619-15_0_6_load_152 | 154 | 0.00261 | 0.00065412 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_3619-15_0_6_load_154 | 155 | 0.00080441 | 0.0002016 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_3619-15_0_6_load_169 | 156 | 0.00060627 | 0.00015195 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_3619-15_0_6_load_164 | 157 | 0.00060798 | 0.00015237 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_3619-15_0_6_load_156 | 158 | 0.0012719 | 0.00031877 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_3619-15_0_6_load_153 | 159 | 0.00098122 | 0.00024592 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_3619-15_0_6_load_161 | 160 | 0.0011451 | 0.00028698 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_3619-15_0_6_load_155 | 161 | 0.00076079 | 0.00019067 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_3619-15_0_6_load_163 | 162 | 0.0023465 | 0.00058808 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_3619-15_0_6_load_162 | 163 | 0.0015277 | 0.00038289 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_3619-15_0_6_load_160 | 164 | 0.0016759 | 0.00042002 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_3619-15_0_6_load_157 | 165 | 0.0013122 | 0.00032887 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3619-15_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3619-15_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.039522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3619-15_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.017679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3619-15_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3619-15_0_6_line_4 | NAYY 4x150 SE | 2 | 5 | 0.007241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3619-15_0_6_line_5 | NAYY 4x150 SE | 3 | 6 | 0.037689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3619-15_0_6_line_6 | NAYY 4x150 SE | 4 | 7 | 0.017779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3619-15_0_6_line_7 | NAYY 4x150 SE | 5 | 8 | 0.037015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3619-15_0_6_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0089437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3619-15_0_6_line_9 | NAYY 4x150 SE | 6 | 10 | 0.032928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3619-15_0_6_line_10 | NAYY 4x150 SE | 6 | 11 | 0.029673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3619-15_0_6_line_11 | NAYY 4x150 SE | 7 | 12 | 0.10618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3619-15_0_6_line_12 | NAYY 4x150 SE | 7 | 13 | 0.038725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3619-15_0_6_line_13 | NAYY 4x150 SE | 9 | 14 | 0.050263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3619-15_0_6_line_14 | NAYY 4x150 SE | 12 | 15 | 0.019238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3619-15_0_6_line_15 | NAYY 4x150 SE | 13 | 16 | 0.015202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3619-15_0_6_line_16 | NAYY 4x150 SE | 13 | 17 | 0.13014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3619-15_0_6_line_17 | NAYY 4x150 SE | 14 | 18 | 0.059809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3619-15_0_6_line_18 | NAYY 4x150 SE | 15 | 23 | 0.040045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3619-15_0_6_line_19 | NAYY 4x150 SE | 17 | 24 | 0.046137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3619-15_0_6_line_20 | NAYY 4x150 SE | 18 | 27 | 0.057044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3619-15_0_6_line_21 | NAYY 4x150 SE | 19 | 20 | 0.042863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3619-15_0_6_line_22 | NAYY 4x150 SE | 20 | 29 | 0.020489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3619-15_0_6_line_23 | NAYY 4x150 SE | 21 | 22 | 0.11364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3619-15_0_6_line_24 | NAYY 4x150 SE | 22 | 39 | 0.020393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3619-15_0_6_line_25 | NAYY 4x150 SE | 22 | 40 | 0.0084026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_3619-15_0_6_line_26 | NAYY 4x150 SE | 22 | 41 | 0.036865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3619-15_0_6_line_27 | NAYY 4x150 SE | 23 | 25 | 0.082914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3619-15_0_6_line_28 | NAYY 4x150 SE | 24 | 26 | 0.01026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3619-15_0_6_line_29 | NAYY 4x150 SE | 25 | 32 | 0.096975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3619-15_0_6_line_30 | NAYY 4x150 SE | 25 | 33 | 0.11362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3619-15_0_6_line_31 | NAYY 4x150 SE | 25 | 34 | 0.11137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3619-15_0_6_line_32 | NAYY 4x150 SE | 27 | 28 | 0.017147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3619-15_0_6_line_33 | NAYY 4x150 SE | 28 | 29 | 0.011375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3619-15_0_6_line_34 | NAYY 4x150 SE | 28 | 30 | 0.012999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_3619-15_0_6_line_35 | NAYY 4x150 SE | 28 | 31 | 0.010769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_3619-15_0_6_line_36 | NAYY 4x150 SE | 30 | 47 | 0.018399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_3619-15_0_6_line_37 | NAYY 4x150 SE | 31 | 48 | 0.014812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_3619-15_0_6_line_38 | NAYY 4x150 SE | 33 | 35 | 0.086093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3619-15_0_6_line_39 | NAYY 4x150 SE | 35 | 36 | 0.020801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3619-15_0_6_line_40 | NAYY 4x150 SE | 36 | 37 | 0.031307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3619-15_0_6_line_41 | NAYY 4x150 SE | 36 | 38 | 0.10364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3619-15_0_6_line_42 | NAYY 4x150 SE | 37 | 46 | 0.035366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3619-15_0_6_line_43 | NAYY 4x150 SE | 38 | 45 | 0.058047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3619-15_0_6_line_44 | NAYY 4x150 SE | 39 | 42 | 0.0098339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3619-15_0_6_line_45 | NAYY 4x150 SE | 40 | 43 | 0.0013785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_3619-15_0_6_line_46 | NAYY 4x150 SE | 41 | 44 | 0.010422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3619-15_0_6_line_47 | NAYY 4x150 SE | 42 | 137 | 0.024104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3619-15_0_6_line_48 | NAYY 4x150 SE | 43 | 64 | 0.0085683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_3619-15_0_6_line_49 | NAYY 4x150 SE | 44 | 134 | 0.01622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3619-15_0_6_line_50 | NAYY 4x150 SE | 44 | 132 | 0.018734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3619-15_0_6_line_51 | NAYY 4x150 SE | 46 | 86 | 0.065134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3619-15_0_6_line_52 | NAYY 4x150 SE | 47 | 49 | 0.029958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_3619-15_0_6_line_53 | NAYY 4x150 SE | 48 | 50 | 0.0162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_3619-15_0_6_line_54 | NAYY 4x150 SE | 49 | 57 | 0.088681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_3619-15_0_6_line_55 | NAYY 4x150 SE | 50 | 51 | 0.052923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_3619-15_0_6_line_56 | NAYY 4x150 SE | 51 | 52 | 0.012401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_3619-15_0_6_line_57 | NAYY 4x150 SE | 52 | 53 | 0.020749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_3619-15_0_6_line_58 | NAYY 4x150 SE | 52 | 54 | 0.0069847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3619-15_0_6_line_59 | NAYY 4x150 SE | 53 | 55 | 0.025484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_3619-15_0_6_line_60 | NAYY 4x150 SE | 54 | 56 | 0.0041109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3619-15_0_6_line_61 | NAYY 4x150 SE | 55 | 67 | 0.020857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_3619-15_0_6_line_62 | NAYY 4x150 SE | 56 | 65 | 0.013049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3619-15_0_6_line_63 | NAYY 4x150 SE | 56 | 62 | 0.035915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3619-15_0_6_line_64 | NAYY 4x150 SE | 57 | 58 | 0.077306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_3619-15_0_6_line_65 | NAYY 4x150 SE | 58 | 61 | 0.051118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_3619-15_0_6_line_66 | NAYY 4x150 SE | 59 | 60 | 0.032747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3619-15_0_6_line_67 | NAYY 4x150 SE | 60 | 62 | 0.0085849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3619-15_0_6_line_68 | NAYY 4x150 SE | 61 | 63 | 0.011577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_3619-15_0_6_line_69 | NAYY 4x150 SE | 63 | 64 | 0.018895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_3619-15_0_6_line_70 | NAYY 4x150 SE | 65 | 66 | 0.037752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3619-15_0_6_line_71 | NAYY 4x150 SE | 66 | 72 | 0.033983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3619-15_0_6_line_72 | NAYY 4x150 SE | 67 | 68 | 6.0929e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_3619-15_0_6_line_73 | NAYY 4x150 SE | 68 | 69 | 0.0047247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_3619-15_0_6_line_74 | NAYY 4x150 SE | 69 | 70 | 0.013853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_3619-15_0_6_line_75 | NAYY 4x150 SE | 70 | 71 | 0.0066381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_3619-15_0_6_line_76 | NAYY 4x150 SE | 71 | 88 | 0.0071063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_3619-15_0_6_line_77 | NAYY 4x150 SE | 73 | 74 | 0.012115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3619-15_0_6_line_78 | NAYY 4x150 SE | 73 | 75 | 0.10105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3619-15_0_6_line_79 | NAYY 4x150 SE | 74 | 76 | 0.015002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3619-15_0_6_line_80 | NAYY 4x150 SE | 75 | 77 | 0.07689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3619-15_0_6_line_81 | NAYY 4x150 SE | 75 | 78 | 0.011849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3619-15_0_6_line_82 | NAYY 4x150 SE | 76 | 84 | 0.0071867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3619-15_0_6_line_83 | NAYY 4x150 SE | 76 | 85 | 0.0022522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3619-15_0_6_line_84 | NAYY 4x150 SE | 77 | 79 | 0.073158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3619-15_0_6_line_85 | NAYY 4x150 SE | 77 | 80 | 0.0037058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_3619-15_0_6_line_86 | NAYY 4x150 SE | 78 | 81 | 0.03244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3619-15_0_6_line_87 | NAYY 4x150 SE | 79 | 109 | 0.03492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3619-15_0_6_line_88 | NAYY 4x150 SE | 81 | 82 | 0.0022854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3619-15_0_6_line_89 | NAYY 4x150 SE | 82 | 83 | 0.062462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3619-15_0_6_line_90 | NAYY 4x150 SE | 83 | 151 | 0.051321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3619-15_0_6_line_91 | NAYY 4x150 SE | 85 | 104 | 0.030193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_3619-15_0_6_line_92 | NAYY 4x150 SE | 86 | 111 | 0.02823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3619-15_0_6_line_93 | NAYY 4x150 SE | 87 | 88 | 0.011543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3619-15_0_6_line_94 | NAYY 4x150 SE | 88 | 89 | 0.020078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_3619-15_0_6_line_95 | NAYY 4x150 SE | 89 | 90 | 0.0060276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_3619-15_0_6_line_96 | NAYY 4x150 SE | 90 | 91 | 0.009607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_3619-15_0_6_line_97 | NAYY 4x150 SE | 91 | 99 | 0.021663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_3619-15_0_6_line_98 | NAYY 4x150 SE | 92 | 93 | 0.0061173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_3619-15_0_6_line_99 | NAYY 4x150 SE | 92 | 94 | 0.012497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_3619-15_0_6_line_100 | NAYY 4x150 SE | 93 | 95 | 0.042887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_3619-15_0_6_line_101 | NAYY 4x150 SE | 94 | 96 | 0.0020958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_3619-15_0_6_line_102 | NAYY 4x150 SE | 94 | 97 | 0.09153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3619-15_0_6_line_103 | NAYY 4x150 SE | 95 | 98 | 0.057295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_3619-15_0_6_line_104 | NAYY 4x150 SE | 96 | 99 | 0.033571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_3619-15_0_6_line_105 | NAYY 4x150 SE | 97 | 100 | 0.066176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3619-15_0_6_line_106 | NAYY 4x150 SE | 98 | 101 | 0.025458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_3619-15_0_6_line_107 | NAYY 4x150 SE | 101 | 102 | 0.03004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_3619-15_0_6_line_108 | NAYY 4x150 SE | 102 | 103 | 0.018814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_3619-15_0_6_line_109 | NAYY 4x150 SE | 103 | 104 | 0.066613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3619-15_0_6_line_110 | NAYY 4x150 SE | 103 | 105 | 0.021113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_3619-15_0_6_line_111 | NAYY 4x150 SE | 105 | 106 | 0.11191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_3619-15_0_6_line_112 | NAYY 4x150 SE | 106 | 107 | 0.011276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
113 | LV_3619-15_0_6_line_113 | NAYY 4x150 SE | 107 | 108 | 0.01065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_3619-15_0_6_line_114 | NAYY 4x150 SE | 108 | 157 | 0.36095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_3619-15_0_6_line_115 | NAYY 4x150 SE | 110 | 111 | 0.043145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3619-15_0_6_line_116 | NAYY 4x150 SE | 110 | 112 | 0.015803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3619-15_0_6_line_117 | NAYY 4x150 SE | 113 | 114 | 0.14105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3619-15_0_6_line_118 | NAYY 4x150 SE | 114 | 115 | 0.015843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3619-15_0_6_line_119 | NAYY 4x150 SE | 115 | 116 | 0.013866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3619-15_0_6_line_120 | NAYY 4x150 SE | 116 | 117 | 0.0021696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3619-15_0_6_line_121 | NAYY 4x150 SE | 116 | 118 | 0.0095275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3619-15_0_6_line_122 | NAYY 4x150 SE | 117 | 119 | 0.022487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3619-15_0_6_line_123 | NAYY 4x150 SE | 118 | 120 | 0.024583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3619-15_0_6_line_124 | NAYY 4x150 SE | 119 | 142 | 0.022284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3619-15_0_6_line_125 | NAYY 4x150 SE | 121 | 122 | 0.016875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3619-15_0_6_line_126 | NAYY 4x150 SE | 121 | 123 | 0.023074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3619-15_0_6_line_127 | NAYY 4x150 SE | 123 | 124 | 0.021863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3619-15_0_6_line_128 | NAYY 4x150 SE | 123 | 125 | 0.013029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3619-15_0_6_line_129 | NAYY 4x150 SE | 123 | 126 | 0.054505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3619-15_0_6_line_130 | NAYY 4x150 SE | 125 | 128 | 0.0056707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3619-15_0_6_line_131 | NAYY 4x150 SE | 126 | 127 | 0.0062474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3619-15_0_6_line_132 | NAYY 4x150 SE | 127 | 129 | 0.053369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3619-15_0_6_line_133 | NAYY 4x150 SE | 128 | 130 | 0.0047806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3619-15_0_6_line_134 | NAYY 4x150 SE | 129 | 131 | 0.023659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3619-15_0_6_line_135 | NAYY 4x150 SE | 129 | 132 | 0.0043927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3619-15_0_6_line_136 | NAYY 4x150 SE | 131 | 133 | 0.0077778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3619-15_0_6_line_137 | NAYY 4x150 SE | 134 | 135 | 0.027887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3619-15_0_6_line_138 | NAYY 4x150 SE | 135 | 136 | 0.0082365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3619-15_0_6_line_139 | NAYY 4x150 SE | 137 | 138 | 0.0061896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3619-15_0_6_line_140 | NAYY 4x150 SE | 138 | 139 | 0.021516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3619-15_0_6_line_141 | NAYY 4x150 SE | 139 | 140 | 0.013453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3619-15_0_6_line_142 | NAYY 4x150 SE | 140 | 141 | 0.016827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3619-15_0_6_line_143 | NAYY 4x150 SE | 141 | 142 | 0.0088762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3619-15_0_6_line_144 | NAYY 4x150 SE | 142 | 143 | 0.014119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3619-15_0_6_line_145 | NAYY 4x150 SE | 143 | 144 | 0.024078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3619-15_0_6_line_146 | NAYY 4x150 SE | 144 | 145 | 0.0064954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_3619-15_0_6_line_147 | NAYY 4x150 SE | 145 | 146 | 0.011445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_3619-15_0_6_line_148 | NAYY 4x150 SE | 146 | 147 | 0.019384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_3619-15_0_6_line_149 | NAYY 4x150 SE | 147 | 148 | 0.00021364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_3619-15_0_6_line_150 | NAYY 4x150 SE | 148 | 149 | 0.016326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_3619-15_0_6_line_151 | NAYY 4x150 SE | 149 | 150 | 0.087099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_3619-15_0_6_line_152 | NAYY 4x150 SE | 151 | 152 | 0.037795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_3619-15_0_6_line_153 | NAYY 4x150 SE | 153 | 154 | 0.10257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
154 | LV_3619-15_0_6_line_154 | NAYY 4x150 SE | 153 | 155 | 0.14609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
155 | LV_3619-15_0_6_line_155 | NAYY 4x150 SE | 154 | 156 | 0.17289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_3619-15_0_6_line_156 | NAYY 4x150 SE | 154 | 157 | 0.31314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
157 | LV_3619-15_0_6_line_157 | NAYY 4x150 SE | 155 | 158 | 0.14091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
158 | LV_3619-15_0_6_line_158 | NAYY 4x150 SE | 155 | 159 | 0.0094457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_3619-15_0_6_line_159 | NAYY 4x150 SE | 158 | 160 | 0.12498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
160 | LV_3619-15_0_6_line_160 | NAYY 4x150 SE | 159 | 161 | 0.013131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_3619-15_0_6_line_161 | NAYY 4x150 SE | 160 | 163 | 0.059707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_3619-15_0_6_line_162 | NAYY 4x150 SE | 160 | 164 | 0.07453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_3619-15_0_6_line_163 | NAYY 4x150 SE | 162 | 163 | 0.058758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_3619-15_0_6_line_164 | NAYY 4x150 SE | 164 | 165 | 0.09808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3619-15_0_6_trafo_44 | 0.25 MVA 20/0.4 kV | 166 | 57 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2732891.5427 | 1181922.5549 | 2732904.1142 | 1181925.0311
1 | 2732852.7657 | 1181914.9171 | 2732891.5427 | 1181922.5549
2 | 2732921.4597 | 1181928.4476 | 2732904.1142 | 1181925.0311
3 | 2732852.7657 | 1181914.9171 | 2732831.7755 | 1181911.5661
4 | 2732854.6888 | 1181921.8983 | 2732852.7657 | 1181914.9171
5 | 2732958.4381 | 1181935.7312 | 2732921.4597 | 1181928.4476
6 | 2732814.6138 | 1181907.366 | 2732818.1898 | 1181909.0576 | 2732822.7574 | 1181910.1263 | 2732831.7755 | 1181911.5661
7 | 2732854.6888 | 1181921.8983 | 2732842.1118 | 1181926.145 | 2732818.3248 | 1181927.7748
8 | 2732854.6888 | 1181921.8983 | 2732860.7858 | 1181928.4417
9 | 2732958.4381 | 1181935.7312 | 2732990.9561 | 1181940.9106
10 | 2732958.4381 | 1181935.7312 | 2732963.4224 | 1181906.4797
11 | 2732814.6138 | 1181907.366 | 2732801.4352 | 1181905.6728 | 2732798.2701 | 1181905.0911 | 2732795.6306 | 1181904.232 | 2732793.3727 | 1181903.0478 | 2732791.315 | 1181901.4454 | 2732779.9539 | 1181889.4403 | 2732777.8523 | 1181888.0927 | 2732775.4111 | 1181887.2491 | 2732773.0795 | 1181886.975 | 2732715.4493 | 1181891.2038
12 | 2732814.6138 | 1181907.366 | 2732811.3278 | 1181904.3131 | 2732809.6106 | 1181900.45 | 2732800.9891 | 1181871.6928
13 | 2732898.3414 | 1181961.1874 | 2732888.9541 | 1181955.5277 | 2732881.9317 | 1181951.1353 | 2732860.7858 | 1181928.4417
14 | 2732715.4493 | 1181891.2038 | 2732696.2628 | 1181892.6116
15 | 2732800.9891 | 1181871.6928 | 2732811.7089 | 1181868.5168 | 2732815.4993 | 1181867.172
16 | 2732800.9891 | 1181871.6928 | 2732789.6047 | 1181874.5205 | 2732779.3603 | 1181876.5841 | 2732769.4514 | 1181877.9879 | 2732757.1685 | 1181879.3057 | 2732737.2058 | 1181881.065 | 2732671.8054 | 1181885.6726
17 | 2732898.3414 | 1181961.1874 | 2732945.7642 | 1181989.7798 | 2732949.4517 | 1181992.2416
18 | 2732696.2628 | 1181892.6116 | 2732691.3728 | 1181892.9705 | 2732687.2483 | 1181894.3135 | 2732683.5812 | 1181896.7342 | 2732680.9319 | 1181900.4561 | 2732679.1583 | 1181904.6534 | 2732678.3985 | 1181909.6403 | 2732677.8592 | 1181921.8692
19 | 2732625.9312 | 1181890.36 | 2732636.5783 | 1181888.688 | 2732654.9534 | 1181886.8598 | 2732671.8054 | 1181885.6726
20 | 2732949.4517 | 1181992.2416 | 2732970.2294 | 1182006.1126 | 2732985.9164 | 1182030.39 | 2732987.6298 | 1182033.0411
21 | 2733020.1973 | 1182016.6628 | 2733044.934 | 1181981.6584
22 | 2733008.3728 | 1182033.3955 | 2733020.1973 | 1182016.6628
23 | 2733308.4312 | 1181998.4848 | 2733196.7507 | 1181977.477
24 | 2733308.4312 | 1181998.4848 | 2733328.4771 | 1182002.2318
25 | 2733308.4312 | 1181998.4848 | 2733307.7362 | 1182002.25 | 2733306.9039 | 1182005.3227 | 2733306.0811 | 1182006.4434
26 | 2733308.4312 | 1181998.4848 | 2733307.9221 | 1181992.1798 | 2733306.7394 | 1181986.9718 | 2733299.1679 | 1181962.9375
27 | 2732663.6163 | 1182003.117 | 2732663.0603 | 1181995.4545 | 2732673.2291 | 1181956.7837 | 2732677.6157 | 1181927.3919 | 2732677.8592 | 1181921.8692
28 | 2732615.8913 | 1181892.429 | 2732621.5604 | 1181891.0464 | 2732625.9312 | 1181890.36
29 | 2732663.6163 | 1182003.117 | 2732651.8585 | 1182060.4223 | 2732654.5229 | 1182098.788
30 | 2732663.6163 | 1182003.117 | 2732632.6016 | 1181997.9046 | 2732596.3466 | 1181998.5475 | 2732554.8476 | 1182006.5913 | 2732551.2237 | 1182006.2816
31 | 2732663.6163 | 1182003.117 | 2732668.3945 | 1182006.0583 | 2732732.8389 | 1182016.7708 | 2732748.8829 | 1182021.8743 | 2732761.7175 | 1182030.1203 | 2732767.6949 | 1182035.9314
32 | 2733001.8081 | 1182042.6852 | 2732987.6298 | 1182033.0411
33 | 2733001.8081 | 1182042.6852 | 2733008.3728 | 1182033.3955
34 | 2733001.8081 | 1182042.6852 | 2733012.9401 | 1182049.3967
35 | 2733001.8081 | 1182042.6852 | 2732996.7827 | 1182047.0993 | 2732994.9946 | 1182050.7671
36 | 2733029.1365 | 1182058.0365 | 2733022.7948 | 1182055.3382 | 2733012.9401 | 1182049.3967
37 | 2732989.5296 | 1182064.4296 | 2732990.3957 | 1182060.2008 | 2732994.9946 | 1182050.7671
38 | 2732472.0095 | 1182002.6906 | 2732478.4968 | 1182003.3122 | 2732484.9752 | 1182004.3339 | 2732502.2141 | 1182009.997 | 2732515.7968 | 1182011.7207 | 2732531.0834 | 1181999.2715 | 2732547.4744 | 1182005.9612 | 2732551.2237 | 1182006.2816
39 | 2732454.3446 | 1181992.1145 | 2732458.8392 | 1181996.4838 | 2732464.8337 | 1181999.6964 | 2732472.0095 | 1182002.6906
40 | 2732454.3446 | 1181992.1145 | 2732430.1005 | 1182011.9218
41 | 2732454.3446 | 1181992.1145 | 2732434.0225 | 1181966.6129 | 2732430.0978 | 1181960.6551 | 2732411.9741 | 1181922.4371 | 2732406.9501 | 1181913.3303 | 2732401.1824 | 1181903.6512
42 | 2732402.7124 | 1182034.2977 | 2732430.1005 | 1182011.9218
43 | 2732401.1824 | 1181903.6512 | 2732387.618 | 1181895.9014 | 2732378.9776 | 1181892.4524 | 2732369.0989 | 1181890.0769 | 2732346.3233 | 1181887.1597
44 | 2733328.4771 | 1182002.2318 | 2733338.1436 | 1182004.0387
45 | 2733305.2653 | 1182007.5546 | 2733305.2653 | 1182007.5546 | 2733306.0811 | 1182006.4434
46 | 2733296.0364 | 1181952.997 | 2733299.1679 | 1181962.9375
47 | 2733361.8896 | 1182008.1514 | 2733354.3511 | 1182007.0682 | 2733338.1436 | 1182004.0387
48 | 2733305.2653 | 1182007.5546 | 2733302.4592 | 1182009.3825 | 2733297.6009 | 1182011.2902
49 | 2733296.0364 | 1181952.997 | 2733310.9497 | 1181946.6181
50 | 2733296.0364 | 1181952.997 | 2733287.5462 | 1181936.2973
51 | 2732350.0005 | 1182072.2814 | 2732354.4949 | 1182069.7454 | 2732370.9224 | 1182059.9229 | 2732381.6194 | 1182051.5306 | 2732402.7124 | 1182034.2977
52 | 2733058.5654 | 1182055.3535 | 2733048.7538 | 1182057.705 | 2733040.0961 | 1182059.1917 | 2733034.5422 | 1182059.2018 | 2733029.1365 | 1182058.0365 | 2733029.1365 | 1182058.0365
53 | 2732989.5296 | 1182064.4296 | 2732988.2623 | 1182070.6169 | 2732988.2198 | 1182080.4456 | 2732988.2188 | 1182080.5007
54 | 2733145.6279 | 1182042.8891 | 2733133.1336 | 1182041.3549 | 2733127.5486 | 1182041.0417 | 2733119.1623 | 1182042.0007 | 2733082.9765 | 1182049.5029 | 2733058.5654 | 1182055.3535
55 | 2732988.2188 | 1182080.5007 | 2732987.7962 | 1182103.6537 | 2732987.1025 | 1182107.3745 | 2732983.4595 | 1182111.4634 | 2732968.9668 | 1182115.9898 | 2732965.2386 | 1182119.7878
56 | 2732965.6975 | 1182132.1517 | 2732965.0682 | 1182126.4335 | 2732965.2386 | 1182119.7878
57 | 2732965.6975 | 1182132.1517 | 2732958.9662 | 1182134.6154 | 2732953.4266 | 1182136.3939 | 2732945.7045 | 1182137.1939
58 | 2732965.6975 | 1182132.1517 | 2732972.4103 | 1182130.2218
59 | 2732920.3991 | 1182140.1307 | 2732925.0507 | 1182139.3335 | 2732945.7045 | 1182137.1939
60 | 2732976.3611 | 1182129.086 | 2732972.4103 | 1182130.2218
61 | 2732920.3991 | 1182140.1307 | 2732918.732 | 1182140.4164 | 2732915.5779 | 1182141.4139 | 2732902.5508 | 1182150.4563
62 | 2732976.3611 | 1182129.086 | 2732987.4816 | 1182130.2113 | 2732989.3422 | 1182130.4146
63 | 2732976.3611 | 1182129.086 | 2732993.3262 | 1182121.9236 | 2733001.4347 | 1182117.3 | 2733007.7792 | 1182112.1596
64 | 2733145.6279 | 1182042.8891 | 2733192.8066 | 1182047.7631 | 2733200.8431 | 1182047.4191 | 2733210.5655 | 1182045.467 | 2733221.6568 | 1182041.1117
65 | 2733221.6568 | 1182041.1117 | 2733269.2374 | 1182022.4279
66 | 2733043.0009 | 1182091.4361 | 2733043.0009 | 1182091.4361 | 2733031.3941 | 1182096.0376 | 2733023.094 | 1182100.0008 | 2733016.9458 | 1182103.7228 | 2733014.1124 | 1182106.3677
67 | 2733007.7792 | 1182112.1596 | 2733008.7549 | 1182111.369 | 2733014.1124 | 1182106.3677
68 | 2733280.013 | 1182018.1966 | 2733269.2374 | 1182022.4279
69 | 2733297.6009 | 1182011.2902 | 2733280.013 | 1182018.1966
70 | 2732989.3422 | 1182130.4146 | 2733009.833 | 1182132.6535 | 2733018.964 | 1182137.3708 | 2733025.7564 | 1182136.397
71 | 2733025.7564 | 1182136.397 | 2733039.3796 | 1182134.4438 | 2733059.361 | 1182131.3413
72 | 2732902.5458 | 1182150.4598 | 2732902.5508 | 1182150.4563
73 | 2732902.5458 | 1182150.4598 | 2732898.6645 | 1182153.1539
74 | 2732887.2844 | 1182161.0531 | 2732898.6645 | 1182153.1539
75 | 2732881.8313 | 1182164.8383 | 2732887.2844 | 1182161.0531
76 | 2732875.9935 | 1182168.8904 | 2732881.8313 | 1182164.8383
77 | 2732559.6265 | 1182312.1072 | 2732558.0291 | 1182309.8571 | 2732553.384 | 1182301.7364
78 | 2732553.384 | 1182301.7364 | 2732452.583 | 1182308.7699
79 | 2732568.3113 | 1182324.3399 | 2732559.6265 | 1182312.1072
80 | 2732380.5676 | 1182317.9193 | 2732400.7931 | 1182310.0712 | 2732425.6356 | 1182300.3571 | 2732441.5211 | 1182302.5875 | 2732452.583 | 1182308.7699
81 | 2732452.583 | 1182308.7699 | 2732448.9957 | 1182298.961 | 2732448.0862 | 1182297.8899
82 | 2732568.3113 | 1182324.3399 | 2732564.2965 | 1182326.2637 | 2732562.2444 | 1182328.0713
83 | 2732568.3113 | 1182324.3399 | 2732570.5015 | 1182323.8148
84 | 2732380.5676 | 1182317.9193 | 2732375.0741 | 1182320.044 | 2732340.848 | 1182334.7438 | 2732326.4138 | 1182338.7504 | 2732312.0191 | 1182334.396
85 | 2732380.5676 | 1182317.9193 | 2732376.9143 | 1182317.2981
86 | 2732424.9206 | 1182279.6133 | 2732435.8384 | 1182280.4452 | 2732438.93 | 1182287.1074 | 2732448.0862 | 1182297.8899
87 | 2732312.0191 | 1182334.396 | 2732303.0547 | 1182338.3789 | 2732292.0601 | 1182344.363 | 2732280.769 | 1182349.9403
88 | 2732424.9206 | 1182279.6133 | 2732422.6418 | 1182279.4396
89 | 2732361.5291 | 1182268.2503 | 2732365.5564 | 1182270.5966 | 2732390.4851 | 1182274.9615 | 2732413.0212 | 1182278.7065 | 2732422.6418 | 1182279.4396
90 | 2732394.0851 | 1182235.4668 | 2732361.8325 | 1182256.5927 | 2732359.6713 | 1182261.0594 | 2732359.4098 | 1182265.2902 | 2732361.5291 | 1182268.2503
91 | 2732600.4772 | 1182324.7517 | 2732599.5001 | 1182324.3742 | 2732592.8092 | 1182323.3032 | 2732581.4046 | 1182322.9507 | 2732572.0052 | 1182323.4543 | 2732570.5015 | 1182323.8148
92 | 2732350.0005 | 1182072.2814 | 2732330.5167 | 1182080.7577 | 2732323.9157 | 1182083.0342
93 | 2732875.9935 | 1182168.8904 | 2732869.2442 | 1182159.5264
94 | 2732875.9935 | 1182168.8904 | 2732859.9965 | 1182181.024
95 | 2732859.9965 | 1182181.024 | 2732855.194 | 1182184.6666
96 | 2732847.5397 | 1182190.4723 | 2732855.194 | 1182184.6666
97 | 2732829.7439 | 1182202.7925 | 2732839.359 | 1182196.6773 | 2732847.5397 | 1182190.4723
98 | 2732789.046 | 1182228.5433 | 2732783.6824 | 1182231.4849
99 | 2732789.046 | 1182228.5433 | 2732790.5679 | 1182227.7086 | 2732799.6483 | 1182221.9334
100 | 2732745.2444 | 1182249.9744 | 2732750.2589 | 1182246.2298 | 2732755.1063 | 1182243.2793 | 2732762.9085 | 1182240.0497 | 2732779.3241 | 1182233.8753 | 2732783.6824 | 1182231.4849
101 | 2732801.4167 | 1182220.8087 | 2732799.6483 | 1182221.9334
102 | 2732799.6483 | 1182221.9334 | 2732848.2469 | 1182299.4964
103 | 2732745.2444 | 1182249.9744 | 2732740.8447 | 1182253.2599 | 2732732.9865 | 1182260.3913 | 2732727.9774 | 1182266.1625 | 2732721.7921 | 1182273.987 | 2732709.6207 | 1182292.3759 | 2732708.7781 | 1182293.6463
104 | 2732801.4167 | 1182220.8087 | 2732829.7439 | 1182202.7925
105 | 2732848.2469 | 1182299.4964 | 2732912.6672 | 1182284.3561
106 | 2732708.7781 | 1182293.6463 | 2732702.5634 | 1182303.0166 | 2732694.0797 | 1182314.4208
107 | 2732694.0797 | 1182314.4208 | 2732691.9029 | 1182317.347 | 2732674.677 | 1182337.3433
108 | 2732661.6888 | 1182350.9036 | 2732667.4641 | 1182345.7163 | 2732674.677 | 1182337.3433
109 | 2732661.6888 | 1182350.9036 | 2732650.827 | 1182343.9802 | 2732625.6112 | 1182334.3149 | 2732600.4772 | 1182324.7517
110 | 2732655.254 | 1182370.6983 | 2732658.0108 | 1182357.2825 | 2732659.3661 | 1182354.0323 | 2732661.6888 | 1182350.9036
111 | 2732655.254 | 1182370.6983 | 2732636.795 | 1182398.4552 | 2732630.4967 | 1182443.8279 | 2732623.7537 | 1182468.2305 | 2732618.1221 | 1182473.1089
112 | 2732609.5997 | 1182480.4916 | 2732618.1221 | 1182473.1089
113 | 2732601.55 | 1182487.4649 | 2732609.5997 | 1182480.4916
114 | 2732601.55 | 1182487.4649 | 2732649.5266 | 1182845.2077
115 | 2732282.1357 | 1182093.296 | 2732282.9233 | 1182093.2722 | 2732308.1238 | 1182088.4803 | 2732323.9157 | 1182083.0342
116 | 2732282.1357 | 1182093.296 | 2732266.3403 | 1182093.7724
117 | 2733486.6039 | 1181805.4731 | 2733485.831 | 1181810.3121 | 2733476.0945 | 1181838.2498 | 2733465.2099 | 1181869.3755 | 2733456.833 | 1181892.184 | 2733444.7391 | 1181913.4754 | 2733436.9855 | 1181937.0423
118 | 2733433.5911 | 1181952.5041 | 2733436.299 | 1181939.1291 | 2733436.9855 | 1181937.0423
119 | 2733430.8396 | 1181966.0947 | 2733433.5911 | 1181952.5041
120 | 2733430.8396 | 1181966.0947 | 2733430.7169 | 1181968.2608
121 | 2733430.8396 | 1181966.0947 | 2733421.6022 | 1181963.7617
122 | 2733430.7169 | 1181968.2608 | 2733429.4446 | 1181990.7115
123 | 2733421.6022 | 1181963.7617 | 2733397.7676 | 1181957.7421
124 | 2733428.1838 | 1182012.96 | 2733429.4446 | 1181990.7115
125 | 2733183.347 | 1181857.509 | 2733183.347 | 1181857.509 | 2733198.5576 | 1181850.2002
126 | 2733219.3548 | 1181840.2071 | 2733198.5576 | 1181850.2002
127 | 2733219.3548 | 1181840.2071 | 2733214.6389 | 1181849.9318 | 2733212.3281 | 1181860.7442
128 | 2733219.3548 | 1181840.2071 | 2733225.6589 | 1181828.8052 | 2733225.6589 | 1181828.8052
129 | 2733254.5313 | 1181881.9204 | 2733241.9163 | 1181867.2512 | 2733219.3548 | 1181840.2071
130 | 2733222.8587 | 1181823.8741 | 2733225.6589 | 1181828.8052
131 | 2733254.5313 | 1181881.9204 | 2733258.6058 | 1181886.6564
132 | 2733285.5555 | 1181932.3816 | 2733267.6006 | 1181897.1113 | 2733258.6058 | 1181886.6564
133 | 2733220.4981 | 1181819.717 | 2733222.8587 | 1181823.8741
134 | 2733285.5555 | 1181932.3816 | 2733300.4415 | 1181913.9927
135 | 2733285.5555 | 1181932.3816 | 2733287.5462 | 1181936.2973
136 | 2733305.3353 | 1181907.9474 | 2733300.4415 | 1181913.9927
137 | 2733338.0198 | 1181942.6523 | 2733335.0912 | 1181941.9127 | 2733327.4354 | 1181941.9646 | 2733320.9649 | 1181942.9882 | 2733313.853 | 1181945.3763 | 2733310.9497 | 1181946.6181
138 | 2733338.0198 | 1181942.6523 | 2733346.0055 | 1181944.6692
139 | 2733368.0162 | 1182009.0318 | 2733361.8896 | 1182008.1514
140 | 2733368.0162 | 1182009.0318 | 2733389.3136 | 1182012.0922
141 | 2733389.3136 | 1182012.0922 | 2733402.6293 | 1182014.0056
142 | 2733402.6293 | 1182014.0056 | 2733405.1733 | 1182014.3711 | 2733416.7949 | 1182014.6189 | 2733419.4003 | 1182014.2394
143 | 2733428.1838 | 1182012.96 | 2733419.4003 | 1182014.2394
144 | 2733428.1838 | 1182012.96 | 2733441.8612 | 1182009.458
145 | 2733441.8612 | 1182009.458 | 2733459.1469 | 1182005.0321 | 2733465.2919 | 1182003.9777
146 | 2733471.6937 | 1182002.8793 | 2733465.2919 | 1182003.9777
147 | 2733471.6937 | 1182002.8793 | 2733474.4612 | 1182002.4044 | 2733483.0796 | 1182001.831
148 | 2733483.0796 | 1182001.831 | 2733489.6096 | 1182001.3965 | 2733502.4464 | 1182001.6807
149 | 2733502.66 | 1182001.6854 | 2733502.4464 | 1182001.6807
150 | 2733502.66 | 1182001.6854 | 2733518.9816 | 1182002.0467
151 | 2733518.9816 | 1182002.0467 | 2733606.0595 | 1182003.9744
152 | 2732394.0851 | 1182235.4668 | 2732383.3047 | 1182236.5851 | 2732356.9658 | 1182242.797
153 | 2732956.0697 | 1182781.2846 | 2732979.5462 | 1182783.5182 | 2733004.2631 | 1182773.5702 | 2733031.9465 | 1182751.4679 | 2733048.8701 | 1182751.5613
154 | 2732990.4149 | 1182617.6713 | 2733048.8701 | 1182751.5613
155 | 2732956.0697 | 1182781.2846 | 2732945.4488 | 1182953.8463
156 | 2732956.0697 | 1182781.2846 | 2732649.5266 | 1182845.2077
157 | 2732990.4149 | 1182617.6713 | 2732992.2967 | 1182617.9536 | 2733010.6199 | 1182616.6481 | 2733033.2182 | 1182611.3345 | 2733057.802 | 1182605.0087 | 2733117.3723 | 1182597.2254 | 2733129.2859 | 1182596.2004
158 | 2732981.3916 | 1182615.3777 | 2732983.5111 | 1182616.6355 | 2732990.4149 | 1182617.6713
159 | 2733124.7356 | 1182471.3061 | 2733129.2859 | 1182596.2004
160 | 2732970.0989 | 1182608.6764 | 2732981.3916 | 1182615.3777
161 | 2733124.7356 | 1182471.3061 | 2733115.0871 | 1182470.4565 | 2733094.7536 | 1182464.923 | 2733068.609 | 1182452.4947
162 | 2733198.8413 | 1182474.9069 | 2733188.0697 | 1182476.8826 | 2733124.7356 | 1182471.3061
163 | 2733029.8581 | 1182480.2607 | 2733040.4399 | 1182469.4986 | 2733049.3848 | 1182448.181 | 2733057.0875 | 1182447.0177 | 2733068.609 | 1182452.4947
164 | 2733198.8413 | 1182474.9069 | 2733218.4591 | 1182378.8092

## bus_geodata
| x | y | coords
0 | 2732891.5427 | 1181922.5549
1 | 2732904.1142 | 1181925.0311
2 | 2732852.7657 | 1181914.9171
3 | 2732921.4597 | 1181928.4476
4 | 2732831.7755 | 1181911.5661
5 | 2732854.6888 | 1181921.8983
6 | 2732958.4381 | 1181935.7312
7 | 2732814.6138 | 1181907.366
8 | 2732818.3248 | 1181927.7748
9 | 2732860.7858 | 1181928.4417
10 | 2732990.9562 | 1181940.9106
11 | 2732963.4224 | 1181906.4797
12 | 2732715.4493 | 1181891.2038
13 | 2732800.9891 | 1181871.6928
14 | 2732898.3414 | 1181961.1874
15 | 2732696.2628 | 1181892.6116
16 | 2732815.4993 | 1181867.172
17 | 2732671.8054 | 1181885.6726
18 | 2732949.4517 | 1181992.2416
19 | 2733044.934 | 1181981.6584
20 | 2733020.1973 | 1182016.6628
21 | 2733196.7507 | 1181977.477
22 | 2733308.4312 | 1181998.4848
23 | 2732677.8592 | 1181921.8692
24 | 2732625.9312 | 1181890.36
25 | 2732663.6163 | 1182003.117
26 | 2732615.8913 | 1181892.429
27 | 2732987.6298 | 1182033.0411
28 | 2733001.8081 | 1182042.6852
29 | 2733008.3728 | 1182033.3955
30 | 2733012.9401 | 1182049.3967
31 | 2732994.9946 | 1182050.7671
32 | 2732654.5229 | 1182098.788
33 | 2732551.2237 | 1182006.2816
34 | 2732767.6949 | 1182035.9314
35 | 2732472.0095 | 1182002.6906
36 | 2732454.3446 | 1181992.1145
37 | 2732430.1005 | 1182011.9218
38 | 2732401.1824 | 1181903.6512
39 | 2733328.4771 | 1182002.2318
40 | 2733306.0811 | 1182006.4434
41 | 2733299.1679 | 1181962.9375
42 | 2733338.1436 | 1182004.0387
43 | 2733305.2653 | 1182007.5546
44 | 2733296.0364 | 1181952.997
45 | 2732346.3233 | 1181887.1597
46 | 2732402.7124 | 1182034.2977
47 | 2733029.1365 | 1182058.0365
48 | 2732989.5296 | 1182064.4296
49 | 2733058.5654 | 1182055.3535
50 | 2732988.2188 | 1182080.5007
51 | 2732965.2386 | 1182119.7878
52 | 2732965.6975 | 1182132.1517
53 | 2732945.7045 | 1182137.1939
54 | 2732972.4103 | 1182130.2218
55 | 2732920.3991 | 1182140.1307
56 | 2732976.3611 | 1182129.086
57 | 2733145.6279 | 1182042.8891
58 | 2733221.6568 | 1182041.1117
59 | 2733043.0009 | 1182091.4361
60 | 2733014.1124 | 1182106.3677
61 | 2733269.2374 | 1182022.4279
62 | 2733007.7792 | 1182112.1596
63 | 2733280.013 | 1182018.1966
64 | 2733297.6009 | 1182011.2902
65 | 2732989.3422 | 1182130.4146
66 | 2733025.7564 | 1182136.397
67 | 2732902.5508 | 1182150.4563
68 | 2732902.5458 | 1182150.4598
69 | 2732898.6645 | 1182153.1539
70 | 2732887.2844 | 1182161.0531
71 | 2732881.8313 | 1182164.8383
72 | 2733059.361 | 1182131.3413
73 | 2732553.384 | 1182301.7364
74 | 2732559.6265 | 1182312.1072
75 | 2732452.583 | 1182308.7699
76 | 2732568.3113 | 1182324.3399
77 | 2732380.5676 | 1182317.9193
78 | 2732448.0862 | 1182297.8899
79 | 2732312.0191 | 1182334.396
80 | 2732376.9143 | 1182317.2981
81 | 2732424.9206 | 1182279.6133
82 | 2732422.6418 | 1182279.4396
83 | 2732361.5291 | 1182268.2503
84 | 2732562.2444 | 1182328.0713
85 | 2732570.5015 | 1182323.8148
86 | 2732350.0005 | 1182072.2814
87 | 2732869.2442 | 1182159.5264
88 | 2732875.9935 | 1182168.8904
89 | 2732859.9965 | 1182181.024
90 | 2732855.194 | 1182184.6666
91 | 2732847.5397 | 1182190.4723
92 | 2732789.046 | 1182228.5433
93 | 2732783.6824 | 1182231.4849
94 | 2732799.6483 | 1182221.9334
95 | 2732745.2444 | 1182249.9744
96 | 2732801.4167 | 1182220.8087
97 | 2732848.2469 | 1182299.4964
98 | 2732708.7781 | 1182293.6463
99 | 2732829.7439 | 1182202.7925
100 | 2732912.6672 | 1182284.3561
101 | 2732694.0797 | 1182314.4208
102 | 2732674.677 | 1182337.3433
103 | 2732661.6888 | 1182350.9036
104 | 2732600.4772 | 1182324.7517
105 | 2732655.254 | 1182370.6983
106 | 2732618.1221 | 1182473.1089
107 | 2732609.5997 | 1182480.4916
108 | 2732601.55 | 1182487.4649
109 | 2732280.769 | 1182349.9403
110 | 2732282.1357 | 1182093.296
111 | 2732323.9157 | 1182083.0342
112 | 2732266.3403 | 1182093.7724
113 | 2733486.6039 | 1181805.4731
114 | 2733436.9855 | 1181937.0423
115 | 2733433.5911 | 1181952.5041
116 | 2733430.8396 | 1181966.0947
117 | 2733430.7169 | 1181968.2608
118 | 2733421.6022 | 1181963.7617
119 | 2733429.4446 | 1181990.7115
120 | 2733397.7676 | 1181957.7421
121 | 2733198.5576 | 1181850.2002
122 | 2733183.347 | 1181857.509
123 | 2733219.3548 | 1181840.2071
124 | 2733212.3281 | 1181860.7442
125 | 2733225.6589 | 1181828.8052
126 | 2733254.5313 | 1181881.9204
127 | 2733258.6058 | 1181886.6564
128 | 2733222.8587 | 1181823.8741
129 | 2733285.5555 | 1181932.3816
130 | 2733220.4981 | 1181819.717
131 | 2733300.4415 | 1181913.9927
132 | 2733287.5462 | 1181936.2973
133 | 2733305.3353 | 1181907.9474
134 | 2733310.9497 | 1181946.6181
135 | 2733338.0198 | 1181942.6523
136 | 2733346.0055 | 1181944.6692
137 | 2733361.8896 | 1182008.1514
138 | 2733368.0162 | 1182009.0318
139 | 2733389.3136 | 1182012.0922
140 | 2733402.6293 | 1182014.0056
141 | 2733419.4003 | 1182014.2394
142 | 2733428.1838 | 1182012.96
143 | 2733441.8612 | 1182009.458
144 | 2733465.2919 | 1182003.9777
145 | 2733471.6937 | 1182002.8793
146 | 2733483.0796 | 1182001.831
147 | 2733502.4464 | 1182001.6807
148 | 2733502.66 | 1182001.6854
149 | 2733518.9816 | 1182002.0467
150 | 2733606.0595 | 1182003.9744
151 | 2732394.0851 | 1182235.4668
152 | 2732356.9658 | 1182242.797
153 | 2733048.8701 | 1182751.5613
154 | 2732956.0697 | 1182781.2846
155 | 2732990.4149 | 1182617.6713
156 | 2732945.4488 | 1182953.8463
157 | 2732649.5266 | 1182845.2077
158 | 2733129.2859 | 1182596.2004
159 | 2732981.3916 | 1182615.3777
160 | 2733124.7356 | 1182471.3061
161 | 2732970.0989 | 1182608.6764
162 | 2733029.8581 | 1182480.2607
163 | 2733068.609 | 1182452.4947
164 | 2733198.8413 | 1182474.9069
165 | 2733218.4591 | 1182378.8092
166 | 2733001.8081 | 1182042.6852

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1