## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3619-20_1_5_node_58 | 0.4 | n |  | TRUE
1 | bus_LV_3619-20_1_5_node_147 | 0.4 | n |  | TRUE
2 | bus_LV_3619-20_1_5_node_136 | 0.4 | n |  | TRUE
3 | bus_LV_3619-20_1_5_node_139 | 0.4 | n |  | TRUE
4 | bus_LV_3619-20_1_5_node_134 | 0.4 | n |  | TRUE
5 | bus_LV_3619-20_1_5_node_69 | 0.4 | n |  | TRUE
6 | bus_LV_3619-20_1_5_node_68 | 0.4 | n |  | TRUE
7 | bus_LV_3619-20_1_5_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_3619-20_1_5_node_63 | 0.4 | n |  | TRUE
9 | bus_LV_3619-20_1_5_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_3619-20_1_5_node_79 | 0.4 | n |  | TRUE
11 | bus_LV_3619-20_1_5_node_65 | 0.4 | n |  | TRUE
12 | bus_LV_3619-20_1_5_node_75 | 0.4 | n |  | TRUE
13 | bus_LV_3619-20_1_5_node_77 | 0.4 | n |  | TRUE
14 | bus_LV_3619-20_1_5_node_74 | 0.4 | n |  | TRUE
15 | bus_LV_3619-20_1_5_node_155 | 0.4 | n |  | TRUE
16 | bus_LV_3619-20_1_5_node_152 | 0.4 | n |  | TRUE
17 | bus_LV_3619-20_1_5_node_154 | 0.4 | n |  | TRUE
18 | bus_LV_3619-20_1_5_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_3619-20_1_5_node_104 | 0.4 | n |  | TRUE
20 | bus_LV_3619-20_1_5_node_101 | 0.4 | n |  | TRUE
21 | bus_LV_3619-20_1_5_node_102 | 0.4 | n |  | TRUE
22 | bus_LV_3619-20_1_5_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_3619-20_1_5_node_76 | 0.4 | n |  | TRUE
24 | bus_LV_3619-20_1_5_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_3619-20_1_5_node_82 | 0.4 | n |  | TRUE
26 | bus_LV_3619-20_1_5_node_105 | 0.4 | n |  | TRUE
27 | bus_LV_3619-20_1_5_node_106 | 0.4 | n |  | TRUE
28 | bus_LV_3619-20_1_5_node_103 | 0.4 | n |  | TRUE
29 | bus_LV_3619-20_1_5_node_71 | 0.4 | n |  | TRUE
30 | bus_LV_3619-20_1_5_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_3619-20_1_5_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_3619-20_1_5_node_121 | 0.4 | n |  | TRUE
33 | bus_LV_3619-20_1_5_node_119 | 0.4 | n |  | TRUE
34 | bus_LV_3619-20_1_5_node_78 | 0.4 | n |  | TRUE
35 | bus_LV_3619-20_1_5_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_3619-20_1_5_node_83 | 0.4 | n |  | TRUE
37 | bus_LV_3619-20_1_5_node_84 | 0.4 | n |  | TRUE
38 | bus_LV_3619-20_1_5_node_85 | 0.4 | n |  | TRUE
39 | bus_LV_3619-20_1_5_node_86 | 0.4 | n |  | TRUE
40 | bus_LV_3619-20_1_5_node_87 | 0.4 | n |  | TRUE
41 | bus_LV_3619-20_1_5_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_3619-20_1_5_node_90 | 0.4 | n |  | TRUE
43 | bus_LV_3619-20_1_5_node_89 | 0.4 | n |  | TRUE
44 | bus_LV_3619-20_1_5_node_91 | 0.4 | n |  | TRUE
45 | bus_LV_3619-20_1_5_node_92 | 0.4 | n |  | TRUE
46 | bus_LV_3619-20_1_5_node_93 | 0.4 | n |  | TRUE
47 | bus_LV_3619-20_1_5_node_94 | 0.4 | n |  | TRUE
48 | bus_LV_3619-20_1_5_node_98 | 0.4 | n |  | TRUE
49 | bus_LV_3619-20_1_5_node_95 | 0.4 | n |  | TRUE
50 | bus_LV_3619-20_1_5_node_99 | 0.4 | n |  | TRUE
51 | bus_LV_3619-20_1_5_node_96 | 0.4 | n |  | TRUE
52 | bus_LV_3619-20_1_5_node_97 | 0.4 | n |  | TRUE
53 | bus_LV_3619-20_1_5_node_125 | 0.4 | n |  | TRUE
54 | bus_LV_3619-20_1_5_node_124 | 0.4 | n |  | TRUE
55 | bus_LV_3619-20_1_5_node_100 | 0.4 | n |  | TRUE
56 | bus_LV_3619-20_1_5_node_107 | 0.4 | n |  | TRUE
57 | bus_LV_3619-20_1_5_node_108 | 0.4 | n |  | TRUE
58 | bus_LV_3619-20_1_5_node_109 | 0.4 | n |  | TRUE
59 | bus_LV_3619-20_1_5_node_110 | 0.4 | n |  | TRUE
60 | bus_LV_3619-20_1_5_node_111 | 0.4 | n |  | TRUE
61 | bus_LV_3619-20_1_5_node_208 | 0.4 | n |  | TRUE
62 | bus_LV_3619-20_1_5_node_112 | 0.4 | n |  | TRUE
63 | bus_LV_3619-20_1_5_node_206 | 0.4 | n |  | TRUE
64 | bus_LV_3619-20_1_5_node_113 | 0.4 | n |  | TRUE
65 | bus_LV_3619-20_1_5_node_114 | 0.4 | n |  | TRUE
66 | bus_LV_3619-20_1_5_node_205 | 0.4 | n |  | TRUE
67 | bus_LV_3619-20_1_5_node_196 | 0.4 | n |  | TRUE
68 | bus_LV_3619-20_1_5_node_197 | 0.4 | n |  | TRUE
69 | bus_LV_3619-20_1_5_node_198 | 0.4 | n |  | TRUE
70 | bus_LV_3619-20_1_5_node_207 | 0.4 | n |  | TRUE
71 | bus_LV_3619-20_1_5_node_199 | 0.4 | n |  | TRUE
72 | bus_LV_3619-20_1_5_node_200 | 0.4 | n |  | TRUE
73 | bus_LV_3619-20_1_5_node_203 | 0.4 | n |  | TRUE
74 | bus_LV_3619-20_1_5_node_201 | 0.4 | n |  | TRUE
75 | bus_LV_3619-20_1_5_node_202 | 0.4 | n |  | TRUE
76 | bus_LV_3619-20_1_5_node_204 | 0.4 | n |  | TRUE
77 | bus_LV_3619-20_1_5_node_115 | 0.4 | n |  | TRUE
78 | bus_LV_3619-20_1_5_node_116 | 0.4 | n |  | TRUE
79 | bus_LV_3619-20_1_5_node_117 | 0.4 | n |  | TRUE
80 | bus_LV_3619-20_1_5_node_118 | 0.4 | n |  | TRUE
81 | bus_LV_3619-20_1_5_node_120 | 0.4 | n |  | TRUE
82 | bus_LV_3619-20_1_5_node_122 | 0.4 | n |  | TRUE
83 | bus_LV_3619-20_1_5_node_153 | 0.4 | n |  | TRUE
84 | bus_LV_3619-20_1_5_node_123 | 0.4 | n |  | TRUE
85 | bus_LV_3619-20_1_5_node_157 | 0.4 | n |  | TRUE
86 | bus_LV_3619-20_1_5_node_165 | 0.4 | n |  | TRUE
87 | bus_LV_3619-20_1_5_node_127 | 0.4 | n |  | TRUE
88 | bus_LV_3619-20_1_5_node_133 | 0.4 | n |  | TRUE
89 | bus_LV_3619-20_1_5_node_130 | 0.4 | n |  | TRUE
90 | bus_LV_3619-20_1_5_node_131 | 0.4 | n |  | TRUE
91 | bus_LV_3619-20_1_5_node_132 | 0.4 | n |  | TRUE
92 | bus_LV_3619-20_1_5_node_140 | 0.4 | n |  | TRUE
93 | bus_LV_3619-20_1_5_node_135 | 0.4 | n |  | TRUE
94 | bus_LV_3619-20_1_5_node_162 | 0.4 | n |  | TRUE
95 | bus_LV_3619-20_1_5_node_138 | 0.4 | n |  | TRUE
96 | bus_LV_3619-20_1_5_node_161 | 0.4 | n |  | TRUE
97 | bus_LV_3619-20_1_5_node_160 | 0.4 | n |  | TRUE
98 | bus_LV_3619-20_1_5_node_163 | 0.4 | n |  | TRUE
99 | bus_LV_3619-20_1_5_node_145 | 0.4 | n |  | TRUE
100 | bus_LV_3619-20_1_5_node_146 | 0.4 | n |  | TRUE
101 | bus_LV_3619-20_1_5_node_148 | 0.4 | n |  | TRUE
102 | bus_LV_3619-20_1_5_node_149 | 0.4 | n |  | TRUE
103 | bus_LV_3619-20_1_5_node_171 | 0.4 | n |  | TRUE
104 | bus_LV_3619-20_1_5_node_175 | 0.4 | n |  | TRUE
105 | bus_LV_3619-20_1_5_node_173 | 0.4 | n |  | TRUE
106 | bus_LV_3619-20_1_5_node_170 | 0.4 | n |  | TRUE
107 | bus_LV_3619-20_1_5_node_176 | 0.4 | n |  | TRUE
108 | bus_LV_3619-20_1_5_node_150 | 0.4 | n |  | TRUE
109 | bus_LV_3619-20_1_5_node_151 | 0.4 | n |  | TRUE
110 | bus_LV_3619-20_1_5_node_180 | 0.4 | n |  | TRUE
111 | bus_LV_3619-20_1_5_node_184 | 0.4 | n |  | TRUE
112 | bus_LV_3619-20_1_5_node_186 | 0.4 | n |  | TRUE
113 | bus_LV_3619-20_1_5_node_183 | 0.4 | n |  | TRUE
114 | bus_LV_3619-20_1_5_node_179 | 0.4 | n |  | TRUE
115 | bus_LV_3619-20_1_5_node_156 | 0.4 | n |  | TRUE
116 | bus_LV_3619-20_1_5_node_158 | 0.4 | n |  | TRUE
117 | bus_LV_3619-20_1_5_node_159 | 0.4 | n |  | TRUE
118 | bus_LV_3619-20_1_5_node_166 | 0.4 | n |  | TRUE
119 | bus_LV_3619-20_1_5_node_164 | 0.4 | n |  | TRUE
120 | bus_LV_3619-20_1_5_node_169 | 0.4 | n |  | TRUE
121 | bus_LV_3619-20_1_5_node_167 | 0.4 | n |  | TRUE
122 | bus_LV_3619-20_1_5_node_168 | 0.4 | n |  | TRUE
123 | bus_LV_3619-20_1_5_node_182 | 0.4 | n |  | TRUE
124 | bus_LV_3619-20_1_5_node_195 | 0.4 | n |  | TRUE
125 | bus_LV_3619-20_1_5_node_181 | 0.4 | n |  | TRUE
126 | bus_LV_3619-20_1_5_node_194 | 0.4 | n |  | TRUE
127 | bus_LV_3619-20_1_5_node_172 | 0.4 | n |  | TRUE
128 | bus_LV_3619-20_1_5_node_174 | 0.4 | n |  | TRUE
129 | bus_LV_3619-20_1_5_node_177 | 0.4 | n |  | TRUE
130 | bus_LV_3619-20_1_5_node_178 | 0.4 | n |  | TRUE
131 | bus_LV_3619-20_1_5_node_185 | 0.4 | n |  | TRUE
132 | bus_LV_3619-20_1_5_node_187 | 0.4 | n |  | TRUE
133 | bus_LV_3619-20_1_5_node_190 | 0.4 | n |  | TRUE
134 | bus_LV_3619-20_1_5_node_188 | 0.4 | n |  | TRUE
135 | bus_LV_3619-20_1_5_node_189 | 0.4 | n |  | TRUE
136 | bus_LV_3619-20_1_5_node_193 | 0.4 | n |  | TRUE
137 | bus_MV_0_node_125 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3619-20_1_5_load_58 | 0 | 0.00027861 | 6.9826e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3619-20_1_5_load_147 | 1 | 0.00030789 | 7.7164e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3619-20_1_5_load_136 | 2 | 0.00025989 | 6.5133e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3619-20_1_5_load_139 | 3 | 0.00068381 | 0.00017138 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3619-20_1_5_load_69 | 5 | 0.00017716 | 4.44e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3619-20_1_5_load_62 | 7 | 0.00057348 | 0.00014373 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3619-20_1_5_load_63 | 8 | 0.0006801 | 0.00017045 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3619-20_1_5_load_79 | 10 | 0.0010461 | 0.00026217 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3619-20_1_5_load_65 | 11 | 0.00067239 | 0.00016852 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3619-20_1_5_load_75 | 12 | 0.00064603 | 0.00016191 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3619-20_1_5_load_77 | 13 | 0.00083596 | 0.00020951 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3619-20_1_5_load_74 | 14 | 0.00089143 | 0.00022341 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3619-20_1_5_load_155 | 15 | 0.0001412 | 3.5388e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3619-20_1_5_load_152 | 16 | 6.747e-05 | 1.691e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3619-20_1_5_load_81 | 18 | 0.00068804 | 0.00017244 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3619-20_1_5_load_104 | 19 | 0.0022297 | 0.00055881 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3619-20_1_5_load_101 | 20 | 0.0011788 | 0.00029543 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3619-20_1_5_load_102 | 21 | 0.00058189 | 0.00014584 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3619-20_1_5_load_70 | 22 | 0.00010267 | 2.5732e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3619-20_1_5_load_76 | 23 | 9.6847e-05 | 2.4272e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3619-20_1_5_load_67 | 24 | 0.00078558 | 0.00019689 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3619-20_1_5_load_82 | 25 | 0.00097452 | 0.00024424 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3619-20_1_5_load_105 | 26 | 0.00058342 | 0.00014622 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3619-20_1_5_load_106 | 27 | 0.00087789 | 0.00022002 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3619-20_1_5_load_103 | 28 | 0.00053354 | 0.00013372 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3619-20_1_5_load_71 | 29 | 0.00014777 | 3.7036e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3619-20_1_5_load_72 | 30 | 6.9807e-05 | 1.7495e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3619-20_1_5_load_73 | 31 | 0.00010586 | 2.6532e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3619-20_1_5_load_121 | 32 | 0.00018207 | 4.563e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3619-20_1_5_load_119 | 33 | 7.7998e-05 | 1.9548e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3619-20_1_5_load_78 | 34 | 7.7563e-05 | 1.9439e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3619-20_1_5_load_80 | 35 | 8.0135e-05 | 2.0084e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3619-20_1_5_load_83 | 36 | 0.00064122 | 0.0001607 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3619-20_1_5_load_84 | 37 | 0.00080065 | 0.00020066 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3619-20_1_5_load_85 | 38 | 0.00071845 | 0.00018006 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3619-20_1_5_load_87 | 40 | 0.00099283 | 0.00024883 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3619-20_1_5_load_88 | 41 | 0.00082384 | 0.00020647 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3619-20_1_5_load_89 | 43 | 0.00090493 | 0.0002268 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3619-20_1_5_load_92 | 45 | 0.00097886 | 0.00024533 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3619-20_1_5_load_93 | 46 | 0.00074578 | 0.00018691 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3619-20_1_5_load_94 | 47 | 0.00074687 | 0.00018718 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3619-20_1_5_load_98 | 48 | 0.00051918 | 0.00013012 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3619-20_1_5_load_95 | 49 | 0.00010049 | 2.5184e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3619-20_1_5_load_99 | 50 | 0.00052956 | 0.00013272 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3619-20_1_5_load_96 | 51 | 8.75e-05 | 2.193e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3619-20_1_5_load_97 | 52 | 6.7609e-05 | 1.6944e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3619-20_1_5_load_125 | 53 | 7.4003e-05 | 1.8547e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3619-20_1_5_load_124 | 54 | 0.00011977 | 3.0017e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3619-20_1_5_load_100 | 55 | 0.00062919 | 0.00015769 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3619-20_1_5_load_107 | 56 | 0.00049444 | 0.00012392 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3619-20_1_5_load_108 | 57 | 0.00097969 | 0.00024553 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3619-20_1_5_load_109 | 58 | 0.00071696 | 0.00017969 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3619-20_1_5_load_110 | 59 | 0.00010311 | 2.5841e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3619-20_1_5_load_111 | 60 | 0.00011343 | 2.8429e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3619-20_1_5_load_208 | 61 | 0.000944 | 0.00023659 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3619-20_1_5_load_112 | 62 | 0.00037895 | 9.4975e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3619-20_1_5_load_206 | 63 | 0.00016314 | 4.0888e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3619-20_1_5_load_113 | 64 | 0.00014139 | 3.5436e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3619-20_1_5_load_114 | 65 | 0.00016808 | 4.2125e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3619-20_1_5_load_205 | 66 | 0.00013662 | 3.4239e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3619-20_1_5_load_196 | 67 | 0.00047875 | 0.00011999 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3619-20_1_5_load_197 | 68 | 0.00022026 | 5.5203e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3619-20_1_5_load_207 | 70 | 9.2105e-05 | 2.3084e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3619-20_1_5_load_199 | 71 | 0.00011006 | 2.7584e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3619-20_1_5_load_201 | 74 | 8.9448e-05 | 2.2418e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3619-20_1_5_load_202 | 75 | 0.00016563 | 4.1512e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3619-20_1_5_load_115 | 77 | 6.9826e-05 | 1.75e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3619-20_1_5_load_116 | 78 | 8.5424e-05 | 2.1409e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3619-20_1_5_load_117 | 79 | 9.3447e-05 | 2.342e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3619-20_1_5_load_118 | 80 | 0.00015541 | 3.8949e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3619-20_1_5_load_120 | 81 | 0.00012337 | 3.092e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3619-20_1_5_load_153 | 83 | 0.00012184 | 3.0535e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3619-20_1_5_load_123 | 84 | 8.1663e-05 | 2.0467e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3619-20_1_5_load_165 | 86 | 8.6839e-05 | 2.1764e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3619-20_1_5_load_127 | 87 | 0.00028827 | 7.2247e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3619-20_1_5_load_133 | 88 | 0.00026895 | 6.7405e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3619-20_1_5_load_131 | 90 | 0.00010178 | 2.5509e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3619-20_1_5_load_140 | 92 | 0.00015897 | 3.9841e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3619-20_1_5_load_135 | 93 | 0.00030112 | 7.5468e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3619-20_1_5_load_162 | 94 | 7.8016e-05 | 1.9553e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3619-20_1_5_load_138 | 95 | 7.7665e-05 | 1.9465e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3619-20_1_5_load_161 | 96 | 0.00015647 | 3.9215e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3619-20_1_5_load_160 | 97 | 0.00013127 | 3.2899e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3619-20_1_5_load_163 | 98 | 8.8347e-05 | 2.2142e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3619-20_1_5_load_146 | 100 | 0.00055974 | 0.00014028 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3619-20_1_5_load_148 | 101 | 7.4863e-05 | 1.8762e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3619-20_1_5_load_149 | 102 | 8.4462e-05 | 2.1168e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3619-20_1_5_load_175 | 104 | 0.00045576 | 0.00011423 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3619-20_1_5_load_173 | 105 | 0.00015331 | 3.8422e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3619-20_1_5_load_176 | 107 | 0.00011359 | 2.8469e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3619-20_1_5_load_150 | 108 | 0.00013309 | 3.3356e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3619-20_1_5_load_151 | 109 | 0.00023011 | 5.7672e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3619-20_1_5_load_180 | 110 | 0.00010675 | 2.6754e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3619-20_1_5_load_184 | 111 | 0.00092469 | 0.00023175 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3619-20_1_5_load_183 | 113 | 0.00011052 | 2.7698e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3619-20_1_5_load_156 | 115 | 9.4141e-05 | 2.3594e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3619-20_1_5_load_158 | 116 | 0.00012978 | 3.2525e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3619-20_1_5_load_159 | 117 | 7.2701e-05 | 1.8221e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3619-20_1_5_load_166 | 118 | 0.00018204 | 4.5623e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3619-20_1_5_load_164 | 119 | 9.2615e-05 | 2.3212e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3619-20_1_5_load_169 | 120 | 9.4598e-05 | 2.3709e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3619-20_1_5_load_167 | 121 | 7.622e-05 | 1.9103e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3619-20_1_5_load_182 | 123 | 0.00011489 | 2.8794e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3619-20_1_5_load_181 | 125 | 0.00013959 | 3.4986e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3619-20_1_5_load_194 | 126 | 0.00024222 | 6.0706e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3619-20_1_5_load_172 | 127 | 0.00012777 | 3.2023e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3619-20_1_5_load_174 | 128 | 9.713e-05 | 2.4343e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3619-20_1_5_load_177 | 129 | 0.00016895 | 4.2344e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3619-20_1_5_load_178 | 130 | 0.00011567 | 2.899e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3619-20_1_5_load_185 | 131 | 7.7056e-05 | 1.9312e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3619-20_1_5_load_187 | 132 | 0.00050228 | 0.00012588 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3619-20_1_5_load_188 | 134 | 0.0011017 | 0.0002761 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3619-20_1_5_load_189 | 135 | 0.00078835 | 0.00019758 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3619-20_1_5_load_193 | 136 | 0.00012702 | 3.1835e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3619-20_1_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.25846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3619-20_1_5_line_1 | NAYY 4x150 SE | 1 | 102 | 0.02798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3619-20_1_5_line_2 | NAYY 4x150 SE | 1 | 99 | 0.10596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3619-20_1_5_line_3 | NAYY 4x150 SE | 2 | 3 | 0.037721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3619-20_1_5_line_4 | NAYY 4x150 SE | 2 | 4 | 0.054751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3619-20_1_5_line_5 | NAYY 4x150 SE | 4 | 88 | 0.07356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3619-20_1_5_line_6 | NAYY 4x150 SE | 4 | 87 | 0.13124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3619-20_1_5_line_7 | NAYY 4x150 SE | 5 | 6 | 0.16517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3619-20_1_5_line_8 | NAYY 4x150 SE | 6 | 22 | 0.020712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3619-20_1_5_line_9 | NAYY 4x150 SE | 6 | 11 | 0.013424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3619-20_1_5_line_10 | NAYY 4x150 SE | 7 | 8 | 0.2039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3619-20_1_5_line_11 | NAYY 4x150 SE | 7 | 9 | 0.014304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3619-20_1_5_line_12 | NAYY 4x150 SE | 8 | 10 | 0.19602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3619-20_1_5_line_13 | NAYY 4x150 SE | 9 | 11 | 0.20987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3619-20_1_5_line_14 | NAYY 4x150 SE | 10 | 18 | 0.086147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3619-20_1_5_line_15 | NAYY 4x150 SE | 10 | 13 | 0.10631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3619-20_1_5_line_16 | NAYY 4x150 SE | 12 | 13 | 0.043289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3619-20_1_5_line_17 | NAYY 4x150 SE | 12 | 14 | 0.094083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3619-20_1_5_line_18 | NAYY 4x150 SE | 14 | 23 | 0.18159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3619-20_1_5_line_19 | NAYY 4x150 SE | 15 | 16 | 0.20754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_3619-20_1_5_line_20 | NAYY 4x150 SE | 15 | 17 | 0.093741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_3619-20_1_5_line_21 | NAYY 4x150 SE | 16 | 83 | 0.18722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3619-20_1_5_line_22 | NAYY 4x150 SE | 16 | 33 | 0.15363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_3619-20_1_5_line_23 | NAYY 4x150 SE | 17 | 115 | 0.078168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_3619-20_1_5_line_24 | NAYY 4x150 SE | 17 | 85 | 0.17436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3619-20_1_5_line_25 | NAYY 4x150 SE | 18 | 25 | 0.08952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3619-20_1_5_line_26 | NAYY 4x150 SE | 19 | 20 | 0.2804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3619-20_1_5_line_27 | NAYY 4x150 SE | 19 | 21 | 0.038676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3619-20_1_5_line_28 | NAYY 4x150 SE | 20 | 55 | 0.079703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3619-20_1_5_line_29 | NAYY 4x150 SE | 21 | 28 | 0.028036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3619-20_1_5_line_30 | NAYY 4x150 SE | 22 | 29 | 0.22157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3619-20_1_5_line_31 | NAYY 4x150 SE | 23 | 34 | 0.02964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3619-20_1_5_line_32 | NAYY 4x150 SE | 24 | 25 | 0.19612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3619-20_1_5_line_33 | NAYY 4x150 SE | 26 | 27 | 0.12726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3619-20_1_5_line_34 | NAYY 4x150 SE | 26 | 28 | 0.065257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3619-20_1_5_line_35 | NAYY 4x150 SE | 27 | 56 | 0.031099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3619-20_1_5_line_36 | NAYY 4x150 SE | 29 | 30 | 0.017785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3619-20_1_5_line_37 | NAYY 4x150 SE | 30 | 31 | 0.040385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3619-20_1_5_line_38 | NAYY 4x150 SE | 31 | 32 | 0.33717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_3619-20_1_5_line_39 | NAYY 4x150 SE | 32 | 33 | 0.073021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_3619-20_1_5_line_40 | NAYY 4x150 SE | 33 | 79 | 0.1199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_3619-20_1_5_line_41 | NAYY 4x150 SE | 34 | 35 | 0.032799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3619-20_1_5_line_42 | NAYY 4x150 SE | 36 | 37 | 0.13924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3619-20_1_5_line_43 | NAYY 4x150 SE | 36 | 38 | 0.044534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3619-20_1_5_line_44 | NAYY 4x150 SE | 37 | 39 | 0.18285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3619-20_1_5_line_45 | NAYY 4x150 SE | 39 | 40 | 0.1778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3619-20_1_5_line_46 | NAYY 4x150 SE | 39 | 41 | 0.022779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3619-20_1_5_line_47 | NAYY 4x150 SE | 40 | 42 | 0.070023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3619-20_1_5_line_48 | NAYY 4x150 SE | 41 | 43 | 0.069005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3619-20_1_5_line_49 | NAYY 4x150 SE | 42 | 44 | 0.19751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3619-20_1_5_line_50 | NAYY 4x150 SE | 42 | 45 | 0.10204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3619-20_1_5_line_51 | NAYY 4x150 SE | 44 | 46 | 0.04646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3619-20_1_5_line_52 | NAYY 4x150 SE | 44 | 47 | 0.057128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3619-20_1_5_line_53 | NAYY 4x150 SE | 46 | 48 | 0.049349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3619-20_1_5_line_54 | NAYY 4x150 SE | 47 | 49 | 0.21754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3619-20_1_5_line_55 | NAYY 4x150 SE | 48 | 50 | 0.00181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3619-20_1_5_line_56 | NAYY 4x150 SE | 49 | 51 | 0.034444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3619-20_1_5_line_57 | NAYY 4x150 SE | 50 | 55 | 0.021702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3619-20_1_5_line_58 | NAYY 4x150 SE | 51 | 52 | 0.0037725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3619-20_1_5_line_59 | NAYY 4x150 SE | 52 | 53 | 0.21781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_3619-20_1_5_line_60 | NAYY 4x150 SE | 53 | 54 | 0.018987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_3619-20_1_5_line_61 | NAYY 4x150 SE | 54 | 84 | 0.039097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_3619-20_1_5_line_62 | NAYY 4x150 SE | 56 | 57 | 0.036279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3619-20_1_5_line_63 | NAYY 4x150 SE | 57 | 58 | 0.034699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3619-20_1_5_line_64 | NAYY 4x150 SE | 58 | 59 | 0.15799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3619-20_1_5_line_65 | NAYY 4x150 SE | 59 | 60 | 0.0049511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3619-20_1_5_line_66 | NAYY 4x150 SE | 59 | 61 | 0.22204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3619-20_1_5_line_67 | NAYY 4x150 SE | 60 | 62 | 0.0078269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3619-20_1_5_line_68 | NAYY 4x150 SE | 61 | 63 | 0.19977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3619-20_1_5_line_69 | NAYY 4x150 SE | 62 | 64 | 0.010012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3619-20_1_5_line_70 | NAYY 4x150 SE | 63 | 66 | 0.059846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3619-20_1_5_line_71 | NAYY 4x150 SE | 64 | 65 | 0.046715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3619-20_1_5_line_72 | NAYY 4x150 SE | 66 | 76 | 0.078342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3619-20_1_5_line_73 | NAYY 4x150 SE | 67 | 68 | 0.0056149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3619-20_1_5_line_74 | NAYY 4x150 SE | 67 | 69 | 0.24711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3619-20_1_5_line_75 | NAYY 4x150 SE | 68 | 70 | 0.19 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3619-20_1_5_line_76 | NAYY 4x150 SE | 69 | 71 | 0.053554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3619-20_1_5_line_77 | NAYY 4x150 SE | 71 | 72 | 0.078157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3619-20_1_5_line_78 | NAYY 4x150 SE | 72 | 73 | 0.093492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3619-20_1_5_line_79 | NAYY 4x150 SE | 73 | 74 | 0.15205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3619-20_1_5_line_80 | NAYY 4x150 SE | 74 | 75 | 0.0080803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3619-20_1_5_line_81 | NAYY 4x150 SE | 75 | 76 | 0.040715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3619-20_1_5_line_82 | NAYY 4x150 SE | 77 | 78 | 0.015632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_3619-20_1_5_line_83 | NAYY 4x150 SE | 77 | 79 | 0.20082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_3619-20_1_5_line_84 | NAYY 4x150 SE | 78 | 80 | 0.12575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_3619-20_1_5_line_85 | NAYY 4x150 SE | 80 | 81 | 0.12286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_3619-20_1_5_line_86 | NAYY 4x150 SE | 81 | 82 | 0.14129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_3619-20_1_5_line_87 | NAYY 4x150 SE | 82 | 84 | 0.13161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_3619-20_1_5_line_88 | NAYY 4x150 SE | 85 | 86 | 0.044678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3619-20_1_5_line_89 | NAYY 4x150 SE | 86 | 118 | 0.052883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3619-20_1_5_line_90 | NAYY 4x150 SE | 88 | 91 | 0.32554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3619-20_1_5_line_91 | NAYY 4x150 SE | 89 | 90 | 0.11809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_3619-20_1_5_line_92 | NAYY 4x150 SE | 89 | 91 | 0.074302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_3619-20_1_5_line_93 | NAYY 4x150 SE | 90 | 92 | 0.14971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_3619-20_1_5_line_94 | NAYY 4x150 SE | 91 | 93 | 0.0060987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_3619-20_1_5_line_95 | NAYY 4x150 SE | 92 | 94 | 0.17344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_3619-20_1_5_line_96 | NAYY 4x150 SE | 93 | 95 | 0.053209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_3619-20_1_5_line_97 | NAYY 4x150 SE | 94 | 98 | 0.080835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_3619-20_1_5_line_98 | NAYY 4x150 SE | 95 | 96 | 0.064935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_3619-20_1_5_line_99 | NAYY 4x150 SE | 96 | 97 | 0.0033749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_3619-20_1_5_line_100 | NAYY 4x150 SE | 97 | 117 | 0.0015502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_3619-20_1_5_line_101 | NAYY 4x150 SE | 98 | 119 | 0.0060507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_3619-20_1_5_line_102 | NAYY 4x150 SE | 99 | 100 | 0.28417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3619-20_1_5_line_103 | NAYY 4x150 SE | 100 | 101 | 0.078894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3619-20_1_5_line_104 | NAYY 4x150 SE | 101 | 103 | 0.025667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3619-20_1_5_line_105 | NAYY 4x150 SE | 102 | 104 | 0.082031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3619-20_1_5_line_106 | NAYY 4x150 SE | 103 | 105 | 0.052614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3619-20_1_5_line_107 | NAYY 4x150 SE | 103 | 106 | 0.10369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
108 | LV_3619-20_1_5_line_108 | NAYY 4x150 SE | 104 | 107 | 0.10272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3619-20_1_5_line_109 | NAYY 4x150 SE | 106 | 127 | 0.20378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3619-20_1_5_line_110 | NAYY 4x150 SE | 106 | 120 | 0.01095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_3619-20_1_5_line_111 | NAYY 4x150 SE | 107 | 129 | 0.24101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3619-20_1_5_line_112 | NAYY 4x150 SE | 108 | 109 | 0.02244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_3619-20_1_5_line_113 | NAYY 4x150 SE | 109 | 110 | 0.15624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3619-20_1_5_line_114 | NAYY 4x150 SE | 110 | 114 | 0.016695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3619-20_1_5_line_115 | NAYY 4x150 SE | 111 | 112 | 0.23025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3619-20_1_5_line_116 | NAYY 4x150 SE | 111 | 113 | 0.18231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3619-20_1_5_line_117 | NAYY 4x150 SE | 112 | 132 | 0.063278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3619-20_1_5_line_118 | NAYY 4x150 SE | 113 | 131 | 0.037637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3619-20_1_5_line_119 | NAYY 4x150 SE | 114 | 125 | 0.32533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3619-20_1_5_line_120 | NAYY 4x150 SE | 114 | 131 | 0.19159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3619-20_1_5_line_121 | NAYY 4x150 SE | 114 | 130 | 0.18958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3619-20_1_5_line_122 | NAYY 4x150 SE | 115 | 116 | 0.027993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_3619-20_1_5_line_123 | NAYY 4x150 SE | 116 | 117 | 0.063461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
124 | LV_3619-20_1_5_line_124 | NAYY 4x150 SE | 119 | 120 | 0.17767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_3619-20_1_5_line_125 | NAYY 4x150 SE | 121 | 122 | 0.12864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3619-20_1_5_line_126 | NAYY 4x150 SE | 122 | 123 | 0.23167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3619-20_1_5_line_127 | NAYY 4x150 SE | 122 | 124 | 0.19558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3619-20_1_5_line_128 | NAYY 4x150 SE | 123 | 125 | 0.011519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3619-20_1_5_line_129 | NAYY 4x150 SE | 124 | 126 | 0.22576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3619-20_1_5_line_130 | NAYY 4x150 SE | 126 | 136 | 0.23931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3619-20_1_5_line_131 | NAYY 4x150 SE | 127 | 128 | 0.0068125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3619-20_1_5_line_132 | NAYY 4x150 SE | 129 | 130 | 0.056279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3619-20_1_5_line_133 | NAYY 4x150 SE | 132 | 133 | 0.03912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3619-20_1_5_line_134 | NAYY 4x150 SE | 133 | 134 | 0.021575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3619-20_1_5_line_135 | NAYY 4x150 SE | 134 | 135 | 0.093074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3619-20_1_5_trafo_125 | 0.25 MVA 20/0.4 kV | 137 | 53 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2729126.1403 | 1184017.2211 | 2728869.1139 | 1184044.404
1 | 2729133.7196 | 1183990.4486 | 2729127.0909 | 1184008.9308 | 2729126.1403 | 1184017.2211
2 | 2729130.2673 | 1184116.9575 | 2729118.27 | 1184103.8781 | 2729114.4824 | 1184087.5844 | 2729116.8121 | 1184075.5145 | 2729122.6847 | 1184052.1347 | 2729124.9465 | 1184027.6319 | 2729126.1403 | 1184017.2211
3 | 2729250.9167 | 1184589.1437 | 2729232.6326 | 1184591.8069 | 2729213.9968 | 1184596.6085
4 | 2729159.3889 | 1184597.8766 | 2729194.669 | 1184595.2686 | 2729213.9968 | 1184596.6085
5 | 2729159.3889 | 1184597.8766 | 2729179.8204 | 1184580.9711 | 2729190.2841 | 1184565.9855 | 2729210.9882 | 1184546.0171
6 | 2729159.3889 | 1184597.8766 | 2729086.6769 | 1184488.6173
7 | 2730280.477 | 1185036.9978 | 2730263.2998 | 1185031.6314 | 2730236.3877 | 1185034.682 | 2730247.8779 | 1185071.2259 | 2730245.2091 | 1185089.3147 | 2730234.6872 | 1185091.799 | 2730189.3167 | 1185064.5036
8 | 2730280.477 | 1185036.9978 | 2730268.0949 | 1185020.3939 | 2730268.0949 | 1185020.3939
9 | 2730280.477 | 1185036.9978 | 2730290.8113 | 1185045.5657
10 | 2730484.4915 | 1185122.6177 | 2730522.0245 | 1185125.7325 | 2730550.8094 | 1185120.4668 | 2730596.5031 | 1185070.2026 | 2730665.4998 | 1185067.7267
11 | 2730470.237 | 1185121.4347 | 2730484.4915 | 1185122.6177
12 | 2730718.9979 | 1184879.1526 | 2730665.4998 | 1185067.7267
13 | 2730470.237 | 1185121.4347 | 2730458.9253 | 1185118.464 | 2730446.978 | 1185123.641 | 2730354.4422 | 1185109.839 | 2730332.5356 | 1185091.6599 | 2730319.8142 | 1185069.6111 | 2730290.8113 | 1185045.5657
14 | 2730790.6696 | 1184838.4936 | 2730782.392 | 1184852.4047 | 2730771.7402 | 1184860.8007 | 2730747.0644 | 1184865.2434 | 2730718.9979 | 1184879.1526
15 | 2730620.1804 | 1184840.2461 | 2730620.1804 | 1184840.2461 | 2730707.228 | 1184876.1713 | 2730718.9979 | 1184879.1526 | 2730718.9979 | 1184879.1526
16 | 2730583.6136 | 1184831.6896 | 2730599.1348 | 1184845.2356 | 2730610.9544 | 1184845.9493 | 2730620.1804 | 1184840.2461
17 | 2730510.1447 | 1184772.9757 | 2730510.1447 | 1184772.9757 | 2730563.4084 | 1184814.0558 | 2730583.6136 | 1184831.6896
18 | 2730489.9961 | 1184674.0849 | 2730557.9797 | 1184749.9672 | 2730556.3959 | 1184759.9179 | 2730501.7645 | 1184760.5394 | 2730510.1447 | 1184772.9757
19 | 2729715.048 | 1184311.5768 | 2729899.4103 | 1184406.8862
20 | 2729670.431 | 1184240.2913 | 2729673.4462 | 1184247.3952 | 2729671.8717 | 1184264.7407 | 2729675.5906 | 1184274.2617 | 2729686.3169 | 1184298.3562 | 2729697.7137 | 1184306.2977 | 2729715.048 | 1184311.5768
21 | 2729899.4103 | 1184406.8862 | 2729906.7693 | 1184416.8421 | 2729913.2052 | 1184431.6816 | 2729917.1027 | 1184450.5468 | 2729916.9032 | 1184459.7383 | 2729908.7953 | 1184493.4544 | 2729902.0823 | 1184510.0435 | 2729896.1954 | 1184517.0655 | 2729890.5944 | 1184520.4133 | 2729879.7134 | 1184521.8118 | 2729868.2098 | 1184523.397 | 2729857.0486 | 1184527.8585 | 2729835.1111 | 1184538.4021 | 2729832.8461 | 1184540.3742
22 | 2730052.4228 | 1184393.0735 | 2729899.4103 | 1184406.8862
23 | 2729670.431 | 1184240.2913 | 2729656.2724 | 1184242.4532 | 2729636.7598 | 1184257.7091 | 2729621.2051 | 1184270.3932 | 2729613.0114 | 1184272.8623 | 2729606.3012 | 1184272.4168 | 2729602.8909 | 1184270.9227
24 | 2729670.431 | 1184240.2913 | 2729669.3848 | 1184234.2975 | 2729687.1855 | 1184208.886 | 2729713.8486 | 1184197.3878 | 2729720.0553 | 1184191.4733 | 2729728.9553 | 1184175.0871 | 2729748.7073 | 1184161.4935 | 2729755.0255 | 1184150.4331 | 2729757.3114 | 1184135.1601 | 2729750.5368 | 1184134.8576 | 2729743.6772 | 1184138.8343 | 2729736.6144 | 1184143.3737 | 2729730.9131 | 1184143.9396
25 | 2730790.6696 | 1184838.4936 | 2730803.1754 | 1184817.4766 | 2730809.3874 | 1184804.0021 | 2730818.9723 | 1184802.8549 | 2730845.4398 | 1184820.2125 | 2730854.2077 | 1184821.8634
26 | 2730939.7201 | 1184091.2911 | 2730971.7585 | 1184369.8504
27 | 2730939.7201 | 1184091.2911 | 2730975.2549 | 1184089.4551 | 2730978.27 | 1184088.7638
28 | 2730894.6439 | 1184382.5361 | 2730894.6439 | 1184382.5361 | 2730910.0592 | 1184374.9449 | 2730927.1679 | 1184370.2374 | 2730943.0279 | 1184368.1602 | 2730971.7585 | 1184369.8504
29 | 2730978.27 | 1184088.7638 | 2731003.9902 | 1184082.8672 | 2731005.6312 | 1184083.0269
30 | 2730268.0949 | 1185020.3939 | 2730201.215 | 1184977.6638 | 2730195.4582 | 1184970.2776 | 2730192.7688 | 1184947.5354 | 2730182.0919 | 1184936.4173 | 2730170.1387 | 1184878.9924 | 2730173.7057 | 1184861.3789 | 2730164.8803 | 1184845.8042
31 | 2730489.9961 | 1184674.0849 | 2730484.3722 | 1184644.9835
32 | 2731045.8178 | 1184846.1248 | 2731025.3796 | 1184854.0923 | 2730854.2077 | 1184821.8634
33 | 2731096.6265 | 1183978.9072 | 2731066.6518 | 1184102.5855
34 | 2731005.6312 | 1184083.0269 | 2731034.4867 | 1184085.8362 | 2731066.6518 | 1184102.5855 | 2731066.6518 | 1184102.5855
35 | 2731096.6265 | 1183978.9072 | 2731076.8737 | 1183954.8866
36 | 2730156.1125 | 1184830.3311 | 2730164.8803 | 1184845.8042
37 | 2730156.1125 | 1184830.3311 | 2730155.7413 | 1184829.676 | 2730145.6479 | 1184791.3503
38 | 2730073.4228 | 1184462.0022 | 2730145.6479 | 1184791.3503
39 | 2730073.4228 | 1184462.0022 | 2730054.1513 | 1184417.9732 | 2730052.4228 | 1184393.0735
40 | 2730116.3073 | 1184352.8038 | 2730110.4521 | 1184340.3039 | 2730094.0817 | 1184325.8265 | 2730084.6661 | 1184328.6465 | 2730051.4525 | 1184379.0966 | 2730052.4228 | 1184393.0735
41 | 2730464.3396 | 1184619.085 | 2730484.2733 | 1184644.4714 | 2730484.3722 | 1184644.9835
42 | 2730753.2655 | 1184672.188 | 2730751.943 | 1184674.0062 | 2730774.5924 | 1184699.4529 | 2730837.6458 | 1184709.0032 | 2730873.5088 | 1184724.7119
43 | 2730916.7209 | 1184735.2279 | 2730876.8693 | 1184726.1838 | 2730873.5088 | 1184724.7119
44 | 2730912.9238 | 1184617.6343 | 2730865.0666 | 1184641.5402 | 2730844.97 | 1184665.6083 | 2730781.8413 | 1184680.1077 | 2730756.1625 | 1184668.205 | 2730753.2655 | 1184672.188
45 | 2730912.9238 | 1184617.6343 | 2730921.7518 | 1184609.2097 | 2730920.094 | 1184601.9125 | 2730899.2755 | 1184596.4647 | 2730848.5724 | 1184604.8858 | 2730839.4748 | 1184604.687 | 2730840.5812 | 1184595.6377 | 2730855.7624 | 1184588.2525 | 2730874.3838 | 1184569.156 | 2730883.3369 | 1184547.5143
46 | 2730912.9238 | 1184617.6343 | 2730935.6993 | 1184617.2199
47 | 2730933.4824 | 1184504.7097 | 2730904.2129 | 1184516.2678 | 2730891.6847 | 1184527.3358 | 2730883.3369 | 1184547.5143
48 | 2730897.1099 | 1184656.7516 | 2730935.0056 | 1184635.141 | 2730942.3782 | 1184621.692 | 2730940.9585 | 1184617.1243 | 2730935.6993 | 1184617.2199
49 | 2730933.4824 | 1184504.7097 | 2730954.2565 | 1184496.4909 | 2730961.2583 | 1184488.4823 | 2730955.9499 | 1184481.5611 | 2730855.7852 | 1184462.125 | 2730809.6895 | 1184467.9229 | 2730805.256 | 1184461.4879
50 | 2730933.4824 | 1184504.7097 | 2730971.9374 | 1184507.152 | 2730997.0433 | 1184527.1047 | 2731008.2885 | 1184533.155 | 2731009.7082 | 1184537.7229 | 2731006.3085 | 1184542.6856 | 2730998.2238 | 1184542.253
51 | 2730805.256 | 1184461.4879 | 2730837.2769 | 1184432.6987 | 2730839.7757 | 1184430.3936
52 | 2730805.256 | 1184461.4879 | 2730794.6921 | 1184471.0757 | 2730783.291 | 1184475.2966 | 2730772.2695 | 1184473.3213 | 2730761.9336 | 1184465.4787 | 2730755.4865 | 1184464.4217
53 | 2730839.7757 | 1184430.3936 | 2730874.9572 | 1184397.9399 | 2730876.1267 | 1184397.0248
54 | 2730548.2017 | 1184416.2513 | 2730574.948 | 1184423.8923 | 2730607.8476 | 1184432.4935 | 2730629.6349 | 1184436.2713 | 2730664.7507 | 1184453.8834 | 2730688.5021 | 1184466.6777 | 2730703.9161 | 1184468.5708 | 2730733.4549 | 1184465.6575 | 2730753.0921 | 1184464.0292 | 2730755.4865 | 1184464.4217
55 | 2730877.5522 | 1184395.9094 | 2730876.1267 | 1184397.0248
56 | 2730548.2017 | 1184416.2513 | 2730528.9749 | 1184410.7586 | 2730514.5972 | 1184409.3379
57 | 2730877.5522 | 1184395.9094 | 2730894.6439 | 1184382.5361
58 | 2730510.8429 | 1184408.967 | 2730514.5972 | 1184409.3379
59 | 2730510.8429 | 1184408.967 | 2730498.3666 | 1184407.7341 | 2730483.8452 | 1184401.3131 | 2730462.5866 | 1184384.8268 | 2730434.0187 | 1184367.0026 | 2730421.7431 | 1184352.1243 | 2730402.6998 | 1184329.2705 | 2730376.2041 | 1184296.5695 | 2730366.1421 | 1184288.7336 | 2730350.7778 | 1184275.4116 | 2730348.1374 | 1184271.6304
60 | 2730337.5798 | 1184255.8671 | 2730339.4401 | 1184259.175 | 2730348.1374 | 1184271.6304
61 | 2730319.966 | 1184221.0007 | 2730319.966 | 1184221.0007 | 2730328.5448 | 1184239.8013 | 2730337.5798 | 1184255.8671
62 | 2731076.8737 | 1183954.8866 | 2731060.998 | 1183935.5808 | 2731053.7427 | 1183926.9385
63 | 2731037.947 | 1183896.3762 | 2731047.9509 | 1183920.0394 | 2731053.7427 | 1183926.9385
64 | 2731037.947 | 1183896.3762 | 2730992.2949 | 1183788.3904 | 2730984.6299 | 1183769.075 | 2730976.833 | 1183760.6761 | 2730969.6317 | 1183756.1432
65 | 2730969.6317 | 1183756.1432 | 2730965.4416 | 1183753.5058
66 | 2730969.6317 | 1183756.1432 | 2731174.5192 | 1183670.5655
67 | 2730958.8177 | 1183749.3363 | 2730965.4416 | 1183753.5058
68 | 2731099.5981 | 1183485.3759 | 2731174.5192 | 1183670.5655
69 | 2730958.8177 | 1183749.3363 | 2730954.414 | 1183746.5644 | 2730950.114 | 1183744.4118
70 | 2731099.5981 | 1183485.3759 | 2731081.1499 | 1183428.4442
71 | 2730909.6626 | 1183721.7014 | 2730916.9785 | 1183728.3551 | 2730930.4216 | 1183734.5534 | 2730950.114 | 1183744.4118
72 | 2731092.4854 | 1183357.0907 | 2731075.3533 | 1183378.432 | 2731075.0667 | 1183409.6714 | 2731081.1499 | 1183428.4442
73 | 2730820.912 | 1183246.6183 | 2730819.628 | 1183241.1522
74 | 2730991.8912 | 1183113.0526 | 2730968.4891 | 1183107.4593 | 2730960.6732 | 1183106.1764 | 2730951.4112 | 1183105.707 | 2730944.3544 | 1183106.0309 | 2730938.0386 | 1183107.7497 | 2730931.6947 | 1183110.402 | 2730917.3211 | 1183119.1057 | 2730899.6338 | 1183130.906 | 2730884.1144 | 1183142.7648 | 2730874.6776 | 1183148.8967 | 2730851.6197 | 1183161.814 | 2730847.0961 | 1183164.7063 | 2730841.787 | 1183168.938 | 2730836.7547 | 1183175.8889 | 2730832.5203 | 1183183.0241 | 2730827.7363 | 1183193.294 | 2730819.8781 | 1183214.9276 | 2730818.5959 | 1183218.38 | 2730818.0008 | 1183220.8021 | 2730817.6536 | 1183224.1081 | 2730817.6442 | 1183228.0331 | 2730818.0994 | 1183232.3685 | 2730819.0532 | 1183238.7052 | 2730819.628 | 1183241.1522
75 | 2730820.912 | 1183246.6183 | 2730666.3746 | 1183357.1522
76 | 2730991.8912 | 1183113.0526 | 2731008.9477 | 1183117.5288 | 2731017.7956 | 1183120.1686 | 2731034.082 | 1183125.9846 | 2731040.7172 | 1183127.8199 | 2731043.1606 | 1183128.3895
77 | 2731102.0255 | 1183176.3193 | 2731097.257 | 1183174.3468 | 2731091.1557 | 1183169.0538 | 2731061.7955 | 1183135.5866 | 2731058.8677 | 1183132.9095 | 2731055.9836 | 1183131.3786 | 2731043.1606 | 1183128.3895
78 | 2731102.0255 | 1183176.3193 | 2731098.2168 | 1183232.0333 | 2731103.4972 | 1183236.441 | 2731113.2866 | 1183231.6516 | 2731132.7233 | 1183227.1623
79 | 2731132.7233 | 1183227.1623 | 2731126.7125 | 1183235.5371 | 2731122.5474 | 1183246.1206 | 2731123.0501 | 1183283.1594 | 2731120.243 | 1183291.3708 | 2731115.7238 | 1183298.2438 | 2731079.3657 | 1183332.5965 | 2731060.1507 | 1183350.7009
80 | 2731060.1507 | 1183350.7009 | 2731057.2514 | 1183358.2432
81 | 2731092.4854 | 1183357.0907 | 2731070.9905 | 1183365.6047 | 2731061.9826 | 1183365.4076 | 2731057.2514 | 1183358.2432
82 | 2730262.9467 | 1184472.7508 | 2730269.3643 | 1184474.5792 | 2730278.0132 | 1184472.2433
83 | 2730262.9467 | 1184472.7508 | 2730192.7154 | 1184452.7415 | 2730138.2413 | 1184399.6295 | 2730116.3073 | 1184352.8038
84 | 2730278.0132 | 1184472.2433 | 2730278.0132 | 1184472.2433 | 2730278.9168 | 1184465.4578 | 2730232.6925 | 1184416.8166 | 2730237.8826 | 1184399.0272 | 2730240.495 | 1184365.8575
85 | 2730240.495 | 1184365.8575 | 2730242.7776 | 1184336.8759 | 2730261.3192 | 1184309.8031 | 2730266.3447 | 1184299.5825 | 2730264.3171 | 1184276.599 | 2730270.1412 | 1184250.7326
86 | 2730255.4581 | 1184114.107 | 2730256.4848 | 1184125.1821 | 2730262.3501 | 1184134.6389 | 2730261.7891 | 1184148.4926 | 2730254.4413 | 1184184.3708 | 2730269.7323 | 1184236.887 | 2730270.1919 | 1184250.5072 | 2730270.1412 | 1184250.7326
87 | 2730255.4581 | 1184114.107 | 2730262.8003 | 1184114.6448 | 2730269.0809 | 1184120.4523 | 2730273.7544 | 1184136.5994 | 2730276.3373 | 1184154.7691 | 2730279.6896 | 1184169.1639 | 2730288.5556 | 1184182.8447 | 2730296.5045 | 1184193.4032 | 2730311.5259 | 1184210.5649 | 2730319.966 | 1184221.0007
88 | 2729730.9131 | 1184143.9396 | 2729727.1786 | 1184144.3034 | 2729720.9693 | 1184144.3468 | 2729708.9773 | 1184150.4696 | 2729689.1555 | 1184158.1336
89 | 2729649.5342 | 1184192.1588 | 2729658.986 | 1184181.6666 | 2729669.7751 | 1184170.0803 | 2729682.779 | 1184160.599 | 2729689.1555 | 1184158.1336
90 | 2729415.7616 | 1184333.5666 | 2729415.044 | 1184339.2109 | 2729411.4336 | 1184345.1484 | 2729400.1611 | 1184350.5201 | 2729387.0393 | 1184360.5554 | 2729375.9863 | 1184379.0972 | 2729370.3733 | 1184397.1451 | 2729366.2269 | 1184423.2973 | 2729352.9391 | 1184459.7598 | 2729340.4766 | 1184477.4596 | 2729320.0851 | 1184492.1193 | 2729302.4771 | 1184501.6464 | 2729287.5189 | 1184520.7156 | 2729283.2893 | 1184527.0513 | 2729266.7009 | 1184531.797 | 2729251.9355 | 1184546.9008 | 2729239.4327 | 1184547.0313 | 2729225.348 | 1184545.1038 | 2729210.9882 | 1184546.0171
91 | 2729352.6136 | 1184359.945 | 2729353.2988 | 1184352.2652 | 2729356.2776 | 1184347.6372 | 2729368.6632 | 1184333.5051 | 2729377.6995 | 1184318.8893 | 2729378.9093 | 1184312.0214 | 2729377.7045 | 1184304.5232 | 2729358.6334 | 1184264.0368 | 2729354.7397 | 1184255.2844
92 | 2729352.6136 | 1184359.945 | 2729357.5202 | 1184362.931 | 2729363.0941 | 1184362.9513 | 2729369.3413 | 1184356.9039 | 2729377.1764 | 1184345.5757 | 2729387.5329 | 1184340.1842 | 2729415.7616 | 1184333.5666
93 | 2729354.7397 | 1184255.2844 | 2729349.9525 | 1184244.5238 | 2729347.7436 | 1184229.0646 | 2729344.7229 | 1184193.206 | 2729346.9732 | 1184180.9454 | 2729359.0035 | 1184147.2244 | 2729363.1254 | 1184139.174 | 2729382.8444 | 1184117.8839 | 2729382.8444 | 1184117.8839
94 | 2729415.7616 | 1184333.5666 | 2729421.6915 | 1184332.1415
95 | 2729382.8444 | 1184117.8839 | 2729392.6358 | 1184102.6173 | 2729410.8877 | 1184067.2406 | 2729423.2194 | 1184049.9829 | 2729438.98 | 1184035.2012 | 2729466.7572 | 1184014.9194 | 2729480.1493 | 1184004.7901 | 2729493.7426 | 1183991.0069 | 2729495.3327 | 1183989.5894
96 | 2729473.385 | 1184319.5348 | 2729451.8005 | 1184324.9052 | 2729421.6915 | 1184332.1415
97 | 2729569.1127 | 1183963.2598 | 2729569.1127 | 1183963.2598 | 2729558.9597 | 1183965.2084 | 2729544.7061 | 1183965.3781 | 2729525.3567 | 1183969.5296 | 2729508.7709 | 1183977.6105 | 2729495.3327 | 1183989.5894
98 | 2729529.9162 | 1184292.3076 | 2729522.7404 | 1184302.3102 | 2729510.376 | 1184309.4372 | 2729491.232 | 1184315.0943 | 2729473.385 | 1184319.5348
99 | 2729529.9162 | 1184292.3076 | 2729531.8835 | 1184289.5654
100 | 2729531.8835 | 1184289.5654 | 2729532.7872 | 1184288.3058
101 | 2729571.8413 | 1183957.8592 | 2729571.8413 | 1183957.8592 | 2729569.1127 | 1183963.2598
102 | 2729130.2673 | 1184116.9575 | 2729147.033 | 1184132.3636 | 2729157.0623 | 1184150.2931 | 2729161.8361 | 1184176.7935 | 2729159.4745 | 1184187.5061 | 2729158.561 | 1184197.6384 | 2729162.1166 | 1184205.2096 | 2729170.6307 | 1184207.7061 | 2729176.1436 | 1184199.9413 | 2729177.1217 | 1184185.0402 | 2729161.5732 | 1184115.3421 | 2729162.9918 | 1184105.8656 | 2729169.2102 | 1184095.1361 | 2729188.5423 | 1184075.1157 | 2729213.5458 | 1184058.7836
103 | 2729279.5694 | 1184015.8607 | 2729257.7175 | 1184027.5163 | 2729223.1808 | 1184052.4901 | 2729213.5458 | 1184058.7836
104 | 2729302.2164 | 1184003.7808 | 2729279.5694 | 1184015.8607
105 | 2729133.7196 | 1183990.4486 | 2729137.0279 | 1183981.2243 | 2729141.387 | 1183965.7067 | 2729137.7442 | 1183951.551 | 2729132.1632 | 1183939.7998 | 2729132.2614 | 1183924.2681 | 2729136.3676 | 1183911.9808 | 2729136.3676 | 1183911.9808
106 | 2729302.2164 | 1184003.7808 | 2729304.4811 | 1183997.9254 | 2729321.4394 | 1183971.5161 | 2729331.4841 | 1183960.4431
107 | 2729391.3601 | 1183950.6654 | 2729375.1247 | 1183959.4992 | 2729345.2333 | 1183975.1323 | 2729302.2164 | 1184003.7808
108 | 2729196.4374 | 1183828.9104 | 2729164.4609 | 1183869.2322 | 2729143.3375 | 1183898.6322 | 2729136.3676 | 1183911.9808
109 | 2729391.3601 | 1183950.6654 | 2729475.3075 | 1183890.011 | 2729475.1162 | 1183878.0202 | 2729464.8113 | 1183860.4956 | 2729473.7292 | 1183839.3837 | 2729448.7173 | 1183802.0044
110 | 2729391.3601 | 1183950.6654 | 2729402.2141 | 1183949.2201
111 | 2729196.4374 | 1183828.9104 | 2729199.0964 | 1183825.5574 | 2729225.6299 | 1183796.0297 | 2729237.0905 | 1183787.9931 | 2729251.3769 | 1183784.5542 | 2729260.7516 | 1183777.629 | 2729266.5872 | 1183768.7372 | 2729268.6057 | 1183753.7696 | 2729268.2285 | 1183740.8185 | 2729270.2516 | 1183725.2839 | 2729280.2836 | 1183705.6078 | 2729298.7846 | 1183684.5357 | 2729309.6538 | 1183670.3041 | 2729319.3529 | 1183652.9671 | 2729324.5791 | 1183639.5244
112 | 2729356.5429 | 1183480.3114 | 2729362.6504 | 1183487.356 | 2729371.3405 | 1183497.181
113 | 2729371.3405 | 1183497.181 | 2729395.7585 | 1183524.7875 | 2729411.9156 | 1183539.0692 | 2729433.1908 | 1183550.8152 | 2729448.3424 | 1183559.6713 | 2729464.1532 | 1183570.532 | 2729474.5352 | 1183570.0337 | 2729500.9118 | 1183569.0695
114 | 2729514.887 | 1183577.5779 | 2729510.1411 | 1183572.7829 | 2729500.9118 | 1183569.0695
115 | 2729486.9626 | 1183294.7861 | 2729547.9008 | 1183072.7487
116 | 2729602.4512 | 1183402.318 | 2729575.5382 | 1183394.1522 | 2729553.0774 | 1183377.532 | 2729536.1423 | 1183363.9003 | 2729510.6327 | 1183362.5257 | 2729499.7039 | 1183357.9195 | 2729488.5154 | 1183339.186 | 2729483.577 | 1183321.0325 | 2729486.9626 | 1183294.7861 | 2729486.9626 | 1183294.7861
117 | 2729547.9008 | 1183072.7487 | 2729563.9033 | 1183072.6834 | 2729583.9498 | 1183068.2135 | 2729608.9842 | 1183058.8257
118 | 2729631.8425 | 1183425.8267 | 2729602.4512 | 1183402.318
119 | 2729514.887 | 1183577.5779 | 2729566.4314 | 1183572.2102 | 2729630.9324 | 1183579.0101 | 2729705.6769 | 1183592.7598 | 2729767.5874 | 1183612.3035 | 2729789.4848 | 1183608.3414 | 2729812.7971 | 1183613.0943 | 2729834.149 | 1183609.3384
120 | 2729514.887 | 1183577.5779 | 2729631.8425 | 1183425.8267
121 | 2729514.887 | 1183577.5779 | 2729513.9242 | 1183586.4303 | 2729509.9336 | 1183590.1469 | 2729501.7561 | 1183590.4148 | 2729485.4079 | 1183586.0472 | 2729460.9145 | 1183587.1633 | 2729439.196 | 1183584.9815 | 2729413.298 | 1183578.295 | 2729393.1509 | 1183571.5994 | 2729378.4961 | 1183566.2568 | 2729357.4515 | 1183575.2982 | 2729345.9763 | 1183588.2268 | 2729345.9763 | 1183588.2268
122 | 2729602.8909 | 1184270.9227 | 2729579.5228 | 1184260.6845 | 2729577.1765 | 1184259.879
123 | 2729577.1765 | 1184259.879 | 2729565.2119 | 1184255.7714 | 2729552.2615 | 1184256.4475 | 2729545.331 | 1184263.0025 | 2729539.158 | 1184273.3768 | 2729532.7872 | 1184288.3058 | 2729532.7872 | 1184288.3058
124 | 2729571.8413 | 1183957.8592 | 2729569.9999 | 1183950.8475 | 2729562.212 | 1183947.5989 | 2729534.8239 | 1183948.4519 | 2729519.3352 | 1183945.3481 | 2729494.2848 | 1183939.4468 | 2729471.4077 | 1183938.9855 | 2729448.0574 | 1183940.2821 | 2729423.404 | 1183946.3986 | 2729402.2141 | 1183949.2201
125 | 2730071.9728 | 1183618.907 | 2730062.9085 | 1183626.2491 | 2730021.2404 | 1183638.2205 | 2729958.6724 | 1183677.0211
126 | 2730071.9728 | 1183618.907 | 2730064.0733 | 1183613.4092 | 2730027.5082 | 1183616.1623 | 2729938.1917 | 1183628.8679 | 2729845.4939 | 1183607.3427
127 | 2730071.9728 | 1183618.907 | 2730087.365 | 1183611.0129 | 2730100.143 | 1183609.5559 | 2730109.174 | 1183613.9441 | 2730124.4513 | 1183617.3116 | 2730128.4099 | 1183615.0848 | 2730125.3741 | 1183608.236 | 2730127.4463 | 1183599.3299 | 2730132.9087 | 1183594.6784 | 2730143.2758 | 1183591.0007 | 2730149.08 | 1183583.6213 | 2730147.3624 | 1183566.7158 | 2730151.0385 | 1183557.8112 | 2730175.8105 | 1183549.165 | 2730208.0976 | 1183539.1144 | 2730211.1603 | 1183535.5894
128 | 2729834.149 | 1183609.3384 | 2729845.4939 | 1183607.3427
129 | 2730211.1603 | 1183535.5894 | 2730220.7266 | 1183534.3296 | 2730326.6958 | 1183540.8602 | 2730355.527 | 1183548.8933 | 2730397.9431 | 1183582.6079 | 2730414.7667 | 1183589.6681 | 2730421.5609 | 1183586.2912 | 2730421.5609 | 1183586.2912
130 | 2730275.508 | 1183405.7986 | 2730281.3564 | 1183414.0018 | 2730315.3176 | 1183429.8965 | 2730338.4203 | 1183473.4203 | 2730420.4479 | 1183572.5234 | 2730421.5609 | 1183586.2912
131 | 2729442.0094 | 1183803.1937 | 2729448.7173 | 1183802.0044
132 | 2729345.9763 | 1183588.2268 | 2729335.0715 | 1183604.0922 | 2729329.5173 | 1183626.8226 | 2729324.5791 | 1183639.5244
133 | 2729647.621 | 1183054.3245 | 2729614.928 | 1183056.5969 | 2729608.9842 | 1183058.8257
134 | 2729647.621 | 1183054.3245 | 2729666.3857 | 1183064.9717 | 2729666.3857 | 1183064.9717
135 | 2729666.3857 | 1183064.9717 | 2729685.433 | 1183067.4968 | 2729743.2618 | 1183108.6012 | 2729746.0766 | 1183109.3448

## bus_geodata
| x | y | coords
0 | 2728869.1139 | 1184044.404
1 | 2729126.1403 | 1184017.2211
2 | 2729213.9968 | 1184596.6085
3 | 2729250.9167 | 1184589.1437
4 | 2729159.3889 | 1184597.8766
5 | 2730189.3167 | 1185064.5036
6 | 2730280.477 | 1185036.9978
7 | 2730484.4915 | 1185122.6177
8 | 2730665.4998 | 1185067.7267
9 | 2730470.237 | 1185121.4347
10 | 2730718.9979 | 1184879.1526
11 | 2730290.8113 | 1185045.5657
12 | 2730583.6136 | 1184831.6896
13 | 2730620.1804 | 1184840.2461
14 | 2730510.1447 | 1184772.9757
15 | 2729715.048 | 1184311.5768
16 | 2729899.4103 | 1184406.8862
17 | 2729670.431 | 1184240.2913
18 | 2730790.6696 | 1184838.4936
19 | 2730939.7201 | 1184091.2911
20 | 2730971.7585 | 1184369.8504
21 | 2730978.27 | 1184088.7638
22 | 2730268.0949 | 1185020.3939
23 | 2730489.9961 | 1184674.0849
24 | 2731045.8178 | 1184846.1248
25 | 2730854.2077 | 1184821.8634
26 | 2731066.6518 | 1184102.5855
27 | 2731096.6265 | 1183978.9072
28 | 2731005.6312 | 1184083.0269
29 | 2730164.8803 | 1184845.8042
30 | 2730156.1125 | 1184830.3311
31 | 2730145.6479 | 1184791.3503
32 | 2730073.4228 | 1184462.0022
33 | 2730052.4228 | 1184393.0735
34 | 2730484.3722 | 1184644.9835
35 | 2730464.3396 | 1184619.085
36 | 2730873.5088 | 1184724.7119
37 | 2730753.2655 | 1184672.188
38 | 2730916.7209 | 1184735.2279
39 | 2730912.9238 | 1184617.6343
40 | 2730883.3369 | 1184547.5143
41 | 2730935.6993 | 1184617.2199
42 | 2730933.4824 | 1184504.7097
43 | 2730897.1099 | 1184656.7516
44 | 2730805.256 | 1184461.4879
45 | 2730998.2238 | 1184542.253
46 | 2730839.7757 | 1184430.3936
47 | 2730755.4865 | 1184464.4217
48 | 2730876.1267 | 1184397.0248
49 | 2730548.2017 | 1184416.2513
50 | 2730877.5522 | 1184395.9094
51 | 2730514.5972 | 1184409.3379
52 | 2730510.843 | 1184408.967
53 | 2730348.1375 | 1184271.6304
54 | 2730337.5798 | 1184255.8671
55 | 2730894.6439 | 1184382.5361
56 | 2731076.8737 | 1183954.8866
57 | 2731053.7427 | 1183926.9385
58 | 2731037.947 | 1183896.3762
59 | 2730969.6317 | 1183756.1432
60 | 2730965.4416 | 1183753.5058
61 | 2731174.5192 | 1183670.5655
62 | 2730958.8177 | 1183749.3363
63 | 2731099.5982 | 1183485.3759
64 | 2730950.114 | 1183744.4118
65 | 2730909.6626 | 1183721.7014
66 | 2731081.1499 | 1183428.4442
67 | 2730819.628 | 1183241.1522
68 | 2730820.912 | 1183246.6183
69 | 2730991.8912 | 1183113.0526
70 | 2730666.3746 | 1183357.1522
71 | 2731043.1606 | 1183128.3895
72 | 2731102.0255 | 1183176.3193
73 | 2731132.7233 | 1183227.1623
74 | 2731060.1507 | 1183350.7009
75 | 2731057.2514 | 1183358.2432
76 | 2731092.4854 | 1183357.0907
77 | 2730262.9467 | 1184472.7508
78 | 2730278.0132 | 1184472.2433
79 | 2730116.3073 | 1184352.8038
80 | 2730240.495 | 1184365.8575
81 | 2730270.1412 | 1184250.7326
82 | 2730255.4581 | 1184114.107
83 | 2729832.8461 | 1184540.3742
84 | 2730319.966 | 1184221.0007
85 | 2729730.9131 | 1184143.9396
86 | 2729689.1555 | 1184158.1336
87 | 2729086.6769 | 1184488.6173
88 | 2729210.9882 | 1184546.0171
89 | 2729352.6136 | 1184359.945
90 | 2729354.7397 | 1184255.2844
91 | 2729415.7616 | 1184333.5666
92 | 2729382.8444 | 1184117.8839
93 | 2729421.6915 | 1184332.1415
94 | 2729495.3327 | 1183989.5894
95 | 2729473.385 | 1184319.5348
96 | 2729529.9163 | 1184292.3076
97 | 2729531.8835 | 1184289.5654
98 | 2729569.1127 | 1183963.2598
99 | 2729130.2673 | 1184116.9575
100 | 2729213.5458 | 1184058.7836
101 | 2729279.5694 | 1184015.8607
102 | 2729133.7196 | 1183990.4486
103 | 2729302.2164 | 1184003.7808
104 | 2729136.3676 | 1183911.9808
105 | 2729331.4841 | 1183960.4431
106 | 2729391.3601 | 1183950.6654
107 | 2729196.4374 | 1183828.9104
108 | 2729356.5429 | 1183480.3114
109 | 2729371.3405 | 1183497.181
110 | 2729500.9118 | 1183569.0695
111 | 2729486.9626 | 1183294.7861
112 | 2729547.9008 | 1183072.7487
113 | 2729602.4512 | 1183402.318
114 | 2729514.887 | 1183577.5779
115 | 2729602.8909 | 1184270.9227
116 | 2729577.1765 | 1184259.879
117 | 2729532.7872 | 1184288.3058
118 | 2729649.5342 | 1184192.1588
119 | 2729571.8413 | 1183957.8592
120 | 2729402.2141 | 1183949.2201
121 | 2729958.6724 | 1183677.0211
122 | 2730071.9728 | 1183618.907
123 | 2729845.4939 | 1183607.3427
124 | 2730211.1603 | 1183535.5894
125 | 2729834.149 | 1183609.3384
126 | 2730421.5609 | 1183586.2912
127 | 2729448.7173 | 1183802.0044
128 | 2729442.0094 | 1183803.1937
129 | 2729324.5791 | 1183639.5244
130 | 2729345.9763 | 1183588.2268
131 | 2729631.8425 | 1183425.8267
132 | 2729608.9842 | 1183058.8257
133 | 2729647.621 | 1183054.3245
134 | 2729666.3857 | 1183064.9717
135 | 2729746.0766 | 1183109.3448
136 | 2730275.508 | 1183405.7986
137 | 2730348.1375 | 1184271.6304

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1