## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3619-23_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3619-23_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3619-23_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3619-23_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3619-23_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3619-23_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3619-23_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3619-23_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_3619-23_0_2_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_3619-23_0_2_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_3619-23_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_3619-23_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_3619-23_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_3619-23_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_3619-23_0_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_3619-23_0_2_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_3619-23_0_2_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_3619-23_0_2_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_3619-23_0_2_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_3619-23_0_2_node_43 | 0.4 | n |  | TRUE
20 | bus_LV_3619-23_0_2_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_3619-23_0_2_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_3619-23_0_2_node_45 | 0.4 | n |  | TRUE
23 | bus_LV_3619-23_0_2_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_3619-23_0_2_node_46 | 0.4 | n |  | TRUE
25 | bus_LV_3619-23_0_2_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_3619-23_0_2_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_3619-23_0_2_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_3619-23_0_2_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_3619-23_0_2_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_3619-23_0_2_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_3619-23_0_2_node_56 | 0.4 | n |  | TRUE
32 | bus_LV_3619-23_0_2_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_3619-23_0_2_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_3619-23_0_2_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_3619-23_0_2_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_3619-23_0_2_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_3619-23_0_2_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_3619-23_0_2_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_3619-23_0_2_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_3619-23_0_2_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_3619-23_0_2_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_3619-23_0_2_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_3619-23_0_2_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_3619-23_0_2_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_3619-23_0_2_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_3619-23_0_2_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_3619-23_0_2_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_3619-23_0_2_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_3619-23_0_2_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_3619-23_0_2_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_3619-23_0_2_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_3619-23_0_2_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_3619-23_0_2_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_3619-23_0_2_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_3619-23_0_2_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_3619-23_0_2_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_3619-23_0_2_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_3619-23_0_2_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_3619-23_0_2_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_3619-23_0_2_node_38 | 0.4 | n |  | TRUE
61 | bus_MV_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3619-23_0_2_load_0 | 0 | 0.00027143 | 6.8027e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3619-23_0_2_load_1 | 1 | 0.00025981 | 6.5115e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3619-23_0_2_load_2 | 2 | 0.00029606 | 7.42e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3619-23_0_2_load_3 | 3 | 0.00029887 | 7.4904e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3619-23_0_2_load_4 | 4 | 0.00044387 | 0.00011125 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3619-23_0_2_load_5 | 5 | 0.00026377 | 6.6107e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3619-23_0_2_load_6 | 6 | 0.00024873 | 6.2337e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3619-23_0_2_load_7 | 7 | 0.00028995 | 7.2668e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3619-23_0_2_load_27 | 8 | 0.00037459 | 9.3881e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3619-23_0_2_load_8 | 10 | 0.00036256 | 9.0866e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3619-23_0_2_load_9 | 11 | 0.00031102 | 7.7948e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3619-23_0_2_load_10 | 12 | 0.0004652 | 0.00011659 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3619-23_0_2_load_11 | 13 | 0.0003281 | 8.223e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3619-23_0_2_load_39 | 15 | 0.00050481 | 0.00012652 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3619-23_0_2_load_40 | 16 | 0.00067388 | 0.00016889 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3619-23_0_2_load_41 | 17 | 0.0019456 | 0.00048762 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3619-23_0_2_load_42 | 18 | 0.00054282 | 0.00013604 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3619-23_0_2_load_43 | 19 | 0.00049645 | 0.00012442 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3619-23_0_2_load_44 | 20 | 0.00047776 | 0.00011974 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3619-23_0_2_load_31 | 21 | 0.00053956 | 0.00013523 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3619-23_0_2_load_49 | 23 | 0.00035648 | 8.9343e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3619-23_0_2_load_46 | 24 | 0.00072909 | 0.00018273 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3619-23_0_2_load_47 | 25 | 0.00035349 | 8.8592e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3619-23_0_2_load_48 | 26 | 0.0008473 | 0.00021235 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3619-23_0_2_load_50 | 27 | 0.00032527 | 8.152e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3619-23_0_2_load_51 | 28 | 0.00044999 | 0.00011278 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3619-23_0_2_load_13 | 29 | 0.0003931 | 9.8521e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3619-23_0_2_load_14 | 30 | 0.0003401 | 8.5237e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3619-23_0_2_load_56 | 31 | 0.00039428 | 9.8816e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3619-23_0_2_load_18 | 32 | 0.0003889 | 9.7467e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3619-23_0_2_load_15 | 33 | 0.00029994 | 7.5172e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3619-23_0_2_load_30 | 34 | 0.0015649 | 0.0003922 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3619-23_0_2_load_16 | 35 | 0.00053836 | 0.00013493 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3619-23_0_2_load_17 | 36 | 0.00041168 | 0.00010318 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3619-23_0_2_load_29 | 37 | 0.00024853 | 6.2288e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3619-23_0_2_load_19 | 38 | 0.0004656 | 0.00011669 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3619-23_0_2_load_20 | 39 | 0.00037221 | 9.3284e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3619-23_0_2_load_24 | 42 | 0.00096062 | 0.00024075 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3619-23_0_2_load_25 | 43 | 0.00048399 | 0.0001213 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3619-23_0_2_load_26 | 44 | 0.00040648 | 0.00010187 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3619-23_0_2_load_28 | 45 | 0.00029322 | 7.3488e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3619-23_0_2_load_32 | 46 | 0.00037802 | 9.4741e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3619-23_0_2_load_34 | 47 | 0.00054422 | 0.00013639 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3619-23_0_2_load_52 | 48 | 0.00025853 | 6.4794e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3619-23_0_2_load_53 | 49 | 0.00024767 | 6.2073e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3619-23_0_2_load_54 | 50 | 0.00036657 | 9.1872e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3619-23_0_2_load_55 | 51 | 0.00049601 | 0.00012431 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3619-23_0_2_load_57 | 52 | 0.00024878 | 6.235e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3619-23_0_2_load_58 | 53 | 0.00036817 | 9.2272e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3619-23_0_2_load_59 | 54 | 0.00039206 | 9.826e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3619-23_0_2_load_60 | 55 | 0.00039658 | 9.9392e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3619-23_0_2_load_33 | 56 | 0.00028483 | 7.1384e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3619-23_0_2_load_35 | 57 | 0.00031336 | 7.8535e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3619-23_0_2_load_36 | 58 | 0.00042456 | 0.0001064 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3619-23_0_2_load_37 | 59 | 0.00076848 | 0.0001926 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3619-23_0_2_load_38 | 60 | 0.00029598 | 7.4179e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3619-23_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.057127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3619-23_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.083107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3619-23_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.024322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3619-23_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.038723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3619-23_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.047673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3619-23_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.016434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3619-23_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.016724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3619-23_0_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0037746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3619-23_0_2_line_8 | NAYY 4x150 SE | 8 | 9 | 0.090098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3619-23_0_2_line_9 | NAYY 4x150 SE | 9 | 45 | 0.083391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3619-23_0_2_line_10 | NAYY 4x150 SE | 9 | 40 | 0.14349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3619-23_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.079973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3619-23_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.019548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3619-23_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.19035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3619-23_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.045086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3619-23_0_2_line_15 | NAYY 4x150 SE | 13 | 21 | 0.15304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3619-23_0_2_line_16 | NAYY 4x150 SE | 14 | 29 | 0.12429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3619-23_0_2_line_17 | NAYY 4x150 SE | 14 | 30 | 0.04844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3619-23_0_2_line_18 | NAYY 4x150 SE | 15 | 16 | 0.11265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3619-23_0_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.10968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3619-23_0_2_line_20 | NAYY 4x150 SE | 16 | 18 | 0.00060729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3619-23_0_2_line_21 | NAYY 4x150 SE | 18 | 19 | 0.034879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3619-23_0_2_line_22 | NAYY 4x150 SE | 19 | 20 | 0.048969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3619-23_0_2_line_23 | NAYY 4x150 SE | 20 | 22 | 0.050305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3619-23_0_2_line_24 | NAYY 4x150 SE | 21 | 31 | 0.16482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3619-23_0_2_line_25 | NAYY 4x150 SE | 22 | 23 | 0.23584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3619-23_0_2_line_26 | NAYY 4x150 SE | 22 | 24 | 0.16936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3619-23_0_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.16881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3619-23_0_2_line_28 | NAYY 4x150 SE | 25 | 26 | 0.072422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3619-23_0_2_line_29 | NAYY 4x150 SE | 26 | 27 | 0.022394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3619-23_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.16225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3619-23_0_2_line_31 | NAYY 4x150 SE | 28 | 48 | 0.029426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3619-23_0_2_line_32 | NAYY 4x150 SE | 29 | 32 | 0.0012512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3619-23_0_2_line_33 | NAYY 4x150 SE | 30 | 33 | 0.24388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3619-23_0_2_line_34 | NAYY 4x150 SE | 31 | 52 | 0.10855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3619-23_0_2_line_35 | NAYY 4x150 SE | 31 | 51 | 0.026595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3619-23_0_2_line_36 | NAYY 4x150 SE | 32 | 34 | 0.061046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3619-23_0_2_line_37 | NAYY 4x150 SE | 33 | 35 | 0.063808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3619-23_0_2_line_38 | NAYY 4x150 SE | 34 | 37 | 0.14985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3619-23_0_2_line_39 | NAYY 4x150 SE | 35 | 36 | 0.015089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3619-23_0_2_line_40 | NAYY 4x150 SE | 37 | 45 | 0.10564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3619-23_0_2_line_41 | NAYY 4x150 SE | 38 | 39 | 0.15683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3619-23_0_2_line_42 | NAYY 4x150 SE | 38 | 40 | 0.2505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3619-23_0_2_line_43 | NAYY 4x150 SE | 39 | 41 | 0.062371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3619-23_0_2_line_44 | NAYY 4x150 SE | 40 | 42 | 0.037936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3619-23_0_2_line_45 | NAYY 4x150 SE | 41 | 43 | 0.24175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3619-23_0_2_line_46 | NAYY 4x150 SE | 41 | 44 | 0.23836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3619-23_0_2_line_47 | NAYY 4x150 SE | 43 | 46 | 0.23571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3619-23_0_2_line_48 | NAYY 4x150 SE | 46 | 47 | 0.15983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3619-23_0_2_line_49 | NAYY 4x150 SE | 47 | 56 | 0.002891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3619-23_0_2_line_50 | NAYY 4x150 SE | 48 | 49 | 0.11737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3619-23_0_2_line_51 | NAYY 4x150 SE | 49 | 50 | 0.0085131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3619-23_0_2_line_52 | NAYY 4x150 SE | 50 | 51 | 0.010489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3619-23_0_2_line_53 | NAYY 4x150 SE | 52 | 53 | 0.0155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3619-23_0_2_line_54 | NAYY 4x150 SE | 53 | 54 | 0.080608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3619-23_0_2_line_55 | NAYY 4x150 SE | 54 | 55 | 0.14716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3619-23_0_2_line_56 | NAYY 4x150 SE | 56 | 57 | 0.14685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3619-23_0_2_line_57 | NAYY 4x150 SE | 57 | 58 | 0.21618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3619-23_0_2_line_58 | NAYY 4x150 SE | 58 | 59 | 0.051135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3619-23_0_2_line_59 | NAYY 4x150 SE | 59 | 60 | 0.026507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3619-23_0_2_trafo_13 | 0.25 MVA 20/0.4 kV | 61 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2737377.0492 | 1179212.6648 | 2737378.9759 | 1179227.6962 | 2737379.099 | 1179244.6676 | 2737380.069 | 1179256.0319 | 2737379.8199 | 1179262.5645 | 2737378.7149 | 1179269.5357
1 | 2737378.7149 | 1179269.5357 | 2737378.4974 | 1179270.9073 | 2737367.2443 | 1179305.6985 | 2737360.7156 | 1179322.106 | 2737356.3088 | 1179331.3011 | 2737347.7183 | 1179346.3138
2 | 2737335.7983 | 1179367.5148 | 2737347.6543 | 1179346.4256 | 2737347.7183 | 1179346.3138
3 | 2737335.7983 | 1179367.5148 | 2737356.4441 | 1179356.746 | 2737365.2337 | 1179353.0667 | 2737367.3904 | 1179353.0049 | 2737368.3858 | 1179354.262 | 2737368.4435 | 1179356.4094
4 | 2737335.7983 | 1179367.5148 | 2737332.0974 | 1179376.9261 | 2737328.3882 | 1179391.0409 | 2737326.8494 | 1179404.4938 | 2737325.8182 | 1179413.8626
5 | 2737368.4435 | 1179356.4094 | 2737365.7879 | 1179360.2293 | 2737360.9132 | 1179367.1674 | 2737359.7206 | 1179370.2472
6 | 2737325.8182 | 1179413.8626 | 2737323.9886 | 1179430.4861
7 | 2737323.6028 | 1179434.2408 | 2737323.7413 | 1179432.7333 | 2737323.9886 | 1179430.4861
8 | 2737300.4244 | 1179520.0665 | 2737303.2879 | 1179515.84 | 2737309.1873 | 1179504.533 | 2737315.0618 | 1179489.645 | 2737318.6149 | 1179477.6727 | 2737320.7368 | 1179465.4563 | 2737323.6028 | 1179434.2408
9 | 2737300.4244 | 1179520.0665 | 2737296.86 | 1179517.861 | 2737291.0749 | 1179516.5053 | 2737285.0558 | 1179517.6907 | 2737276.2963 | 1179521.7377 | 2737230.1863 | 1179548.1694 | 2737226.8345 | 1179550.9036
10 | 2737335.7847 | 1179658.9052 | 2737328.4083 | 1179640.9558 | 2737300.4244 | 1179520.0665
11 | 2737149.6568 | 1179943.1693 | 2737139.1185 | 1179941.1104 | 2737123.9088 | 1179937.5154 | 2737110.6237 | 1179929.6278 | 2737077.8538 | 1179910.0823
12 | 2737168.8422 | 1179946.9175 | 2737149.6568 | 1179943.1693
13 | 2737045.0604 | 1179743.3714 | 2737045.2972 | 1179753.9106 | 2737043.8165 | 1179763.8511 | 2737023.1083 | 1179798.1598 | 2737020.0154 | 1179814.1014 | 2737039.9484 | 1179852.453 | 2737064.017 | 1179898.7609 | 2737071.1327 | 1179906.0736 | 2737077.8538 | 1179910.0823
14 | 2737206.4336 | 1179935.3124 | 2737206.3453 | 1179936.8338 | 2737201.3485 | 1179944.7923 | 2737196.8547 | 1179948.4701 | 2737183.6033 | 1179949.8013 | 2737168.8422 | 1179946.9175
15 | 2737045.0604 | 1179743.3714 | 2736977.5805 | 1179606.0166
16 | 2737206.4336 | 1179935.3124 | 2737207.0384 | 1179924.5847 | 2737204.8141 | 1179896.2342 | 2737205.6509 | 1179883.7215 | 2737216.4113 | 1179846.339 | 2737216.9947 | 1179832.8753 | 2737212.416 | 1179813.2122
17 | 2737206.4336 | 1179935.3124 | 2737216.7131 | 1179939.9512 | 2737239.3354 | 1179954.569 | 2737247.147 | 1179961.1716
18 | 2737048.9754 | 1180164.0345 | 2737042.3044 | 1180155.4285 | 2737038.3243 | 1180150.0223 | 2737035.2633 | 1180149.5409 | 2737031.146 | 1180150.4697 | 2737028.4008 | 1180153.8874 | 2737026.8248 | 1180159.9783 | 2737029.4797 | 1180178.2197 | 2737028.8507 | 1180188.0128 | 2737024.2936 | 1180199.1506 | 2737011.9609 | 1180218.4836 | 2737003.6248 | 1180229.5304
19 | 2737117.2155 | 1180249.7024 | 2737100.194 | 1180232.1441 | 2737061.8116 | 1180180.5937 | 2737048.9754 | 1180164.0345
20 | 2737003.6248 | 1180229.5304 | 2737003.259 | 1180230.0151
21 | 2737003.259 | 1180230.0151 | 2736994.8364 | 1180241.1765 | 2736983.1215 | 1180251.539 | 2736978.5101 | 1180254.0613
22 | 2736935.5478 | 1180277.5599 | 2736978.5101 | 1180254.0613
23 | 2736888.5153 | 1180285.0377 | 2736897.4625 | 1180286.7655 | 2736909.508 | 1180288.6753 | 2736916.2796 | 1180288.6299 | 2736927.9151 | 1180281.7347 | 2736935.5478 | 1180277.5599
24 | 2736977.5805 | 1179606.0166 | 2736815.4108 | 1179576.5548
25 | 2736888.5153 | 1180285.0377 | 2736889.2538 | 1180296.53 | 2736886.6276 | 1180307.1227 | 2736887.307 | 1180313.1761 | 2736885.3288 | 1180317.1451 | 2736880.2417 | 1180319.0527 | 2736868.2469 | 1180322.615 | 2736854.1601 | 1180324.4282 | 2736840.5696 | 1180323.2505 | 2736833.9626 | 1180321.4427 | 2736828.824 | 1180318.5788 | 2736826.0849 | 1180314.3798 | 2736824.5238 | 1180308.7843 | 2736823.7492 | 1180303.2179 | 2736819.975 | 1180297.1605 | 2736814.787 | 1180294.1175 | 2736805.5369 | 1180293.2725 | 2736798.1127 | 1180292.447 | 2736793.3287 | 1180289.113 | 2736789.9052 | 1180281.7515 | 2736784.8796 | 1180278.9569 | 2736777.8492 | 1180281.2984 | 2736768.2637 | 1180282.425 | 2736757.6701 | 1180284.5295 | 2736743.2129 | 1180290.1819 | 2736734.5179 | 1180288.1154 | 2736725.0576 | 1180281.7503 | 2736711.4367 | 1180276.5358
26 | 2736888.5153 | 1180285.0377 | 2736887.6718 | 1180284.4958 | 2736833.7484 | 1180258.5451 | 2736826.7072 | 1180252.6577 | 2736819.3356 | 1180243.5047 | 2736796.4153 | 1180205.7973 | 2736778.9776 | 1180179.6461 | 2736772.7871 | 1180169.3399
27 | 2736772.7871 | 1180169.3399 | 2736763.1785 | 1180153.3433 | 2736758.4928 | 1180143.0174 | 2736756.4306 | 1180134.5972 | 2736757.8889 | 1180124.6117 | 2736764.528 | 1180112.2981 | 2736805.8231 | 1180063.1802 | 2736809.9281 | 1180054.0891 | 2736812.8136 | 1180035.1515 | 2736815.1745 | 1180022.6106
28 | 2736815.1745 | 1180022.6106 | 2736820.2842 | 1179995.4692 | 2736826.2121 | 1179951.0593
29 | 2736826.2121 | 1179951.0593 | 2736826.2121 | 1179951.0593 | 2736824.8263 | 1179928.7082
30 | 2736824.8263 | 1179928.7082 | 2736824.7152 | 1179926.9177 | 2736821.0391 | 1179827.5242 | 2736812.169 | 1179785.2338 | 2736809.2503 | 1179767.6928
31 | 2736809.2503 | 1179767.6928 | 2736804.4205 | 1179738.6658
32 | 2737212.416 | 1179813.2122 | 2737212.1322 | 1179811.9935
33 | 2737403.7972 | 1180140.0846 | 2737398.6612 | 1180134.1223 | 2737383.2775 | 1180116.8121 | 2737360.7695 | 1180101.5847 | 2737342.9486 | 1180078.9035 | 2737318.7475 | 1180052.5068 | 2737314.287 | 1180046.0663 | 2737300.1764 | 1180008.8591 | 2737291.741 | 1179992.1197 | 2737288.6414 | 1179988.9797 | 2737265.6499 | 1179976.8106 | 2737247.147 | 1179961.1716
34 | 2736815.4108 | 1179576.5548 | 2736822.5388 | 1179570.0498 | 2736830.1311 | 1179567.5655 | 2736835.9285 | 1179562.6941 | 2736835.9994 | 1179554.9008 | 2736831.2421 | 1179541.3374 | 2736828.5885 | 1179533.3708 | 2736826.8427 | 1179528.4939 | 2736824.1218 | 1179514.7768 | 2736826.4042 | 1179481.2463
35 | 2736811.145 | 1179602.7686 | 2736815.2877 | 1179576.6672 | 2736815.4108 | 1179576.5548
36 | 2737216.2835 | 1179753.4647 | 2737210.9247 | 1179761.2035 | 2737209.0804 | 1179768.3224 | 2737207.3786 | 1179791.5791 | 2737212.1322 | 1179811.9935
37 | 2737449.9174 | 1180183.7861 | 2737422.7195 | 1180162.0507 | 2737403.7972 | 1180140.0846
38 | 2737246.3528 | 1179638.9387 | 2737249.9784 | 1179642.3725 | 2737259.1043 | 1179655.0245 | 2737264.8077 | 1179664.2732 | 2737265.7005 | 1179670.0092 | 2737264.945 | 1179677.2975 | 2737254.8446 | 1179716.5409 | 2737254.2244 | 1179725.934 | 2737254.8223 | 1179737.8679 | 2737252.2033 | 1179742.4337 | 2737245.7995 | 1179744.7445 | 2737229.7711 | 1179746.5124 | 2737216.2835 | 1179753.4647 | 2737216.2835 | 1179753.4647
39 | 2737462.5169 | 1180192.0859 | 2737450.0953 | 1180183.9283 | 2737449.9174 | 1180183.7861
40 | 2737226.8345 | 1179550.9036 | 2737221.409 | 1179555.3296 | 2737214.0651 | 1179567.3152 | 2737210.5191 | 1179578.9875 | 2737209.5835 | 1179588.4734 | 2737233.5068 | 1179626.7725 | 2737246.3528 | 1179638.9387
41 | 2737478.4932 | 1180027.6409 | 2737478.0599 | 1180024.9247 | 2737474.1606 | 1180009.3455 | 2737467.7597 | 1180000.214 | 2737442.431 | 1179973.346 | 2737434.6942 | 1179960.1474 | 2737428.3566 | 1179937.5848 | 2737424.451 | 1179917.9469 | 2737418.7364 | 1179903.2046 | 2737409.0751 | 1179891.2406
42 | 2737335.7847 | 1179658.9052 | 2737391.0602 | 1179774.0377 | 2737395.2764 | 1179786.8108 | 2737397.2969 | 1179801.6796 | 2737392.7625 | 1179856.1176 | 2737395.0005 | 1179870.1686 | 2737400.0543 | 1179880.0698 | 2737409.0751 | 1179891.2406
43 | 2737509.6695 | 1180076.7894 | 2737500.4304 | 1180072.7856 | 2737493.6623 | 1180068.3381 | 2737487.2587 | 1180058.9951 | 2737483.086 | 1180051.338 | 2737480.6522 | 1180041.1744 | 2737478.4932 | 1180027.6409
44 | 2737333.5362 | 1179696.6605 | 2737334.3671 | 1179685.0818 | 2737333.8892 | 1179672.2498 | 2737335.7847 | 1179658.9052
45 | 2737509.6695 | 1180076.7894 | 2737516.1689 | 1180070.3001 | 2737529.5563 | 1180065.0364 | 2737545.9101 | 1180058.0505 | 2737555.5693 | 1180050.4107 | 2737560.3974 | 1180043.1603 | 2737562.8884 | 1180032.8539 | 2737563.9821 | 1180018.8349 | 2737562.0344 | 1179994.1601 | 2737559.3022 | 1179972.692 | 2737548.0137 | 1179946.435 | 2737540.0278 | 1179928.1155 | 2737537.9697 | 1179912.901 | 2737538.2906 | 1179901.255 | 2737542.8255 | 1179868.8229
46 | 2737509.6695 | 1180076.7894 | 2737564.7388 | 1180101.3825 | 2737583.5702 | 1180106.9744 | 2737603.2253 | 1180110.6393 | 2737634.7236 | 1180122.0377 | 2737651.0727 | 1180132.888 | 2737662.16 | 1180143.2505 | 2737685.1978 | 1180164.3179 | 2737706.5246 | 1180196.8464
47 | 2737525.8546 | 1179660.3055 | 2737525.7903 | 1179666.3874 | 2737528.703 | 1179686.9923 | 2737531.5674 | 1179714.0344 | 2737534.2004 | 1179724.514 | 2737538.4169 | 1179734.9298 | 2737544.7493 | 1179744.727 | 2737555.3841 | 1179752.5325 | 2737565.7929 | 1179761.2002 | 2737570.9033 | 1179770.6247 | 2737574.2673 | 1179780.5539 | 2737574.4639 | 1179789.9657 | 2737573.1475 | 1179795.7066 | 2737569.9034 | 1179803.1935 | 2737563.799 | 1179810.1032 | 2737549.4396 | 1179821.7272 | 2737545.5721 | 1179827.4096 | 2737542.8764 | 1179835.3094 | 2737541.84 | 1179844.8374 | 2737542.8091 | 1179860.5495 | 2737542.8255 | 1179868.8229
48 | 2737611.2906 | 1179558.4212 | 2737606.1534 | 1179556.8132 | 2737601.8076 | 1179556.3576 | 2737597.2949 | 1179556.5097 | 2737563.1423 | 1179564.0542 | 2737551.8655 | 1179566.553 | 2737548.5887 | 1179568.4683 | 2737546.8047 | 1179570.2732 | 2737545.7237 | 1179572.7503 | 2737542.795 | 1179586.4715 | 2737533.9346 | 1179619.8829 | 2737529.8352 | 1179633.3325 | 2737525.9209 | 1179654.0365 | 2737525.8546 | 1179660.3055
49 | 2737613.7248 | 1179559.9809 | 2737611.2906 | 1179558.4212 | 2737611.2906 | 1179558.4212
50 | 2736804.4205 | 1179738.6658 | 2736804.4205 | 1179738.6658 | 2736804.9872 | 1179695.768 | 2736805.2363 | 1179639.9976 | 2736808.1664 | 1179621.5361
51 | 2736809.5008 | 1179613.1283 | 2736808.1664 | 1179621.5361
52 | 2736809.5008 | 1179613.1283 | 2736811.145 | 1179602.7686
53 | 2736826.4042 | 1179481.2463 | 2736827.4568 | 1179465.782
54 | 2736851.8405 | 1179389.7411 | 2736850.6523 | 1179401.5397 | 2736846.8753 | 1179414.3189 | 2736836.4133 | 1179432.6832 | 2736827.4568 | 1179465.782 | 2736827.4568 | 1179465.782
55 | 2736851.8405 | 1179389.7411 | 2736853.0343 | 1179377.8871 | 2736862.7769 | 1179355.2253 | 2736891.4219 | 1179312.7576 | 2736902.8586 | 1179287.8774 | 2736912.5563 | 1179257.4139
56 | 2737613.7248 | 1179559.9809 | 2737618.3103 | 1179562.9191 | 2737626.7038 | 1179570.1617 | 2737642.8288 | 1179591.1702 | 2737661.5349 | 1179613.261 | 2737665.8398 | 1179620.154 | 2737673.6249 | 1179642.5611 | 2737680.6174 | 1179663.8714 | 2737687.2351 | 1179672.5522 | 2737694.721 | 1179678.7151
57 | 2737694.721 | 1179678.7151 | 2737699.1011 | 1179682.3211 | 2737707.9356 | 1179692.643 | 2737718.4874 | 1179710.7104 | 2737723.399 | 1179713.4809 | 2737730.1003 | 1179716.1924 | 2737743.4454 | 1179717.4666 | 2737762.209 | 1179721.7342 | 2737771.6585 | 1179727.5669 | 2737780.1632 | 1179736.6026 | 2737783.5666 | 1179746.7997 | 2737783.4517 | 1179753.7914 | 2737781.0187 | 1179788.4733 | 2737778.0632 | 1179812.3127 | 2737778.1569 | 1179819.2091 | 2737780.3869 | 1179826.9218 | 2737783.3924 | 1179832.1504 | 2737790.0542 | 1179838.8976 | 2737790.0542 | 1179838.8976
58 | 2737790.0542 | 1179838.8976 | 2737829.7094 | 1179871.1821
59 | 2737829.7094 | 1179871.1821 | 2737847.6534 | 1179885.7908 | 2737850.5626 | 1179887.4886

## bus_geodata
| x | y | coords
0 | 2737377.0492 | 1179212.6648
1 | 2737378.7149 | 1179269.5357
2 | 2737347.7183 | 1179346.3138
3 | 2737335.7983 | 1179367.5148
4 | 2737368.4435 | 1179356.4094
5 | 2737325.8182 | 1179413.8626
6 | 2737359.7206 | 1179370.2472
7 | 2737323.9886 | 1179430.4861
8 | 2737323.6028 | 1179434.2408
9 | 2737300.4244 | 1179520.0665
10 | 2737149.6568 | 1179943.1693
11 | 2737077.8538 | 1179910.0823
12 | 2737168.8422 | 1179946.9174
13 | 2737045.0604 | 1179743.3714
14 | 2737206.4336 | 1179935.3124
15 | 2737048.9754 | 1180164.0345
16 | 2737003.6248 | 1180229.5304
17 | 2737117.2155 | 1180249.7024
18 | 2737003.259 | 1180230.0151
19 | 2736978.5101 | 1180254.0613
20 | 2736935.5478 | 1180277.5599
21 | 2736977.5805 | 1179606.0166
22 | 2736888.5153 | 1180285.0377
23 | 2736711.4367 | 1180276.5358
24 | 2736772.7871 | 1180169.3399
25 | 2736815.1745 | 1180022.6106
26 | 2736826.2121 | 1179951.0593
27 | 2736824.8263 | 1179928.7082
28 | 2736809.2503 | 1179767.6928
29 | 2737212.416 | 1179813.2122
30 | 2737247.147 | 1179961.1716
31 | 2736815.4108 | 1179576.5548
32 | 2737212.1322 | 1179811.9935
33 | 2737403.7972 | 1180140.0846
34 | 2737216.2835 | 1179753.4647
35 | 2737449.9174 | 1180183.7861
36 | 2737462.5169 | 1180192.0859
37 | 2737246.3528 | 1179638.9387
38 | 2737409.0751 | 1179891.2406
39 | 2737478.4932 | 1180027.6409
40 | 2737335.7847 | 1179658.9052
41 | 2737509.6695 | 1180076.7894
42 | 2737333.5362 | 1179696.6605
43 | 2737542.8255 | 1179868.8229
44 | 2737706.5246 | 1180196.8464
45 | 2737226.8345 | 1179550.9036
46 | 2737525.8546 | 1179660.3055
47 | 2737611.2906 | 1179558.4212
48 | 2736804.4205 | 1179738.6658
49 | 2736808.1664 | 1179621.5361
50 | 2736809.5008 | 1179613.1283
51 | 2736811.145 | 1179602.7686
52 | 2736826.4042 | 1179481.2463
53 | 2736827.4568 | 1179465.782
54 | 2736851.8405 | 1179389.7411
55 | 2736912.5563 | 1179257.4139
56 | 2737613.7248 | 1179559.9809
57 | 2737694.721 | 1179678.7151
58 | 2737790.0542 | 1179838.8976
59 | 2737829.7094 | 1179871.1821
60 | 2737850.5626 | 1179887.4886
61 | 2737212.416 | 1179813.2122

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1