## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3638-8_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3638-8_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3638-8_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3638-8_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_3638-8_0_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_3638-8_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3638-8_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3638-8_0_2_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_3638-8_0_2_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_3638-8_0_2_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_3638-8_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_3638-8_0_2_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_3638-8_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_3638-8_0_2_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_3638-8_0_2_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_3638-8_0_2_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_3638-8_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_3638-8_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_3638-8_0_2_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_3638-8_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_3638-8_0_2_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_3638-8_0_2_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_3638-8_0_2_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_3638-8_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_3638-8_0_2_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_3638-8_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_3638-8_0_2_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_3638-8_0_2_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_3638-8_0_2_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_3638-8_0_2_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_3638-8_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_3638-8_0_2_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_3638-8_0_2_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_3638-8_0_2_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_3638-8_0_2_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_3638-8_0_2_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_3638-8_0_2_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_3638-8_0_2_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_3638-8_0_2_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_3638-8_0_2_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_3638-8_0_2_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_3638-8_0_2_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_3638-8_0_2_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_3638-8_0_2_node_48 | 0.4 | n |  | TRUE
44 | bus_LV_3638-8_0_2_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_3638-8_0_2_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_3638-8_0_2_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_3638-8_0_2_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_3638-8_0_2_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_3638-8_0_2_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_3638-8_0_2_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_3638-8_0_2_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_3638-8_0_2_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_3638-8_0_2_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_3638-8_0_2_node_55 | 0.4 | n |  | TRUE
55 | bus_MV_163_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3638-8_0_2_load_0 | 0 | 0.0016903 | 0.00042362 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3638-8_0_2_load_1 | 1 | 0.015366 | 0.0038511 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3638-8_0_2_load_2 | 2 | 0.00066684 | 0.00016713 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3638-8_0_2_load_3 | 4 | 0.0013662 | 0.0003424 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3638-8_0_2_load_6 | 6 | 0.0056234 | 0.0014094 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3638-8_0_2_load_24 | 7 | 0.0035396 | 0.0008871 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3638-8_0_2_load_10 | 8 | 0.0033345 | 0.00083571 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3638-8_0_2_load_11 | 9 | 0.0040549 | 0.0010162 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3638-8_0_2_load_8 | 10 | 0.0031545 | 0.00079059 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3638-8_0_2_load_20 | 11 | 0.003689 | 0.00092456 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3638-8_0_2_load_7 | 12 | 0.0027522 | 0.00068977 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3638-8_0_2_load_12 | 13 | 0.0081405 | 0.0020402 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3638-8_0_2_load_13 | 14 | 0.0063926 | 0.0016021 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3638-8_0_2_load_15 | 16 | 0.0043981 | 0.0011023 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3638-8_0_2_load_16 | 17 | 0.0028417 | 0.0007122 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3638-8_0_2_load_17 | 18 | 0.0048707 | 0.0012207 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3638-8_0_2_load_18 | 19 | 0.0032937 | 0.00082548 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3638-8_0_2_load_19 | 20 | 0.0023126 | 0.0005796 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3638-8_0_2_load_31 | 21 | 0.0017198 | 0.00043103 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3638-8_0_2_load_21 | 23 | 0.0026229 | 0.00065736 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3638-8_0_2_load_22 | 24 | 0.0045327 | 0.001136 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3638-8_0_2_load_23 | 25 | 0.0031426 | 0.00078762 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3638-8_0_2_load_30 | 26 | 0.0034771 | 0.00087145 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3638-8_0_2_load_28 | 27 | 0.0034291 | 0.00085941 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3638-8_0_2_load_26 | 29 | 0.0011938 | 0.00029919 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3638-8_0_2_load_27 | 30 | 0.0028727 | 0.00071997 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3638-8_0_2_load_29 | 31 | 0.0019915 | 0.00049912 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3638-8_0_2_load_35 | 33 | 0.0015144 | 0.00037955 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3638-8_0_2_load_33 | 35 | 0.0027112 | 0.00067949 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3638-8_0_2_load_37 | 36 | 0.0022125 | 0.0005545 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3638-8_0_2_load_38 | 37 | 0.0012133 | 0.00030407 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3638-8_0_2_load_39 | 38 | 0.010283 | 0.0025771 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3638-8_0_2_load_42 | 39 | 0.0023633 | 0.0005923 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3638-8_0_2_load_40 | 40 | 0.0040042 | 0.0010035 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3638-8_0_2_load_50 | 41 | 0.0011565 | 0.00028984 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3638-8_0_2_load_41 | 42 | 0.01037 | 0.002599 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3638-8_0_2_load_43 | 44 | 0.0029172 | 0.00073111 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3638-8_0_2_load_44 | 45 | 0.0036844 | 0.00092339 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3638-8_0_2_load_47 | 47 | 0.00096928 | 0.00024292 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3638-8_0_2_load_46 | 48 | 0.0026923 | 0.00067476 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3638-8_0_2_load_49 | 49 | 0.0017528 | 0.00043929 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3638-8_0_2_load_54 | 51 | 0.0014935 | 0.00037431 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3638-8_0_2_load_53 | 53 | 0.0030527 | 0.00076507 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3638-8_0_2_load_55 | 54 | 0.0011311 | 0.00028349 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3638-8_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0064204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3638-8_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.004436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3638-8_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.19726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3638-8_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3638-8_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3638-8_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0076018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3638-8_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.05092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3638-8_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.07111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3638-8_0_2_line_8 | NAYY 4x150 SE | 7 | 11 | 0.063315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3638-8_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.0073125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3638-8_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.033192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3638-8_0_2_line_11 | NAYY 4x150 SE | 9 | 13 | 0.010309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3638-8_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.015626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3638-8_0_2_line_13 | NAYY 4x150 SE | 11 | 23 | 0.023419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3638-8_0_2_line_14 | NAYY 4x150 SE | 14 | 15 | 0.012235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3638-8_0_2_line_15 | NAYY 4x150 SE | 15 | 16 | 0.016254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3638-8_0_2_line_16 | NAYY 4x150 SE | 16 | 17 | 0.028593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3638-8_0_2_line_17 | NAYY 4x150 SE | 17 | 18 | 0.027265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3638-8_0_2_line_18 | NAYY 4x150 SE | 18 | 19 | 0.024268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3638-8_0_2_line_19 | NAYY 4x150 SE | 19 | 20 | 0.017919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3638-8_0_2_line_20 | NAYY 4x150 SE | 20 | 21 | 0.028306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3638-8_0_2_line_21 | NAYY 4x150 SE | 21 | 22 | 0.0073445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3638-8_0_2_line_22 | NAYY 4x150 SE | 22 | 35 | 0.017365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3638-8_0_2_line_23 | NAYY 4x150 SE | 23 | 24 | 0.0039371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3638-8_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.022499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3638-8_0_2_line_25 | NAYY 4x150 SE | 25 | 26 | 0.00029967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3638-8_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.02167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3638-8_0_2_line_27 | NAYY 4x150 SE | 27 | 29 | 0.003723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3638-8_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.022145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3638-8_0_2_line_29 | NAYY 4x150 SE | 28 | 30 | 0.017119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3638-8_0_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.024621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3638-8_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.03636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3638-8_0_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.015049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3638-8_0_2_line_33 | NAYY 4x150 SE | 32 | 34 | 0.00647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3638-8_0_2_line_34 | NAYY 4x150 SE | 33 | 36 | 0.0083754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3638-8_0_2_line_35 | NAYY 4x150 SE | 34 | 37 | 0.01625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3638-8_0_2_line_36 | NAYY 4x150 SE | 34 | 38 | 0.028723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3638-8_0_2_line_37 | NAYY 4x150 SE | 35 | 36 | 0.021941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3638-8_0_2_line_38 | NAYY 4x150 SE | 37 | 39 | 0.0061923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3638-8_0_2_line_39 | NAYY 4x150 SE | 38 | 40 | 0.01792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3638-8_0_2_line_40 | NAYY 4x150 SE | 39 | 41 | 0.015948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3638-8_0_2_line_41 | NAYY 4x150 SE | 40 | 42 | 0.056405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3638-8_0_2_line_42 | NAYY 4x150 SE | 41 | 43 | 0.010959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3638-8_0_2_line_43 | NAYY 4x150 SE | 43 | 50 | 0.00832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3638-8_0_2_line_44 | NAYY 4x150 SE | 43 | 48 | 0.018942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3638-8_0_2_line_45 | NAYY 4x150 SE | 44 | 45 | 0.028381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3638-8_0_2_line_46 | NAYY 4x150 SE | 45 | 46 | 0.010975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3638-8_0_2_line_47 | NAYY 4x150 SE | 46 | 47 | 0.022215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3638-8_0_2_line_48 | NAYY 4x150 SE | 47 | 49 | 0.0031074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3638-8_0_2_line_49 | NAYY 4x150 SE | 49 | 51 | 0.018267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3638-8_0_2_line_50 | NAYY 4x150 SE | 50 | 52 | 0.036309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3638-8_0_2_line_51 | NAYY 4x150 SE | 50 | 53 | 0.028252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3638-8_0_2_line_52 | NAYY 4x150 SE | 51 | 54 | 0.010129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3638-8_0_2_line_53 | NAYY 4x150 SE | 52 | 54 | 0.025732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3638-8_0_2_trafo_22 | 0.25 MVA 20/0.4 kV | 55 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2754155.489 | 1175834.3746 | 2754155.0494 | 1175827.9693
1 | 2754155.489 | 1175834.3746 | 2754155.7927 | 1175838.8002 | 2754155.7927 | 1175838.8002
2 | 2754160.2385 | 1175630.7746 | 2754155.0494 | 1175827.9693
3 | 2754158.1497 | 1175850.8106 | 2754155.7927 | 1175838.8002
4 | 2754160.2385 | 1175630.7746 | 2754149.0774 | 1175616.8541
5 | 2754158.1497 | 1175850.8106 | 2754159.6135 | 1175858.2701
6 | 2754149.0774 | 1175616.8541 | 2754111.5068 | 1175582.4846
7 | 2754195.3981 | 1175562.9007 | 2754149.0774 | 1175616.8541
8 | 2754124.7667 | 1175520.5741 | 2754111.5068 | 1175582.4846
9 | 2754195.3981 | 1175562.9007 | 2754189.7319 | 1175558.2781
10 | 2754224.3634 | 1175576.2751 | 2754216.6064 | 1175576.1774 | 2754208.6688 | 1175573.727 | 2754195.3981 | 1175562.9007
11 | 2754181.7438 | 1175551.7614 | 2754189.7319 | 1175558.2781
12 | 2754239.9881 | 1175576.4717 | 2754224.3634 | 1175576.2751
13 | 2754124.7667 | 1175520.5741 | 2754105.6478 | 1175507.0487
14 | 2754191.9246 | 1175506.2406 | 2754201.5885 | 1175513.7442
15 | 2754191.9246 | 1175506.2406 | 2754178.8934 | 1175496.5258
16 | 2754178.8934 | 1175496.5258 | 2754155.9695 | 1175479.4359
17 | 2754134.0593 | 1175463.2116 | 2754135.9669 | 1175464.524 | 2754155.9695 | 1175479.4359
18 | 2754134.0593 | 1175463.2116 | 2754114.0653 | 1175449.4568
19 | 2754114.0653 | 1175449.4568 | 2754104.1966 | 1175442.6677 | 2754100.2091 | 1175438.2637
20 | 2754100.2091 | 1175438.2637 | 2754088.1977 | 1175424.9978 | 2754081.5461 | 1175416.9894
21 | 2754076.8534 | 1175411.3396 | 2754081.5461 | 1175416.9894
22 | 2754076.8534 | 1175411.3396 | 2754060.185 | 1175406.47
23 | 2754102.4337 | 1175504.7749 | 2754105.6478 | 1175507.0487
24 | 2754102.4337 | 1175504.7749 | 2754086.6263 | 1175493.5922 | 2754084.0608 | 1175491.7886
25 | 2754084.0608 | 1175491.7886 | 2754083.8157 | 1175491.6162
26 | 2754083.8157 | 1175491.6162 | 2754066.0881 | 1175479.153
27 | 2754063.0425 | 1175477.0117 | 2754066.0881 | 1175479.153
28 | 2754043.312 | 1175472.6962 | 2754053.4631 | 1175470.277 | 2754063.0425 | 1175477.0117
29 | 2754043.312 | 1175472.6962 | 2754037.3395 | 1175456.6525
30 | 2754037.3395 | 1175456.6525 | 2754028.75 | 1175433.5786
31 | 2754016.0649 | 1175399.5027 | 2754028.75 | 1175433.5786
32 | 2754016.0649 | 1175399.5027 | 2754031.1042 | 1175400.0514
33 | 2754013.8035 | 1175393.4397 | 2754016.0649 | 1175399.5027
34 | 2754039.474 | 1175400.3568 | 2754031.1042 | 1175400.0514
35 | 2754013.8035 | 1175393.4397 | 2754008.2923 | 1175378.1532
36 | 2754013.8035 | 1175393.4397 | 2753987.8328 | 1175405.7097
37 | 2754039.474 | 1175400.3568 | 2754045.9369 | 1175400.5926 | 2754054.1077 | 1175404.6946 | 2754060.185 | 1175406.47
38 | 2754006.1921 | 1175372.3279 | 2754008.2923 | 1175378.1532
39 | 2753987.8328 | 1175405.7097 | 2753971.6298 | 1175413.365
40 | 2754006.1921 | 1175372.3279 | 2754000.7833 | 1175357.3255
41 | 2753942.2502 | 1175458.897 | 2753946.9635 | 1175448.9709 | 2753955.5518 | 1175425.4939 | 2753964.3339 | 1175416.812 | 2753971.6298 | 1175413.365
42 | 2753997.0665 | 1175347.016 | 2754000.7833 | 1175357.3255
43 | 2753996.2004 | 1175338.7425 | 2753997.0665 | 1175347.016
44 | 2753997.0665 | 1175347.016 | 2753982.7947 | 1175359.4713
45 | 2753916.5689 | 1175380.0355 | 2753929.8152 | 1175365.217 | 2753936.3243 | 1175359.7424
46 | 2753944.7239 | 1175352.6778 | 2753936.3243 | 1175359.7424
47 | 2753944.7239 | 1175352.6778 | 2753960.6833 | 1175337.2246
48 | 2753960.6833 | 1175337.2246 | 2753962.9157 | 1175335.063
49 | 2753962.9157 | 1175335.063 | 2753976.0388 | 1175322.356
50 | 2754005.3862 | 1175303.6268 | 2753999.6356 | 1175324.1185 | 2753996.2004 | 1175338.7425
51 | 2753996.2004 | 1175338.7425 | 2754013.2218 | 1175332.1071 | 2754022.1137 | 1175327.5694
52 | 2753976.0388 | 1175322.356 | 2753977.5828 | 1175320.861 | 2753983.3751 | 1175315.3727
53 | 2754005.3862 | 1175303.6268 | 2753991.9689 | 1175307.2299 | 2753983.3751 | 1175315.3727

## bus_geodata
| x | y | coords
0 | 2754155.489 | 1175834.3746
1 | 2754155.0494 | 1175827.9693
2 | 2754155.7927 | 1175838.8002
3 | 2754160.2385 | 1175630.7746
4 | 2754158.1497 | 1175850.8106
5 | 2754149.0774 | 1175616.8541
6 | 2754159.6135 | 1175858.2701
7 | 2754111.5068 | 1175582.4846
8 | 2754195.3981 | 1175562.9007
9 | 2754189.7319 | 1175558.2781
10 | 2754224.3634 | 1175576.2751
11 | 2754124.7667 | 1175520.5741
12 | 2754239.9881 | 1175576.4717
13 | 2754181.7438 | 1175551.7614
14 | 2754201.5885 | 1175513.7442
15 | 2754191.9246 | 1175506.2406
16 | 2754178.8934 | 1175496.5258
17 | 2754155.9695 | 1175479.4359
18 | 2754134.0593 | 1175463.2116
19 | 2754114.0653 | 1175449.4568
20 | 2754100.2091 | 1175438.2637
21 | 2754081.5461 | 1175416.9894
22 | 2754076.8534 | 1175411.3396
23 | 2754105.6478 | 1175507.0487
24 | 2754102.4337 | 1175504.7749
25 | 2754084.0608 | 1175491.7886
26 | 2754083.8157 | 1175491.6162
27 | 2754066.0881 | 1175479.153
28 | 2754043.312 | 1175472.6962
29 | 2754063.0425 | 1175477.0117
30 | 2754037.3395 | 1175456.6525
31 | 2754028.75 | 1175433.5786
32 | 2754016.0649 | 1175399.5027
33 | 2754031.1042 | 1175400.0514
34 | 2754013.8035 | 1175393.4397
35 | 2754060.185 | 1175406.47
36 | 2754039.474 | 1175400.3568
37 | 2754008.2923 | 1175378.1532
38 | 2753987.8328 | 1175405.7097
39 | 2754006.1921 | 1175372.3279
40 | 2753971.6298 | 1175413.365
41 | 2754000.7833 | 1175357.3255
42 | 2753942.2502 | 1175458.897
43 | 2753997.0665 | 1175347.016
44 | 2753916.5689 | 1175380.0355
45 | 2753936.3243 | 1175359.7424
46 | 2753944.7239 | 1175352.6778
47 | 2753960.6833 | 1175337.2246
48 | 2753982.7947 | 1175359.4713
49 | 2753962.9157 | 1175335.063
50 | 2753996.2004 | 1175338.7425
51 | 2753976.0388 | 1175322.356
52 | 2754005.3862 | 1175303.6268
53 | 2754022.1137 | 1175327.5694
54 | 2753983.3751 | 1175315.3727
55 | 2754131.2718 | 1175525.1761

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1