## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3661-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3661-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3661-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3661-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3661-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3661-13_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_3661-13_0_4_node_155 | 0.4 | n |  | TRUE
7 | bus_LV_3661-13_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_3661-13_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_3661-13_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_3661-13_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_3661-13_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_3661-13_0_4_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_3661-13_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_3661-13_0_4_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_3661-13_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_3661-13_0_4_node_137 | 0.4 | n |  | TRUE
17 | bus_LV_3661-13_0_4_node_136 | 0.4 | n |  | TRUE
18 | bus_LV_3661-13_0_4_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_3661-13_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_3661-13_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_3661-13_0_4_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_3661-13_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_3661-13_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_3661-13_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_3661-13_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_3661-13_0_4_node_37 | 0.4 | n |  | TRUE
27 | bus_LV_3661-13_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_3661-13_0_4_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_3661-13_0_4_node_154 | 0.4 | n |  | TRUE
30 | bus_LV_3661-13_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_3661-13_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_3661-13_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_3661-13_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_3661-13_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_3661-13_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_3661-13_0_4_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_3661-13_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_3661-13_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_3661-13_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_3661-13_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_3661-13_0_4_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_3661-13_0_4_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_3661-13_0_4_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_3661-13_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_3661-13_0_4_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_3661-13_0_4_node_89 | 0.4 | n |  | TRUE
47 | bus_LV_3661-13_0_4_node_90 | 0.4 | n |  | TRUE
48 | bus_LV_3661-13_0_4_node_47 | 0.4 | n |  | TRUE
49 | bus_LV_3661-13_0_4_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_3661-13_0_4_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_3661-13_0_4_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_3661-13_0_4_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_3661-13_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_3661-13_0_4_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_3661-13_0_4_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_3661-13_0_4_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_3661-13_0_4_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_3661-13_0_4_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_3661-13_0_4_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_3661-13_0_4_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_3661-13_0_4_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_3661-13_0_4_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_3661-13_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_3661-13_0_4_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_3661-13_0_4_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_3661-13_0_4_node_65 | 0.4 | n |  | TRUE
67 | bus_LV_3661-13_0_4_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_3661-13_0_4_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_3661-13_0_4_node_68 | 0.4 | n |  | TRUE
70 | bus_LV_3661-13_0_4_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_3661-13_0_4_node_111 | 0.4 | n |  | TRUE
72 | bus_LV_3661-13_0_4_node_112 | 0.4 | n |  | TRUE
73 | bus_LV_3661-13_0_4_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_3661-13_0_4_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_3661-13_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_3661-13_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_3661-13_0_4_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_3661-13_0_4_node_75 | 0.4 | n |  | TRUE
79 | bus_LV_3661-13_0_4_node_102 | 0.4 | n |  | TRUE
80 | bus_LV_3661-13_0_4_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_3661-13_0_4_node_103 | 0.4 | n |  | TRUE
82 | bus_LV_3661-13_0_4_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_3661-13_0_4_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_3661-13_0_4_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_3661-13_0_4_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_3661-13_0_4_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_3661-13_0_4_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_3661-13_0_4_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_3661-13_0_4_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_3661-13_0_4_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_3661-13_0_4_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_3661-13_0_4_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_3661-13_0_4_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_3661-13_0_4_node_91 | 0.4 | n |  | TRUE
95 | bus_LV_3661-13_0_4_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_3661-13_0_4_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_3661-13_0_4_node_94 | 0.4 | n |  | TRUE
98 | bus_LV_3661-13_0_4_node_95 | 0.4 | n |  | TRUE
99 | bus_LV_3661-13_0_4_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_3661-13_0_4_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_3661-13_0_4_node_98 | 0.4 | n |  | TRUE
102 | bus_LV_3661-13_0_4_node_129 | 0.4 | n |  | TRUE
103 | bus_LV_3661-13_0_4_node_130 | 0.4 | n |  | TRUE
104 | bus_LV_3661-13_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_3661-13_0_4_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_3661-13_0_4_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_3661-13_0_4_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_3661-13_0_4_node_125 | 0.4 | n |  | TRUE
109 | bus_LV_3661-13_0_4_node_108 | 0.4 | n |  | TRUE
110 | bus_LV_3661-13_0_4_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_3661-13_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_3661-13_0_4_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_3661-13_0_4_node_107 | 0.4 | n |  | TRUE
114 | bus_LV_3661-13_0_4_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_3661-13_0_4_node_120 | 0.4 | n |  | TRUE
116 | bus_LV_3661-13_0_4_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_3661-13_0_4_node_123 | 0.4 | n |  | TRUE
118 | bus_LV_3661-13_0_4_node_140 | 0.4 | n |  | TRUE
119 | bus_LV_3661-13_0_4_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_3661-13_0_4_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_3661-13_0_4_node_118 | 0.4 | n |  | TRUE
122 | bus_LV_3661-13_0_4_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_3661-13_0_4_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_3661-13_0_4_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_3661-13_0_4_node_135 | 0.4 | n |  | TRUE
126 | bus_LV_3661-13_0_4_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_3661-13_0_4_node_122 | 0.4 | n |  | TRUE
128 | bus_LV_3661-13_0_4_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_3661-13_0_4_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_3661-13_0_4_node_127 | 0.4 | n |  | TRUE
131 | bus_LV_3661-13_0_4_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_3661-13_0_4_node_134 | 0.4 | n |  | TRUE
133 | bus_LV_3661-13_0_4_node_139 | 0.4 | n |  | TRUE
134 | bus_LV_3661-13_0_4_node_132 | 0.4 | n |  | TRUE
135 | bus_LV_3661-13_0_4_node_131 | 0.4 | n |  | TRUE
136 | bus_LV_3661-13_0_4_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_3661-13_0_4_node_138 | 0.4 | n |  | TRUE
138 | bus_MV_163_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3661-13_0_4_load_0 | 0 | 0.0010315 | 0.00025851 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3661-13_0_4_load_2 | 2 | 0.0011055 | 0.00027706 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3661-13_0_4_load_18 | 5 | 0.0012701 | 0.00031833 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3661-13_0_4_load_155 | 6 | 0.00083754 | 0.00020991 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3661-13_0_4_load_6 | 7 | 0.0063222 | 0.0015845 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3661-13_0_4_load_19 | 8 | 0.00046156 | 0.00011568 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3661-13_0_4_load_5 | 9 | 0.0029777 | 0.00074627 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3661-13_0_4_load_9 | 10 | 0.0021762 | 0.00054541 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3661-13_0_4_load_16 | 12 | 0.0010241 | 0.00025666 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3661-13_0_4_load_35 | 14 | 0.001539 | 0.00038572 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3661-13_0_4_load_15 | 15 | 0.00045588 | 0.00011425 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3661-13_0_4_load_137 | 16 | 0.0013777 | 0.00034529 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3661-13_0_4_load_136 | 17 | 0.0017782 | 0.00044566 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3661-13_0_4_load_34 | 18 | 0.00084295 | 0.00021126 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3661-13_0_4_load_17 | 19 | 0.0013821 | 0.0003464 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3661-13_0_4_load_43 | 21 | 0.0015121 | 0.00037896 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3661-13_0_4_load_21 | 23 | 0.0027021 | 0.00067721 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3661-13_0_4_load_22 | 24 | 0.00069935 | 0.00017527 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3661-13_0_4_load_23 | 25 | 0.0037912 | 0.00095016 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3661-13_0_4_load_37 | 26 | 0.0010988 | 0.00027538 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3661-13_0_4_load_24 | 27 | 0.0040675 | 0.0010194 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3661-13_0_4_load_154 | 29 | 0.0018141 | 0.00045467 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3661-13_0_4_load_25 | 30 | 0.0021138 | 0.00052977 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3661-13_0_4_load_26 | 31 | 0.0032826 | 0.00082269 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3661-13_0_4_load_33 | 32 | 0.0023355 | 0.00058532 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3661-13_0_4_load_31 | 33 | 0.0011788 | 0.00029543 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3661-13_0_4_load_27 | 34 | 0.0022159 | 0.00055535 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3661-13_0_4_load_28 | 35 | 0.0019658 | 0.00049267 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3661-13_0_4_load_30 | 37 | 0.0024216 | 0.0006069 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3661-13_0_4_load_32 | 38 | 0.0012649 | 0.000317 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3661-13_0_4_load_36 | 39 | 0.0012753 | 0.00031961 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3661-13_0_4_load_39 | 40 | 0.0012767 | 0.00031997 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3661-13_0_4_load_40 | 41 | 0.00084027 | 0.00021059 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3661-13_0_4_load_41 | 42 | 0.00054978 | 0.00013779 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3661-13_0_4_load_42 | 43 | 0.0011784 | 0.00029533 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3661-13_0_4_load_44 | 44 | 0.0010701 | 0.0002682 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3661-13_0_4_load_46 | 45 | 0.0019598 | 0.00049117 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3661-13_0_4_load_89 | 46 | 0.00092528 | 0.0002319 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3661-13_0_4_load_90 | 47 | 0.001688 | 0.00042306 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3661-13_0_4_load_47 | 48 | 0.00076813 | 0.00019251 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3661-13_0_4_load_48 | 49 | 0.00053789 | 0.00013481 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3661-13_0_4_load_49 | 50 | 0.00058969 | 0.00014779 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3661-13_0_4_load_50 | 51 | 0.00059133 | 0.0001482 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3661-13_0_4_load_52 | 53 | 0.001048 | 0.00026265 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3661-13_0_4_load_53 | 54 | 0.00098208 | 0.00024613 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3661-13_0_4_load_54 | 55 | 0.00035324 | 8.853e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3661-13_0_4_load_55 | 56 | 0.00063636 | 0.00015949 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3661-13_0_4_load_56 | 57 | 0.00072664 | 0.00018211 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3661-13_0_4_load_58 | 59 | 0.00076623 | 0.00019203 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3661-13_0_4_load_59 | 60 | 0.0012068 | 0.00030245 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3661-13_0_4_load_60 | 61 | 0.0018339 | 0.00045962 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3661-13_0_4_load_62 | 62 | 0.0013347 | 0.00033452 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3661-13_0_4_load_61 | 63 | 0.00060969 | 0.0001528 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3661-13_0_4_load_63 | 64 | 0.0015098 | 0.0003784 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3661-13_0_4_load_64 | 65 | 0.0019969 | 0.00050048 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3661-13_0_4_load_65 | 66 | 0.0020288 | 0.00050847 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3661-13_0_4_load_66 | 67 | 0.0013407 | 0.00033601 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3661-13_0_4_load_67 | 68 | 0.0010967 | 0.00027486 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3661-13_0_4_load_68 | 69 | 0.0041919 | 0.0010506 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3661-13_0_4_load_69 | 70 | 0.0012051 | 0.00030204 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3661-13_0_4_load_111 | 71 | 0.00123 | 0.00030825 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3661-13_0_4_load_112 | 72 | 0.00096977 | 0.00024305 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3661-13_0_4_load_70 | 73 | 0.0013235 | 0.0003317 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3661-13_0_4_load_71 | 74 | 0.0027034 | 0.00067753 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3661-13_0_4_load_72 | 75 | 0.0013296 | 0.00033324 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3661-13_0_4_load_73 | 76 | 0.0016042 | 0.00040205 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3661-13_0_4_load_74 | 77 | 0.00041851 | 0.00010489 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3661-13_0_4_load_75 | 78 | 0.0018732 | 0.00046946 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3661-13_0_4_load_102 | 79 | 0.0033108 | 0.00082978 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3661-13_0_4_load_76 | 80 | 0.0022188 | 0.00055607 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3661-13_0_4_load_103 | 81 | 0.00087579 | 0.00021949 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3661-13_0_4_load_78 | 83 | 0.000947 | 0.00023734 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3661-13_0_4_load_79 | 84 | 0.0012671 | 0.00031757 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3661-13_0_4_load_83 | 86 | 0.0025597 | 0.00064153 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3661-13_0_4_load_81 | 87 | 0.00082923 | 0.00020783 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3661-13_0_4_load_82 | 88 | 0.0021535 | 0.00053972 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3661-13_0_4_load_86 | 89 | 0.0021109 | 0.00052904 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3661-13_0_4_load_88 | 90 | 0.001838 | 0.00046064 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3661-13_0_4_load_84 | 91 | 0.0019498 | 0.00048865 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3661-13_0_4_load_85 | 92 | 0.0020881 | 0.00052332 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3661-13_0_4_load_87 | 93 | 0.0018529 | 0.00046438 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3661-13_0_4_load_91 | 94 | 0.0021709 | 0.00054409 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3661-13_0_4_load_93 | 96 | 0.0023229 | 0.00058217 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3661-13_0_4_load_94 | 97 | 0.0030453 | 0.00076323 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3661-13_0_4_load_95 | 98 | 0.0036371 | 0.00091155 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3661-13_0_4_load_97 | 99 | 0.0014193 | 0.0003557 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3661-13_0_4_load_96 | 100 | 0.00074324 | 0.00018627 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3661-13_0_4_load_98 | 101 | 0.00067707 | 0.00016969 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3661-13_0_4_load_129 | 102 | 0.0027435 | 0.00068758 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3661-13_0_4_load_130 | 103 | 0.0012077 | 0.00030267 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3661-13_0_4_load_99 | 104 | 0.0018876 | 0.00047307 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3661-13_0_4_load_100 | 105 | 0.0014172 | 0.00035519 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3661-13_0_4_load_101 | 106 | 0.0010101 | 0.00025316 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3661-13_0_4_load_125 | 108 | 0.0010347 | 0.00025933 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3661-13_0_4_load_104 | 110 | 0.0008279 | 0.00020749 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3661-13_0_4_load_105 | 111 | 0.00075096 | 0.00018821 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3661-13_0_4_load_106 | 112 | 0.0016426 | 0.00041168 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3661-13_0_4_load_107 | 113 | 0.0016007 | 0.00040118 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3661-13_0_4_load_117 | 116 | 0.00093658 | 0.00023473 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3661-13_0_4_load_123 | 117 | 0.0018079 | 0.00045309 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3661-13_0_4_load_140 | 118 | 0.0014343 | 0.00035947 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3661-13_0_4_load_116 | 119 | 0.00050841 | 0.00012742 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3661-13_0_4_load_118 | 121 | 0.0014561 | 0.00036494 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3661-13_0_4_load_115 | 122 | 0.0013008 | 0.000326 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3661-13_0_4_load_119 | 123 | 0.0032341 | 0.00081054 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3661-13_0_4_load_114 | 124 | 0.0013726 | 0.000344 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3661-13_0_4_load_121 | 126 | 0.0023133 | 0.00057976 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3661-13_0_4_load_122 | 127 | 0.0014604 | 0.00036601 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3661-13_0_4_load_124 | 128 | 0.0010888 | 0.00027288 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3661-13_0_4_load_126 | 129 | 0.0010977 | 0.0002751 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3661-13_0_4_load_127 | 130 | 0.00055187 | 0.00013831 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3661-13_0_4_load_134 | 132 | 0.0013824 | 0.00034646 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3661-13_0_4_load_139 | 133 | 0.00096839 | 0.0002427 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3661-13_0_4_load_132 | 134 | 0.0019947 | 0.00049992 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3661-13_0_4_load_131 | 135 | 0.0021573 | 0.00054067 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3661-13_0_4_load_133 | 136 | 0.0013621 | 0.00034137 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3661-13_0_4_load_138 | 137 | 0.00065302 | 0.00016366 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 99 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3661-13_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.073444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3661-13_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0010945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3661-13_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.10455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_3661-13_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.10936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_3661-13_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.10314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_3661-13_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.081422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3661-13_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.12696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_3661-13_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0099515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_3661-13_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.035137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_3661-13_0_4_line_9 | NAYY 4x150 SE | 8 | 22 | 0.051537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_3661-13_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.090974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_3661-13_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.21999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_3661-13_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.001914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_3661-13_0_4_line_13 | NAYY 4x150 SE | 12 | 14 | 0.031544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_3661-13_0_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.017096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3661-13_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.18341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_3661-13_0_4_line_16 | NAYY 4x150 SE | 14 | 18 | 0.020607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_3661-13_0_4_line_17 | NAYY 4x150 SE | 16 | 17 | 0.013598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_3661-13_0_4_line_18 | NAYY 4x150 SE | 17 | 137 | 0.015195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_3661-13_0_4_line_19 | NAYY 4x150 SE | 18 | 37 | 0.00054415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_3661-13_0_4_line_20 | NAYY 4x150 SE | 19 | 20 | 0.17656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3661-13_0_4_line_21 | NAYY 4x150 SE | 20 | 21 | 0.045794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3661-13_0_4_line_22 | NAYY 4x150 SE | 21 | 44 | 0.030577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3661-13_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.049596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_3661-13_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.046219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3661-13_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.0067588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_3661-13_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.023116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3661-13_0_4_line_27 | NAYY 4x150 SE | 25 | 27 | 0.0039092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_3661-13_0_4_line_28 | NAYY 4x150 SE | 26 | 28 | 0.00079803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3661-13_0_4_line_29 | NAYY 4x150 SE | 26 | 29 | 0.077299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3661-13_0_4_line_30 | NAYY 4x150 SE | 27 | 30 | 0.0032289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_3661-13_0_4_line_31 | NAYY 4x150 SE | 28 | 40 | 0.033148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3661-13_0_4_line_32 | NAYY 4x150 SE | 28 | 41 | 0.020945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3661-13_0_4_line_33 | NAYY 4x150 SE | 30 | 31 | 0.016406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_3661-13_0_4_line_34 | NAYY 4x150 SE | 31 | 32 | 0.0063694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_3661-13_0_4_line_35 | NAYY 4x150 SE | 32 | 33 | 0.0041215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_3661-13_0_4_line_36 | NAYY 4x150 SE | 33 | 36 | 0.0024995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_3661-13_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.018484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_3661-13_0_4_line_38 | NAYY 4x150 SE | 34 | 36 | 0.013561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_3661-13_0_4_line_39 | NAYY 4x150 SE | 35 | 37 | 0.028875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_3661-13_0_4_line_40 | NAYY 4x150 SE | 36 | 38 | 0.035708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3661-13_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.013145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3661-13_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.023647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3661-13_0_4_line_43 | NAYY 4x150 SE | 42 | 43 | 0.036283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3661-13_0_4_line_44 | NAYY 4x150 SE | 44 | 45 | 0.024922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3661-13_0_4_line_45 | NAYY 4x150 SE | 45 | 46 | 0.040462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3661-13_0_4_line_46 | NAYY 4x150 SE | 46 | 47 | 0.029821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3661-13_0_4_line_47 | NAYY 4x150 SE | 47 | 94 | 0.064128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3661-13_0_4_line_48 | NAYY 4x150 SE | 48 | 49 | 0.013129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3661-13_0_4_line_49 | NAYY 4x150 SE | 48 | 50 | 0.0094829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3661-13_0_4_line_50 | NAYY 4x150 SE | 49 | 51 | 0.019797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3661-13_0_4_line_51 | NAYY 4x150 SE | 51 | 52 | 0.012836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3661-13_0_4_line_52 | NAYY 4x150 SE | 52 | 53 | 0.0017854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3661-13_0_4_line_53 | NAYY 4x150 SE | 52 | 54 | 0.027333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3661-13_0_4_line_54 | NAYY 4x150 SE | 54 | 55 | 0.021601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3661-13_0_4_line_55 | NAYY 4x150 SE | 55 | 56 | 0.0094766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3661-13_0_4_line_56 | NAYY 4x150 SE | 56 | 57 | 0.014438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3661-13_0_4_line_57 | NAYY 4x150 SE | 57 | 58 | 0.022536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3661-13_0_4_line_58 | NAYY 4x150 SE | 58 | 59 | 0.018918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3661-13_0_4_line_59 | NAYY 4x150 SE | 58 | 60 | 0.012364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3661-13_0_4_line_60 | NAYY 4x150 SE | 59 | 61 | 0.019028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3661-13_0_4_line_61 | NAYY 4x150 SE | 60 | 62 | 0.057374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3661-13_0_4_line_62 | NAYY 4x150 SE | 61 | 63 | 0.016896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3661-13_0_4_line_63 | NAYY 4x150 SE | 62 | 64 | 0.013239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3661-13_0_4_line_64 | NAYY 4x150 SE | 63 | 65 | 0.00060402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3661-13_0_4_line_65 | NAYY 4x150 SE | 64 | 67 | 0.0051669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3661-13_0_4_line_66 | NAYY 4x150 SE | 65 | 66 | 0.014565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3661-13_0_4_line_67 | NAYY 4x150 SE | 67 | 68 | 0.010189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3661-13_0_4_line_68 | NAYY 4x150 SE | 68 | 69 | 0.011226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3661-13_0_4_line_69 | NAYY 4x150 SE | 69 | 70 | 0.0014743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3661-13_0_4_line_70 | NAYY 4x150 SE | 70 | 71 | 0.014491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3661-13_0_4_line_71 | NAYY 4x150 SE | 71 | 72 | 0.0028308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3661-13_0_4_line_72 | NAYY 4x150 SE | 72 | 120 | 0.012672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3661-13_0_4_line_73 | NAYY 4x150 SE | 73 | 74 | 0.0056252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_3661-13_0_4_line_74 | NAYY 4x150 SE | 73 | 75 | 0.026487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_3661-13_0_4_line_75 | NAYY 4x150 SE | 74 | 76 | 0.020197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
76 | LV_3661-13_0_4_line_76 | NAYY 4x150 SE | 75 | 77 | 0.0069325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_3661-13_0_4_line_77 | NAYY 4x150 SE | 76 | 78 | 0.028096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3661-13_0_4_line_78 | NAYY 4x150 SE | 77 | 79 | 0.011673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_3661-13_0_4_line_79 | NAYY 4x150 SE | 78 | 80 | 0.0014503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3661-13_0_4_line_80 | NAYY 4x150 SE | 79 | 81 | 0.0012315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_3661-13_0_4_line_81 | NAYY 4x150 SE | 80 | 82 | 0.013321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3661-13_0_4_line_82 | NAYY 4x150 SE | 81 | 110 | 0.014881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_3661-13_0_4_line_83 | NAYY 4x150 SE | 82 | 83 | 0.018959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3661-13_0_4_line_84 | NAYY 4x150 SE | 82 | 84 | 0.047496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3661-13_0_4_line_85 | NAYY 4x150 SE | 83 | 85 | 0.030668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_3661-13_0_4_line_86 | NAYY 4x150 SE | 84 | 86 | 0.0095957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3661-13_0_4_line_87 | NAYY 4x150 SE | 85 | 87 | 0.0080288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3661-13_0_4_line_88 | NAYY 4x150 SE | 85 | 88 | 0.013356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3661-13_0_4_line_89 | NAYY 4x150 SE | 87 | 89 | 0.012061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3661-13_0_4_line_90 | NAYY 4x150 SE | 88 | 90 | 0.023443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3661-13_0_4_line_91 | NAYY 4x150 SE | 89 | 91 | 0.0070105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_3661-13_0_4_line_92 | NAYY 4x150 SE | 91 | 92 | 0.018416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3661-13_0_4_line_93 | NAYY 4x150 SE | 92 | 93 | 0.02738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3661-13_0_4_line_94 | NAYY 4x150 SE | 94 | 95 | 0.004086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_3661-13_0_4_line_95 | NAYY 4x150 SE | 95 | 96 | 0.01907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_3661-13_0_4_line_96 | NAYY 4x150 SE | 95 | 97 | 0.016478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3661-13_0_4_line_97 | NAYY 4x150 SE | 96 | 98 | 0.03625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3661-13_0_4_line_98 | NAYY 4x150 SE | 97 | 99 | 0.0092277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3661-13_0_4_line_99 | NAYY 4x150 SE | 98 | 100 | 0.010326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3661-13_0_4_line_100 | NAYY 4x150 SE | 99 | 101 | 0.01359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_3661-13_0_4_line_101 | NAYY 4x150 SE | 100 | 102 | 0.0022135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3661-13_0_4_line_102 | NAYY 4x150 SE | 101 | 104 | 0.019395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_3661-13_0_4_line_103 | NAYY 4x150 SE | 102 | 103 | 0.0045941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3661-13_0_4_line_104 | NAYY 4x150 SE | 104 | 105 | 0.010529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_3661-13_0_4_line_105 | NAYY 4x150 SE | 105 | 106 | 0.0081912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_3661-13_0_4_line_106 | NAYY 4x150 SE | 106 | 107 | 0.01176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_3661-13_0_4_line_107 | NAYY 4x150 SE | 107 | 108 | 0.017629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_3661-13_0_4_line_108 | NAYY 4x150 SE | 107 | 109 | 0.000686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_3661-13_0_4_line_109 | NAYY 4x150 SE | 108 | 117 | 0.0015301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_3661-13_0_4_line_110 | NAYY 4x150 SE | 109 | 113 | 0.012256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_3661-13_0_4_line_111 | NAYY 4x150 SE | 110 | 111 | 0.0033599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_3661-13_0_4_line_112 | NAYY 4x150 SE | 111 | 112 | 0.010544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
113 | LV_3661-13_0_4_line_113 | NAYY 4x150 SE | 112 | 113 | 0.00093388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_3661-13_0_4_line_114 | NAYY 4x150 SE | 114 | 115 | 0.016142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_3661-13_0_4_line_115 | NAYY 4x150 SE | 114 | 116 | 0.0031968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_3661-13_0_4_line_116 | NAYY 4x150 SE | 115 | 118 | 0.01437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
117 | LV_3661-13_0_4_line_117 | NAYY 4x150 SE | 116 | 119 | 0.0076211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
118 | LV_3661-13_0_4_line_118 | NAYY 4x150 SE | 117 | 126 | 0.0057353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
119 | LV_3661-13_0_4_line_119 | NAYY 4x150 SE | 118 | 125 | 0.0017199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_3661-13_0_4_line_120 | NAYY 4x150 SE | 119 | 124 | 0.0055616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
121 | LV_3661-13_0_4_line_121 | NAYY 4x150 SE | 120 | 121 | 0.023883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3661-13_0_4_line_122 | NAYY 4x150 SE | 120 | 122 | 0.02255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3661-13_0_4_line_123 | NAYY 4x150 SE | 121 | 123 | 0.0029299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3661-13_0_4_line_124 | NAYY 4x150 SE | 122 | 124 | 0.021111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
125 | LV_3661-13_0_4_line_125 | NAYY 4x150 SE | 125 | 133 | 0.007976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
126 | LV_3661-13_0_4_line_126 | NAYY 4x150 SE | 125 | 131 | 0.014414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
127 | LV_3661-13_0_4_line_127 | NAYY 4x150 SE | 126 | 127 | 0.0046297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_3661-13_0_4_line_128 | NAYY 4x150 SE | 127 | 128 | 0.013789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_3661-13_0_4_line_129 | NAYY 4x150 SE | 128 | 129 | 0.0044024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
130 | LV_3661-13_0_4_line_130 | NAYY 4x150 SE | 129 | 130 | 0.003554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_3661-13_0_4_line_131 | NAYY 4x150 SE | 130 | 131 | 0.010392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
132 | LV_3661-13_0_4_line_132 | NAYY 4x150 SE | 131 | 132 | 0.027216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3661-13_0_4_line_133 | NAYY 4x150 SE | 132 | 134 | 0.0058208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3661-13_0_4_line_134 | NAYY 4x150 SE | 133 | 137 | 0.0046726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
135 | LV_3661-13_0_4_line_135 | NAYY 4x150 SE | 134 | 135 | 0.0038974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3661-13_0_4_line_136 | NAYY 4x150 SE | 135 | 136 | 0.017307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3661-13_0_4_trafo_97 | 0.25 MVA 20/0.4 kV | 138 | 99 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2751781.4795 | 1176111.7908 | 2751790.6548 | 1176108.5536 | 2751809.2183 | 1176080.3889 | 2751815.2077 | 1176064.3383 | 2751819.3288 | 1176052.1662
1 | 2751819.6798 | 1176051.1295 | 2751819.3288 | 1176052.1662
2 | 2751781.4795 | 1176111.7908 | 2751771.5712 | 1176112.8633 | 2751768.345 | 1176116.7405 | 2751764.8842 | 1176124.4482 | 2751747.9154 | 1176143.7127 | 2751728.6693 | 1176162.9084 | 2751721.898 | 1176172.0892 | 2751715.5658 | 1176187.7976
3 | 2751781.4795 | 1176111.7908 | 2751781.5175 | 1176099.7152 | 2751780.3556 | 1176066.7587 | 2751781.2263 | 1176053.5143 | 2751792.9469 | 1176018.0149 | 2751795.8767 | 1176004.7002
4 | 2751715.5658 | 1176187.7976 | 2751706.1324 | 1176211.2117 | 2751697.0305 | 1176222.7355 | 2751679.0367 | 1176240.8177 | 2751660.4641 | 1176249.7334 | 2751644.2779 | 1176255.2616
5 | 2751715.5658 | 1176187.7976 | 2751660.4964 | 1176127.8229
6 | 2751795.8767 | 1176004.7002 | 2751739.6917 | 1175890.8523
7 | 2751644.2779 | 1176255.2616 | 2751639.3652 | 1176256.9394 | 2751635.2517 | 1176259.3349
8 | 2751739.6917 | 1175890.8523 | 2751743.1166 | 1175880.03 | 2751752.5839 | 1175862.8553 | 2751754.741 | 1175859.2811
9 | 2751606.6451 | 1176300.0036 | 2751611.257 | 1176291.5243 | 2751616.0351 | 1176277.0776 | 2751620.3585 | 1176270.0254 | 2751628.3664 | 1176263.3445 | 2751635.2517 | 1176259.3349
10 | 2751306.377 | 1176306.2409 | 2751306.6385 | 1176313.4534 | 2751302.7147 | 1176330.1459 | 2751302.5406 | 1176346.1324 | 2751302.789 | 1176372.0489 | 2751299.0481 | 1176394.8288 | 2751298.7891 | 1176396.4269
11 | 2751504.3298 | 1176474.8518 | 2751298.7891 | 1176396.4269
12 | 2751306.377 | 1176306.2409 | 2751307.5771 | 1176304.7477
13 | 2751504.3298 | 1176474.8518 | 2751506.7735 | 1176463.1374 | 2751508.3694 | 1176457.4842 | 2751510.9209 | 1176451.8439 | 2751515.548 | 1176445.9252
14 | 2751504.3298 | 1176474.8518 | 2751500.8385 | 1176491.5878
15 | 2751306.5855 | 1176121.3447 | 2751307.5771 | 1176304.7477
16 | 2751515.548 | 1176445.9252 | 2751528.0308 | 1176429.958 | 2751528.2406 | 1176429.691
17 | 2751310.9444 | 1176108.4646 | 2751306.5855 | 1176121.3447
18 | 2751310.9444 | 1176108.4646 | 2751315.8154 | 1176094.0714 | 2751315.8154 | 1176094.0714
19 | 2751528.5768 | 1176429.2632 | 2751528.2406 | 1176429.691
20 | 2751502.5736 | 1175778.2576 | 2751497.893 | 1175601.7612
21 | 2751502.5736 | 1175778.2576 | 2751494.9311 | 1175784.3808 | 2751492.2203 | 1175790.2616 | 2751492.2603 | 1175800.1819 | 2751495.4658 | 1175819.5232
22 | 2751493.0036 | 1175849.9189 | 2751495.3693 | 1175834.5442 | 2751495.4658 | 1175819.5232
23 | 2751606.6451 | 1176300.0036 | 2751583.7859 | 1176322.7003 | 2751580.9252 | 1176326.6535 | 2751578.7462 | 1176336.0062 | 2751577.9589 | 1176338.7974
24 | 2751606.6451 | 1176300.0036 | 2751604.4334 | 1176310.0449 | 2751597.2475 | 1176319.004 | 2751595.0853 | 1176325.8773 | 2751596.2083 | 1176330.7652 | 2751598.5278 | 1176334.0042 | 2751602.5696 | 1176341.194
25 | 2751576.1239 | 1176345.3023 | 2751577.9589 | 1176338.7974
26 | 2751608.9398 | 1176363.1022 | 2751607.5534 | 1176351.7914 | 2751603.9434 | 1176343.6379 | 2751602.5696 | 1176341.194
27 | 2751576.1239 | 1176345.3023 | 2751575.0626 | 1176349.0647
28 | 2751608.9398 | 1176363.1022 | 2751609.0369 | 1176363.8943
29 | 2751608.9398 | 1176363.1022 | 2751684.253 | 1176345.6914
30 | 2751575.0626 | 1176349.0647 | 2751574.8903 | 1176349.6755 | 2751573.9779 | 1176352.104
31 | 2751609.0369 | 1176363.8943 | 2751603.8879 | 1176378.7987 | 2751601.2204 | 1176388.417 | 2751600.8119 | 1176395.8017
32 | 2751609.0369 | 1176363.8943 | 2751609.8251 | 1176373.5555 | 2751610.8575 | 1176384.7593
33 | 2751568.1922 | 1176367.4554 | 2751568.8392 | 1176365.7804 | 2751573.9779 | 1176352.104
34 | 2751568.1922 | 1176367.4554 | 2751565.8971 | 1176373.397
35 | 2751564.3846 | 1176377.2304 | 2751564.6576 | 1176376.6059 | 2751565.8971 | 1176373.397
36 | 2751563.3833 | 1176379.5205 | 2751564.3846 | 1176377.2304
37 | 2751557.0474 | 1176391.4552 | 2751550.5113 | 1176401.3467 | 2751546.4166 | 1176406.5581
38 | 2751563.3833 | 1176379.5205 | 2751560.3476 | 1176386.4607 | 2751557.0474 | 1176391.4552
39 | 2751546.4166 | 1176406.5581 | 2751528.5768 | 1176429.2632
40 | 2751563.3833 | 1176379.5205 | 2751565.9541 | 1176384.0114 | 2751567.8105 | 1176389.2292 | 2751572.4554 | 1176404.8483 | 2751575.6618 | 1176412.9359
41 | 2751583.7824 | 1176423.2607 | 2751580.4685 | 1176419.4294 | 2751575.6618 | 1176412.9359
42 | 2751610.8575 | 1176384.7593 | 2751611.3493 | 1176390.0965 | 2751614.7594 | 1176401.6144 | 2751617.5194 | 1176407.2494
43 | 2751625.0195 | 1176442.2515 | 2751622.4969 | 1176417.4118 | 2751617.5194 | 1176407.2494
44 | 2751493.0036 | 1175849.9189 | 2751489.2134 | 1175874.5515
45 | 2751489.2134 | 1175874.5515 | 2751487.2067 | 1175887.5928 | 2751480.0343 | 1175913.8993
46 | 2751480.0343 | 1175913.8993 | 2751479.6878 | 1175915.1701 | 2751468.8447 | 1175941.5314
47 | 2751468.8447 | 1175941.5314 | 2751457.8903 | 1175968.1634 | 2751445.8096 | 1175996.1926 | 2751442.6338 | 1175999.8038
48 | 2751219.2608 | 1175758.4054 | 2751224.3796 | 1175770.4952
49 | 2751215.5635 | 1175749.6729 | 2751219.2608 | 1175758.4054
50 | 2751224.3796 | 1175770.4952 | 2751232.0984 | 1175788.7259
51 | 2751237.1031 | 1175800.5463 | 2751232.0984 | 1175788.7259
52 | 2751237.1031 | 1175800.5463 | 2751235.5104 | 1175799.7393
53 | 2751237.1031 | 1175800.5463 | 2751249.3219 | 1175806.7371 | 2751258.7328 | 1175816.6046
54 | 2751258.7328 | 1175816.6046 | 2751262.4687 | 1175837.3825 | 2751262.6131 | 1175837.8503
55 | 2751262.6131 | 1175837.8503 | 2751265.4079 | 1175846.9053
56 | 2751265.4079 | 1175846.9053 | 2751269.6659 | 1175860.7009
57 | 2751276.3124 | 1175882.2349 | 2751269.6659 | 1175860.7009
58 | 2751276.3124 | 1175882.2349 | 2751284.0853 | 1175876.0814 | 2751287.0285 | 1175868.8608 | 2751287.3958 | 1175867.7108
59 | 2751276.3124 | 1175882.2349 | 2751277.7119 | 1175886.785 | 2751279.0352 | 1175894.2729
60 | 2751287.3958 | 1175867.7108 | 2751289.636 | 1175860.6976 | 2751291.4508 | 1175849.1742
61 | 2751279.0352 | 1175894.2729 | 2751286.9143 | 1175938.8598 | 2751289.1849 | 1175950.7412
62 | 2751294.0793 | 1175832.4844 | 2751291.4508 | 1175849.1742
63 | 2751289.1849 | 1175950.7412 | 2751291.67 | 1175963.7446
64 | 2751294.1733 | 1175831.8877 | 2751294.0793 | 1175832.4844
65 | 2751291.67 | 1175963.7446 | 2751292.6399 | 1175968.8197
66 | 2751296.4392 | 1175817.5003 | 2751294.1733 | 1175831.8877
67 | 2751292.6399 | 1175968.8197 | 2751294.5525 | 1175978.8277
68 | 2751296.6597 | 1175989.8541 | 2751294.5525 | 1175978.8277
69 | 2751296.6597 | 1175989.8541 | 2751296.9364 | 1175991.3022
70 | 2751299.6566 | 1176005.5358 | 2751296.9364 | 1175991.3022
71 | 2751300.3313 | 1176008.2846 | 2751299.7035 | 1176005.7816 | 2751299.6566 | 1176005.5358
72 | 2751303.4143 | 1176020.5761 | 2751300.3313 | 1176008.2846
73 | 2751378.9933 | 1175953.4311 | 2751380.7691 | 1175948.0935
74 | 2751378.9933 | 1175953.4311 | 2751378.9396 | 1175953.5926 | 2751370.7505 | 1175978.6026
75 | 2751380.7691 | 1175948.0935 | 2751387.145 | 1175928.9292
76 | 2751368.5933 | 1175985.1909 | 2751370.7505 | 1175978.6026
77 | 2751396.0143 | 1175902.27 | 2751387.145 | 1175928.9292
78 | 2751368.5933 | 1175985.1909 | 2751364.9609 | 1175996.2847
79 | 2751396.4722 | 1175900.8939 | 2751396.0143 | 1175902.27
80 | 2751364.5777 | 1175997.455 | 2751364.9609 | 1175996.2847
81 | 2751400.8478 | 1175888.3139 | 2751399.1585 | 1175892.8195 | 2751396.4722 | 1175900.8939
82 | 2751364.5777 | 1175997.455 | 2751363.5339 | 1176000.6426 | 2751362.0542 | 1176007.7556 | 2751361.7948 | 1176012.0098
83 | 2751400.8478 | 1175888.3139 | 2751407.502 | 1175870.5615
84 | 2751400.8478 | 1175888.3139 | 2751399.3602 | 1175876.956 | 2751397.2606 | 1175848.0348 | 2751395.5686 | 1175841.1974
85 | 2751416.8318 | 1175841.4009 | 2751413.7803 | 1175853.8119 | 2751407.502 | 1175870.5615
86 | 2751393.2636 | 1175831.8827 | 2751395.5686 | 1175841.1974
87 | 2751416.8318 | 1175841.4009 | 2751423.5234 | 1175842.6375 | 2751424.6212 | 1175843.1786
88 | 2751416.8318 | 1175841.4009 | 2751417.5824 | 1175838.3285 | 2751416.3304 | 1175828.2122
89 | 2751432.8091 | 1175851.4092 | 2751432.1664 | 1175849.5835 | 2751428.5167 | 1175845.0988 | 2751424.6212 | 1175843.1786
90 | 2751416.3304 | 1175828.2122 | 2751415.2258 | 1175819.2867 | 2751416.4472 | 1175804.8892
91 | 2751434.7087 | 1175858.1407 | 2751434.0504 | 1175854.9354 | 2751432.8091 | 1175851.4092
92 | 2751434.7087 | 1175858.1407 | 2751435.685 | 1175862.8943 | 2751436.0257 | 1175867.5734 | 2751436.0451 | 1175876.4448
93 | 2751438.3304 | 1175903.5994 | 2751438.4478 | 1175895.2239 | 2751436.0587 | 1175882.62 | 2751436.0451 | 1175876.4448
94 | 2751439.9354 | 1176002.8721 | 2751442.6338 | 1175999.8038
95 | 2751439.9354 | 1176002.8721 | 2751449.1557 | 1176008.754 | 2751456.376 | 1176012.4971
96 | 2751439.9354 | 1176002.8721 | 2751437.0377 | 1176006.1683 | 2751428.9134 | 1176015.12
97 | 2751456.376 | 1176012.4971 | 2751457.8599 | 1176013.2663 | 2751469.7746 | 1176016.6365 | 2751472.8239 | 1176017.9368 | 2751475.7272 | 1176020.779 | 2751481.3718 | 1176034.4799
98 | 2751422.7119 | 1176021.9531 | 2751422.7119 | 1176021.9531 | 2751428.9134 | 1176015.12
99 | 2751485.3052 | 1176044.0273 | 2751481.3718 | 1176034.4799
100 | 2751410.2166 | 1176026.0951 | 2751413.1499 | 1176026.5712 | 2751422.7119 | 1176021.9531
101 | 2751485.3052 | 1176044.0273 | 2751486.1484 | 1176046.0739
102 | 2751410.2166 | 1176026.0951 | 2751398.4647 | 1176024.1876 | 2751391.0938 | 1176025.5126
103 | 2751487.8984 | 1176050.3217 | 2751486.1484 | 1176046.0739
104 | 2751391.0938 | 1176025.5126 | 2751384.0362 | 1176026.7812 | 2751381.576 | 1176029.0668
105 | 2751381.576 | 1176029.0668 | 2751379.6661 | 1176030.841 | 2751376.0138 | 1176035.0655
106 | 2751365.6926 | 1176038.7394 | 2751368.9024 | 1176038.8316 | 2751373.4188 | 1176038.0671 | 2751376.0138 | 1176035.0655
107 | 2751365.6926 | 1176038.7394 | 2751364.6976 | 1176056.3399 | 2751364.6976 | 1176056.3399
108 | 2751365.0047 | 1176038.7221 | 2751365.6926 | 1176038.7394
109 | 2751364.6976 | 1176056.3399 | 2751364.0379 | 1176057.7205
110 | 2751365.0047 | 1176038.7221 | 2751364.4227 | 1176029.9669 | 2751363.6098 | 1176026.582
111 | 2751361.7948 | 1176012.0098 | 2751361.5904 | 1176015.3635
112 | 2751363.3917 | 1176025.6739 | 2751361.4538 | 1176017.6041 | 2751361.5904 | 1176015.3635
113 | 2751363.6098 | 1176026.582 | 2751363.3917 | 1176025.6739
114 | 2751330.0355 | 1176069.1206 | 2751335.8319 | 1176058.547 | 2751337.1533 | 1176054.6771
115 | 2751337.1533 | 1176054.6771 | 2751336.0418 | 1176051.6798
116 | 2751330.0355 | 1176069.1206 | 2751323.5258 | 1176079.4761 | 2751322.5286 | 1176081.3676
117 | 2751333.6838 | 1176044.4508 | 2751334.0814 | 1176046.3929 | 2751336.0418 | 1176051.6798
118 | 2751360.2099 | 1176061.9045 | 2751363.5268 | 1176058.7902 | 2751364.0379 | 1176057.7205
119 | 2751321.7265 | 1176082.889 | 2751322.5286 | 1176081.3676
120 | 2751333.6838 | 1176044.4508 | 2751332.9716 | 1176040.9715 | 2751331.5544 | 1176039.5458
121 | 2751303.4143 | 1176020.5761 | 2751304.8654 | 1176029.142 | 2751309.3547 | 1176043.6588
122 | 2751303.4143 | 1176020.5761 | 2751318.1989 | 1176020.5378 | 2751319.3606 | 1176024.2034 | 2751319.9891 | 1176028.073
123 | 2751310.2204 | 1176046.4579 | 2751309.3547 | 1176043.6588
124 | 2751331.5544 | 1176039.5458 | 2751331.5544 | 1176039.5458 | 2751322.6016 | 1176039.7312 | 2751321.7436 | 1176038.8756 | 2751319.9891 | 1176028.073
125 | 2751321.7265 | 1176082.889 | 2751317.9991 | 1176089.9404
126 | 2751321.7265 | 1176082.889 | 2751335.6471 | 1176086.7766
127 | 2751360.2099 | 1176061.9045 | 2751356.8347 | 1176065.0735
128 | 2751344.9561 | 1176070.9651 | 2751352.074 | 1176069.5434 | 2751356.8347 | 1176065.0735
129 | 2751344.9561 | 1176070.9651 | 2751344.9561 | 1176070.9651 | 2751342.7225 | 1176074.7589
130 | 2751340.9194 | 1176077.8215 | 2751342.7225 | 1176074.7589
131 | 2751335.6471 | 1176086.7766 | 2751340.9194 | 1176077.8215
132 | 2751335.6471 | 1176086.7766 | 2751337.6698 | 1176098.4483 | 2751340.2635 | 1176104.1629 | 2751342.7412 | 1176106.2938 | 2751348.4562 | 1176107.4277 | 2751348.4562 | 1176107.4277
133 | 2751348.4562 | 1176107.4277 | 2751353.1026 | 1176103.9217
134 | 2751317.9991 | 1176089.9404 | 2751315.8154 | 1176094.0714
135 | 2751356.2136 | 1176101.5741 | 2751353.1026 | 1176103.9217
136 | 2751362.1585 | 1176085.422 | 2751357.9486 | 1176098.8935 | 2751356.2136 | 1176101.5741

## bus_geodata
| x | y | coords
0 | 2751819.3288 | 1176052.1662
1 | 2751781.4795 | 1176111.7908
2 | 2751819.6798 | 1176051.1295
3 | 2751715.5658 | 1176187.7976
4 | 2751795.8767 | 1176004.7002
5 | 2751644.2779 | 1176255.2616
6 | 2751660.4964 | 1176127.8229
7 | 2751739.6917 | 1175890.8523
8 | 2751635.2517 | 1176259.3349
9 | 2751754.741 | 1175859.2811
10 | 2751298.7891 | 1176396.4269
11 | 2751306.377 | 1176306.2409
12 | 2751504.3298 | 1176474.8518
13 | 2751307.5771 | 1176304.7477
14 | 2751515.548 | 1176445.9252
15 | 2751500.8385 | 1176491.5878
16 | 2751306.5855 | 1176121.3447
17 | 2751310.9444 | 1176108.4646
18 | 2751528.2406 | 1176429.691
19 | 2751497.893 | 1175601.7612
20 | 2751502.5736 | 1175778.2576
21 | 2751495.4658 | 1175819.5232
22 | 2751606.6451 | 1176300.0036
23 | 2751577.9589 | 1176338.7974
24 | 2751602.5696 | 1176341.194
25 | 2751576.1239 | 1176345.3023
26 | 2751608.9398 | 1176363.1022
27 | 2751575.0626 | 1176349.0647
28 | 2751609.0369 | 1176363.8943
29 | 2751684.253 | 1176345.6914
30 | 2751573.9779 | 1176352.104
31 | 2751568.1922 | 1176367.4554
32 | 2751565.8971 | 1176373.397
33 | 2751564.3846 | 1176377.2304
34 | 2751557.0474 | 1176391.4552
35 | 2751546.4166 | 1176406.5581
36 | 2751563.3833 | 1176379.5205
37 | 2751528.5768 | 1176429.2632
38 | 2751575.6618 | 1176412.9359
39 | 2751583.7824 | 1176423.2607
40 | 2751600.8119 | 1176395.8017
41 | 2751610.8575 | 1176384.7593
42 | 2751617.5194 | 1176407.2494
43 | 2751625.0195 | 1176442.2515
44 | 2751493.0036 | 1175849.9189
45 | 2751489.2134 | 1175874.5515
46 | 2751480.0343 | 1175913.8993
47 | 2751468.8447 | 1175941.5314
48 | 2751219.2608 | 1175758.4054
49 | 2751224.3796 | 1175770.4952
50 | 2751215.5635 | 1175749.6729
51 | 2751232.0984 | 1175788.7259
52 | 2751237.1031 | 1175800.5463
53 | 2751235.5104 | 1175799.7393
54 | 2751258.7328 | 1175816.6046
55 | 2751262.6131 | 1175837.8503
56 | 2751265.4079 | 1175846.9053
57 | 2751269.6659 | 1175860.7009
58 | 2751276.3124 | 1175882.2349
59 | 2751287.3958 | 1175867.7108
60 | 2751279.0352 | 1175894.2729
61 | 2751291.4508 | 1175849.1742
62 | 2751289.1849 | 1175950.7412
63 | 2751294.0793 | 1175832.4844
64 | 2751291.67 | 1175963.7446
65 | 2751294.1733 | 1175831.8877
66 | 2751296.4392 | 1175817.5003
67 | 2751292.6399 | 1175968.8197
68 | 2751294.5525 | 1175978.8277
69 | 2751296.6597 | 1175989.8541
70 | 2751296.9364 | 1175991.3022
71 | 2751299.6566 | 1176005.5358
72 | 2751300.3313 | 1176008.2846
73 | 2751378.9933 | 1175953.4311
74 | 2751380.7691 | 1175948.0935
75 | 2751370.7505 | 1175978.6026
76 | 2751387.145 | 1175928.9292
77 | 2751368.5933 | 1175985.1909
78 | 2751396.0144 | 1175902.27
79 | 2751364.9609 | 1175996.2847
80 | 2751396.4722 | 1175900.8939
81 | 2751364.5777 | 1175997.455
82 | 2751400.8478 | 1175888.3139
83 | 2751407.502 | 1175870.5615
84 | 2751395.5686 | 1175841.1974
85 | 2751416.8318 | 1175841.4009
86 | 2751393.2636 | 1175831.8827
87 | 2751424.6212 | 1175843.1786
88 | 2751416.3304 | 1175828.2122
89 | 2751432.8091 | 1175851.4092
90 | 2751416.4472 | 1175804.8892
91 | 2751434.7087 | 1175858.1407
92 | 2751436.0451 | 1175876.4448
93 | 2751438.3304 | 1175903.5994
94 | 2751442.6338 | 1175999.8038
95 | 2751439.9354 | 1176002.8721
96 | 2751456.376 | 1176012.4971
97 | 2751428.9134 | 1176015.12
98 | 2751481.3718 | 1176034.4799
99 | 2751422.7119 | 1176021.9531
100 | 2751485.3052 | 1176044.0273
101 | 2751410.2166 | 1176026.0951
102 | 2751486.1484 | 1176046.0739
103 | 2751487.8984 | 1176050.3217
104 | 2751391.0938 | 1176025.5126
105 | 2751381.576 | 1176029.0668
106 | 2751376.0138 | 1176035.0655
107 | 2751365.6926 | 1176038.7394
108 | 2751364.6976 | 1176056.3399
109 | 2751365.0047 | 1176038.7221
110 | 2751361.7948 | 1176012.0098
111 | 2751361.5904 | 1176015.3635
112 | 2751363.3917 | 1176025.6739
113 | 2751363.6098 | 1176026.582
114 | 2751337.1533 | 1176054.6771
115 | 2751330.0355 | 1176069.1206
116 | 2751336.0418 | 1176051.6798
117 | 2751364.0379 | 1176057.7205
118 | 2751322.5286 | 1176081.3676
119 | 2751333.6838 | 1176044.4508
120 | 2751303.4143 | 1176020.5761
121 | 2751309.3547 | 1176043.6588
122 | 2751319.9891 | 1176028.073
123 | 2751310.2204 | 1176046.4579
124 | 2751331.5544 | 1176039.5458
125 | 2751321.7265 | 1176082.889
126 | 2751360.2099 | 1176061.9045
127 | 2751356.8347 | 1176065.0735
128 | 2751344.9561 | 1176070.9651
129 | 2751342.7225 | 1176074.7589
130 | 2751340.9194 | 1176077.8215
131 | 2751335.6471 | 1176086.7766
132 | 2751348.4562 | 1176107.4277
133 | 2751317.9991 | 1176089.9404
134 | 2751353.1026 | 1176103.9217
135 | 2751356.2136 | 1176101.5741
136 | 2751362.1585 | 1176085.422
137 | 2751315.8154 | 1176094.0714
138 | 2751439.9354 | 1176002.8721

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1