## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3672-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3672-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3672-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3672-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3672-7_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3672-7_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3672-7_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3672-7_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_3672-7_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_3672-7_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_3672-7_0_3_node_107 | 0.4 | n |  | TRUE
11 | bus_LV_3672-7_0_3_node_106 | 0.4 | n |  | TRUE
12 | bus_LV_3672-7_0_3_node_115 | 0.4 | n |  | TRUE
13 | bus_LV_3672-7_0_3_node_151 | 0.4 | n |  | TRUE
14 | bus_LV_3672-7_0_3_node_105 | 0.4 | n |  | TRUE
15 | bus_LV_3672-7_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_3672-7_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_3672-7_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_3672-7_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_3672-7_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_3672-7_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_3672-7_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_3672-7_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_3672-7_0_3_node_119 | 0.4 | n |  | TRUE
24 | bus_LV_3672-7_0_3_node_124 | 0.4 | n |  | TRUE
25 | bus_LV_3672-7_0_3_node_136 | 0.4 | n |  | TRUE
26 | bus_LV_3672-7_0_3_node_118 | 0.4 | n |  | TRUE
27 | bus_LV_3672-7_0_3_node_125 | 0.4 | n |  | TRUE
28 | bus_LV_3672-7_0_3_node_122 | 0.4 | n |  | TRUE
29 | bus_LV_3672-7_0_3_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_3672-7_0_3_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_3672-7_0_3_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_3672-7_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_3672-7_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_3672-7_0_3_node_129 | 0.4 | n |  | TRUE
35 | bus_LV_3672-7_0_3_node_131 | 0.4 | n |  | TRUE
36 | bus_LV_3672-7_0_3_node_127 | 0.4 | n |  | TRUE
37 | bus_LV_3672-7_0_3_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_3672-7_0_3_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_3672-7_0_3_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_3672-7_0_3_node_144 | 0.4 | n |  | TRUE
41 | bus_LV_3672-7_0_3_node_142 | 0.4 | n |  | TRUE
42 | bus_LV_3672-7_0_3_node_146 | 0.4 | n |  | TRUE
43 | bus_LV_3672-7_0_3_node_145 | 0.4 | n |  | TRUE
44 | bus_LV_3672-7_0_3_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_3672-7_0_3_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_3672-7_0_3_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_3672-7_0_3_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_3672-7_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_3672-7_0_3_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_3672-7_0_3_node_135 | 0.4 | n |  | TRUE
51 | bus_LV_3672-7_0_3_node_85 | 0.4 | n |  | TRUE
52 | bus_LV_3672-7_0_3_node_133 | 0.4 | n |  | TRUE
53 | bus_LV_3672-7_0_3_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_3672-7_0_3_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_3672-7_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_3672-7_0_3_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_3672-7_0_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_3672-7_0_3_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_3672-7_0_3_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_3672-7_0_3_node_96 | 0.4 | n |  | TRUE
61 | bus_LV_3672-7_0_3_node_97 | 0.4 | n |  | TRUE
62 | bus_LV_3672-7_0_3_node_76 | 0.4 | n |  | TRUE
63 | bus_LV_3672-7_0_3_node_75 | 0.4 | n |  | TRUE
64 | bus_LV_3672-7_0_3_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_3672-7_0_3_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_3672-7_0_3_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_3672-7_0_3_node_41 | 0.4 | n |  | TRUE
68 | bus_LV_3672-7_0_3_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_3672-7_0_3_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_3672-7_0_3_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_3672-7_0_3_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_3672-7_0_3_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_3672-7_0_3_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_3672-7_0_3_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_3672-7_0_3_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_3672-7_0_3_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_3672-7_0_3_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_3672-7_0_3_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_3672-7_0_3_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_3672-7_0_3_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_3672-7_0_3_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_3672-7_0_3_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_3672-7_0_3_node_57 | 0.4 | n |  | TRUE
84 | bus_LV_3672-7_0_3_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_3672-7_0_3_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_3672-7_0_3_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_3672-7_0_3_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_3672-7_0_3_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_3672-7_0_3_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_3672-7_0_3_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_3672-7_0_3_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_3672-7_0_3_node_68 | 0.4 | n |  | TRUE
93 | bus_LV_3672-7_0_3_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_3672-7_0_3_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_3672-7_0_3_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_3672-7_0_3_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_3672-7_0_3_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_3672-7_0_3_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_3672-7_0_3_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_3672-7_0_3_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_3672-7_0_3_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_3672-7_0_3_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_3672-7_0_3_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_3672-7_0_3_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_3672-7_0_3_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_3672-7_0_3_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_3672-7_0_3_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_3672-7_0_3_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_3672-7_0_3_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_3672-7_0_3_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_3672-7_0_3_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_3672-7_0_3_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_3672-7_0_3_node_92 | 0.4 | n |  | TRUE
114 | bus_LV_3672-7_0_3_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_3672-7_0_3_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_3672-7_0_3_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_3672-7_0_3_node_147 | 0.4 | n |  | TRUE
118 | bus_LV_3672-7_0_3_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_3672-7_0_3_node_120 | 0.4 | n |  | TRUE
120 | bus_LV_3672-7_0_3_node_99 | 0.4 | n |  | TRUE
121 | bus_LV_3672-7_0_3_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_3672-7_0_3_node_102 | 0.4 | n |  | TRUE
123 | bus_LV_3672-7_0_3_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_3672-7_0_3_node_101 | 0.4 | n |  | TRUE
125 | bus_LV_3672-7_0_3_node_103 | 0.4 | n |  | TRUE
126 | bus_LV_3672-7_0_3_node_148 | 0.4 | n |  | TRUE
127 | bus_LV_3672-7_0_3_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_3672-7_0_3_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_3672-7_0_3_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_3672-7_0_3_node_112 | 0.4 | n |  | TRUE
131 | bus_LV_3672-7_0_3_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_3672-7_0_3_node_116 | 0.4 | n |  | TRUE
133 | bus_LV_3672-7_0_3_node_117 | 0.4 | n |  | TRUE
134 | bus_LV_3672-7_0_3_node_121 | 0.4 | n |  | TRUE
135 | bus_LV_3672-7_0_3_node_123 | 0.4 | n |  | TRUE
136 | bus_LV_3672-7_0_3_node_126 | 0.4 | n |  | TRUE
137 | bus_LV_3672-7_0_3_node_128 | 0.4 | n |  | TRUE
138 | bus_LV_3672-7_0_3_node_130 | 0.4 | n |  | TRUE
139 | bus_LV_3672-7_0_3_node_132 | 0.4 | n |  | TRUE
140 | bus_LV_3672-7_0_3_node_140 | 0.4 | n |  | TRUE
141 | bus_LV_3672-7_0_3_node_137 | 0.4 | n |  | TRUE
142 | bus_LV_3672-7_0_3_node_134 | 0.4 | n |  | TRUE
143 | bus_LV_3672-7_0_3_node_141 | 0.4 | n |  | TRUE
144 | bus_LV_3672-7_0_3_node_138 | 0.4 | n |  | TRUE
145 | bus_LV_3672-7_0_3_node_149 | 0.4 | n |  | TRUE
146 | bus_LV_3672-7_0_3_node_150 | 0.4 | n |  | TRUE
147 | bus_LV_3672-7_0_3_node_139 | 0.4 | n |  | TRUE
148 | bus_MV_56_0_node_142 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3672-7_0_3_load_0 | 0 | 0.00011095 | 2.7806e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3672-7_0_3_load_1 | 1 | 0.00018732 | 4.6946e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3672-7_0_3_load_3 | 3 | 0.00019803 | 4.9631e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3672-7_0_3_load_4 | 4 | 0.00026804 | 6.7178e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3672-7_0_3_load_5 | 5 | 0.00015027 | 3.7662e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3672-7_0_3_load_6 | 6 | 0.00010468 | 2.6235e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3672-7_0_3_load_9 | 9 | 0.00017828 | 4.4681e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3672-7_0_3_load_107 | 10 | 0.00012109 | 3.0347e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3672-7_0_3_load_106 | 11 | 7.9756e-05 | 1.9989e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3672-7_0_3_load_115 | 12 | 0.00015087 | 3.7811e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3672-7_0_3_load_151 | 13 | 0.00015487 | 3.8814e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3672-7_0_3_load_10 | 15 | 0.0001045 | 2.6191e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3672-7_0_3_load_14 | 17 | 0.00025798 | 6.4657e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3672-7_0_3_load_15 | 18 | 0.00024421 | 6.1205e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3672-7_0_3_load_16 | 19 | 0.0001371 | 3.4362e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3672-7_0_3_load_12 | 21 | 0.0001385 | 3.471e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3672-7_0_3_load_136 | 25 | 0.00022248 | 5.576e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3672-7_0_3_load_125 | 27 | 0.00019959 | 5.0022e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3672-7_0_3_load_122 | 28 | 0.00020764 | 5.204e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3672-7_0_3_load_17 | 29 | 7.5816e-05 | 1.9001e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3672-7_0_3_load_19 | 30 | 0.0004726 | 0.00011844 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3672-7_0_3_load_25 | 32 | 0.00010734 | 2.6903e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3672-7_0_3_load_22 | 33 | 0.00020424 | 5.1188e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3672-7_0_3_load_127 | 36 | 0.00010212 | 2.5594e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3672-7_0_3_load_21 | 37 | 9.5694e-05 | 2.3983e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3672-7_0_3_load_23 | 38 | 0.00024618 | 6.1697e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3672-7_0_3_load_142 | 41 | 9.1114e-05 | 2.2835e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3672-7_0_3_load_146 | 42 | 8.369e-05 | 2.0975e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3672-7_0_3_load_145 | 43 | 8.1468e-05 | 2.0418e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3672-7_0_3_load_27 | 44 | 0.00036112 | 9.0506e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3672-7_0_3_load_28 | 45 | 0.0014241 | 0.00035692 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3672-7_0_3_load_31 | 48 | 0.0019481 | 0.00048824 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3672-7_0_3_load_32 | 49 | 0.001513 | 0.00037918 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3672-7_0_3_load_135 | 50 | 0.0015023 | 0.0003765 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3672-7_0_3_load_133 | 52 | 0.00010776 | 2.7008e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3672-7_0_3_load_33 | 53 | 0.00063467 | 0.00015906 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3672-7_0_3_load_37 | 54 | 0.0010016 | 0.00025102 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3672-7_0_3_load_39 | 55 | 0.018707 | 0.0046884 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3672-7_0_3_load_36 | 56 | 0.00061026 | 0.00015295 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3672-7_0_3_load_45 | 57 | 0.0006783 | 0.00017 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3672-7_0_3_load_38 | 58 | 0.0012782 | 0.00032034 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3672-7_0_3_load_40 | 59 | 0.0017488 | 0.00043829 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3672-7_0_3_load_96 | 60 | 0.00011081 | 2.7772e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3672-7_0_3_load_97 | 61 | 0.00015292 | 3.8325e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3672-7_0_3_load_76 | 62 | 0.0091912 | 0.0023035 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3672-7_0_3_load_75 | 63 | 0.0017054 | 0.00042741 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3672-7_0_3_load_46 | 64 | 0.0096693 | 0.0024234 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3672-7_0_3_load_43 | 65 | 0.0007238 | 0.0001814 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3672-7_0_3_load_44 | 66 | 0.00063157 | 0.00015829 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3672-7_0_3_load_41 | 67 | 0.0004557 | 0.00011421 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3672-7_0_3_load_42 | 68 | 0.0013999 | 0.00035085 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3672-7_0_3_load_48 | 69 | 0.0050878 | 0.0012751 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3672-7_0_3_load_49 | 70 | 0.0015419 | 0.00038645 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3672-7_0_3_load_47 | 71 | 0.008004 | 0.002006 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3672-7_0_3_load_51 | 72 | 0.0060433 | 0.0015146 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3672-7_0_3_load_50 | 74 | 0.0018603 | 0.00046623 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3672-7_0_3_load_55 | 75 | 0.0036779 | 0.00092176 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3672-7_0_3_load_56 | 76 | 0.0035085 | 0.00087932 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3672-7_0_3_load_53 | 77 | 0.0032587 | 0.0008167 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3672-7_0_3_load_54 | 78 | 0.00749 | 0.0018772 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3672-7_0_3_load_59 | 79 | 0.0010289 | 0.00025786 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3672-7_0_3_load_73 | 80 | 0.0059923 | 0.0015018 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3672-7_0_3_load_74 | 82 | 0.0064617 | 0.0016195 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3672-7_0_3_load_57 | 83 | 0.0027783 | 0.00069631 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3672-7_0_3_load_58 | 84 | 0.0027725 | 0.00069486 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3672-7_0_3_load_63 | 86 | 0.0056641 | 0.0014196 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3672-7_0_3_load_62 | 87 | 0.0022119 | 0.00055434 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3672-7_0_3_load_64 | 88 | 0.0032269 | 0.00080873 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3672-7_0_3_load_66 | 89 | 0.001724 | 0.00043206 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3672-7_0_3_load_65 | 90 | 0.003124 | 0.00078294 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3672-7_0_3_load_67 | 91 | 0.0011854 | 0.0002971 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3672-7_0_3_load_68 | 92 | 0.00098671 | 0.00024729 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3672-7_0_3_load_69 | 93 | 0.0013671 | 0.00034262 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3672-7_0_3_load_70 | 94 | 0.003062 | 0.00076742 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3672-7_0_3_load_71 | 95 | 0.00078904 | 0.00019775 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3672-7_0_3_load_72 | 96 | 0.0032354 | 0.00081087 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3672-7_0_3_load_77 | 97 | 0.0013188 | 0.00033053 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3672-7_0_3_load_78 | 98 | 0.0021803 | 0.00054644 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3672-7_0_3_load_79 | 99 | 0.0014875 | 0.00037279 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3672-7_0_3_load_81 | 101 | 0.0014992 | 0.00037573 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3672-7_0_3_load_91 | 104 | 0.00084638 | 0.00021212 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3672-7_0_3_load_90 | 105 | 0.00056232 | 0.00014093 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3672-7_0_3_load_84 | 106 | 0.0013509 | 0.00033858 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3672-7_0_3_load_88 | 108 | 0.0022961 | 0.00057545 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3672-7_0_3_load_86 | 109 | 0.0015046 | 0.0003771 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3672-7_0_3_load_89 | 110 | 0.00090537 | 0.00022691 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3672-7_0_3_load_87 | 111 | 0.0023676 | 0.00059339 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3672-7_0_3_load_93 | 112 | 0.00089778 | 0.00022501 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3672-7_0_3_load_92 | 113 | 0.0017193 | 0.00043089 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3672-7_0_3_load_94 | 114 | 0.00099818 | 0.00025017 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3672-7_0_3_load_98 | 115 | 0.00015344 | 3.8457e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3672-7_0_3_load_109 | 116 | 0.00013562 | 3.399e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3672-7_0_3_load_147 | 117 | 0.00057922 | 0.00014517 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3672-7_0_3_load_110 | 118 | 0.00011901 | 2.9827e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3672-7_0_3_load_120 | 119 | 0.00025453 | 6.3792e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3672-7_0_3_load_99 | 120 | 0.00012735 | 3.1917e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3672-7_0_3_load_100 | 121 | 6.4673e-05 | 1.6209e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3672-7_0_3_load_101 | 124 | 8.2582e-05 | 2.0697e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3672-7_0_3_load_148 | 126 | 7.1338e-05 | 1.7879e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3672-7_0_3_load_113 | 128 | 0.00032695 | 8.1942e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3672-7_0_3_load_111 | 129 | 0.00027011 | 6.7695e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3672-7_0_3_load_114 | 131 | 0.00024371 | 6.108e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3672-7_0_3_load_116 | 132 | 0.00016316 | 4.0891e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3672-7_0_3_load_117 | 133 | 0.00053201 | 0.00013333 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3672-7_0_3_load_121 | 134 | 0.00015846 | 3.9713e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3672-7_0_3_load_123 | 135 | 0.00015281 | 3.8297e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3672-7_0_3_load_126 | 136 | 0.00044057 | 0.00011042 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3672-7_0_3_load_128 | 137 | 6.6228e-05 | 1.6598e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3672-7_0_3_load_130 | 138 | 0.00019583 | 4.908e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3672-7_0_3_load_140 | 140 | 0.00014974 | 3.7528e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3672-7_0_3_load_137 | 141 | 0.00021867 | 5.4805e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3672-7_0_3_load_134 | 142 | 0.00014389 | 3.6062e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3672-7_0_3_load_141 | 143 | 0.00025063 | 6.2813e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3672-7_0_3_load_138 | 144 | 0.00011504 | 2.8831e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3672-7_0_3_load_149 | 145 | 0.00012409 | 3.1101e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3672-7_0_3_load_150 | 146 | 0.00068841 | 0.00017253 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3672-7_0_3_load_139 | 147 | 0.00057159 | 0.00014325 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3672-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.11515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3672-7_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.017735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3672-7_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0089564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3672-7_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.006121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3672-7_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.016189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3672-7_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.022921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3672-7_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.20454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3672-7_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3672-7_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.020496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3672-7_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.051407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3672-7_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.066275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3672-7_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.0036052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3672-7_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.16664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3672-7_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.10786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3672-7_0_3_line_14 | NAYY 4x150 SE | 14 | 127 | 0.012265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3672-7_0_3_line_15 | NAYY 4x150 SE | 14 | 125 | 0.010398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3672-7_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.10772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3672-7_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.028827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3672-7_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0062275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3672-7_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.084359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3672-7_0_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.12679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3672-7_0_3_line_21 | NAYY 4x150 SE | 19 | 29 | 0.2096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3672-7_0_3_line_22 | NAYY 4x150 SE | 20 | 30 | 0.04815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3672-7_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.050381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3672-7_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.20559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3672-7_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.006505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3672-7_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.14021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3672-7_0_3_line_27 | NAYY 4x150 SE | 23 | 26 | 0.22932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3672-7_0_3_line_28 | NAYY 4x150 SE | 24 | 27 | 0.03236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3672-7_0_3_line_29 | NAYY 4x150 SE | 24 | 28 | 0.006732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3672-7_0_3_line_30 | NAYY 4x150 SE | 25 | 50 | 0.053633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3672-7_0_3_line_31 | NAYY 4x150 SE | 26 | 119 | 0.094104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3672-7_0_3_line_32 | NAYY 4x150 SE | 26 | 133 | 0.044363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3672-7_0_3_line_33 | NAYY 4x150 SE | 28 | 134 | 0.068404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3672-7_0_3_line_34 | NAYY 4x150 SE | 29 | 31 | 0.025942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3672-7_0_3_line_35 | NAYY 4x150 SE | 30 | 34 | 0.042854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3672-7_0_3_line_36 | NAYY 4x150 SE | 31 | 32 | 0.1448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3672-7_0_3_line_37 | NAYY 4x150 SE | 31 | 33 | 0.092765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3672-7_0_3_line_38 | NAYY 4x150 SE | 33 | 37 | 0.013562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3672-7_0_3_line_39 | NAYY 4x150 SE | 34 | 35 | 0.007218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3672-7_0_3_line_40 | NAYY 4x150 SE | 34 | 36 | 0.059362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3672-7_0_3_line_41 | NAYY 4x150 SE | 35 | 140 | 0.01033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3672-7_0_3_line_42 | NAYY 4x150 SE | 35 | 141 | 0.056079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3672-7_0_3_line_43 | NAYY 4x150 SE | 36 | 136 | 0.010074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3672-7_0_3_line_44 | NAYY 4x150 SE | 37 | 38 | 0.10601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3672-7_0_3_line_45 | NAYY 4x150 SE | 38 | 39 | 0.042174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3672-7_0_3_line_46 | NAYY 4x150 SE | 39 | 40 | 0.010469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3672-7_0_3_line_47 | NAYY 4x150 SE | 39 | 41 | 0.021084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3672-7_0_3_line_48 | NAYY 4x150 SE | 40 | 42 | 0.025015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3672-7_0_3_line_49 | NAYY 4x150 SE | 40 | 43 | 0.047061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3672-7_0_3_line_50 | NAYY 4x150 SE | 44 | 45 | 0.030631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3672-7_0_3_line_51 | NAYY 4x150 SE | 44 | 46 | 0.021321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3672-7_0_3_line_52 | NAYY 4x150 SE | 45 | 47 | 0.0068355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3672-7_0_3_line_53 | NAYY 4x150 SE | 46 | 48 | 0.0055933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3672-7_0_3_line_54 | NAYY 4x150 SE | 46 | 49 | 0.019946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3672-7_0_3_line_55 | NAYY 4x150 SE | 47 | 53 | 0.036882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3672-7_0_3_line_56 | NAYY 4x150 SE | 48 | 54 | 0.031189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3672-7_0_3_line_57 | NAYY 4x150 SE | 49 | 55 | 0.049735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3672-7_0_3_line_58 | NAYY 4x150 SE | 50 | 51 | 0.37295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3672-7_0_3_line_59 | NAYY 4x150 SE | 50 | 52 | 0.21256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3672-7_0_3_line_60 | NAYY 4x150 SE | 51 | 110 | 0.028722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3672-7_0_3_line_61 | NAYY 4x150 SE | 52 | 139 | 0.05802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3672-7_0_3_line_62 | NAYY 4x150 SE | 54 | 58 | 0.0032589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3672-7_0_3_line_63 | NAYY 4x150 SE | 55 | 59 | 0.01093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3672-7_0_3_line_64 | NAYY 4x150 SE | 56 | 57 | 0.013228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3672-7_0_3_line_65 | NAYY 4x150 SE | 57 | 64 | 0.017416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3672-7_0_3_line_66 | NAYY 4x150 SE | 58 | 65 | 0.02728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3672-7_0_3_line_67 | NAYY 4x150 SE | 59 | 67 | 0.20835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3672-7_0_3_line_68 | NAYY 4x150 SE | 60 | 61 | 0.2088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3672-7_0_3_line_69 | NAYY 4x150 SE | 61 | 115 | 0.01338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3672-7_0_3_line_70 | NAYY 4x150 SE | 61 | 116 | 0.10731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3672-7_0_3_line_71 | NAYY 4x150 SE | 62 | 63 | 0.015817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3672-7_0_3_line_72 | NAYY 4x150 SE | 63 | 82 | 0.012231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3672-7_0_3_line_73 | NAYY 4x150 SE | 64 | 71 | 0.022253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3672-7_0_3_line_74 | NAYY 4x150 SE | 65 | 66 | 0.00088252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3672-7_0_3_line_75 | NAYY 4x150 SE | 66 | 69 | 0.01471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3672-7_0_3_line_76 | NAYY 4x150 SE | 67 | 68 | 0.011125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3672-7_0_3_line_77 | NAYY 4x150 SE | 69 | 70 | 0.014684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3672-7_0_3_line_78 | NAYY 4x150 SE | 70 | 74 | 0.011296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3672-7_0_3_line_79 | NAYY 4x150 SE | 71 | 72 | 0.00024617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3672-7_0_3_line_80 | NAYY 4x150 SE | 72 | 73 | 0.048483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3672-7_0_3_line_81 | NAYY 4x150 SE | 73 | 77 | 0.0027624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3672-7_0_3_line_82 | NAYY 4x150 SE | 73 | 78 | 0.01017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3672-7_0_3_line_83 | NAYY 4x150 SE | 74 | 75 | 0.0073143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3672-7_0_3_line_84 | NAYY 4x150 SE | 75 | 76 | 0.015577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_3672-7_0_3_line_85 | NAYY 4x150 SE | 76 | 83 | 0.020828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_3672-7_0_3_line_86 | NAYY 4x150 SE | 77 | 79 | 0.027003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_3672-7_0_3_line_87 | NAYY 4x150 SE | 78 | 80 | 0.027484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_3672-7_0_3_line_88 | NAYY 4x150 SE | 79 | 81 | 0.0045786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_3672-7_0_3_line_89 | NAYY 4x150 SE | 80 | 82 | 0.0092651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_3672-7_0_3_line_90 | NAYY 4x150 SE | 81 | 88 | 0.0031948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_3672-7_0_3_line_91 | NAYY 4x150 SE | 81 | 87 | 0.013733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_3672-7_0_3_line_92 | NAYY 4x150 SE | 83 | 84 | 0.0032168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_3672-7_0_3_line_93 | NAYY 4x150 SE | 84 | 85 | 0.014843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_3672-7_0_3_line_94 | NAYY 4x150 SE | 85 | 86 | 0.033334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
95 | LV_3672-7_0_3_line_95 | NAYY 4x150 SE | 85 | 87 | 0.0053133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_3672-7_0_3_line_96 | NAYY 4x150 SE | 86 | 90 | 0.020765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_3672-7_0_3_line_97 | NAYY 4x150 SE | 88 | 89 | 0.011272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_3672-7_0_3_line_98 | NAYY 4x150 SE | 89 | 91 | 0.0047594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_3672-7_0_3_line_99 | NAYY 4x150 SE | 91 | 92 | 0.0049716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_3672-7_0_3_line_100 | NAYY 4x150 SE | 92 | 93 | 0.0081545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_3672-7_0_3_line_101 | NAYY 4x150 SE | 93 | 94 | 0.0046392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_3672-7_0_3_line_102 | NAYY 4x150 SE | 94 | 95 | 0.015461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_3672-7_0_3_line_103 | NAYY 4x150 SE | 95 | 96 | 0.0058373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_3672-7_0_3_line_104 | NAYY 4x150 SE | 96 | 97 | 0.001423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_3672-7_0_3_line_105 | NAYY 4x150 SE | 97 | 98 | 0.010673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_3672-7_0_3_line_106 | NAYY 4x150 SE | 98 | 99 | 0.021695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_3672-7_0_3_line_107 | NAYY 4x150 SE | 99 | 100 | 0.0045692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_3672-7_0_3_line_108 | NAYY 4x150 SE | 100 | 101 | 0.01431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_3672-7_0_3_line_109 | NAYY 4x150 SE | 100 | 102 | 0.094342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_3672-7_0_3_line_110 | NAYY 4x150 SE | 101 | 103 | 0.016304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_3672-7_0_3_line_111 | NAYY 4x150 SE | 102 | 104 | 0.12123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_3672-7_0_3_line_112 | NAYY 4x150 SE | 102 | 105 | 0.010045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_3672-7_0_3_line_113 | NAYY 4x150 SE | 103 | 106 | 0.011252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_3672-7_0_3_line_114 | NAYY 4x150 SE | 104 | 107 | 0.018977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_3672-7_0_3_line_115 | NAYY 4x150 SE | 105 | 108 | 0.056281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_3672-7_0_3_line_116 | NAYY 4x150 SE | 106 | 109 | 0.024498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_3672-7_0_3_line_117 | NAYY 4x150 SE | 107 | 112 | 0.016736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_3672-7_0_3_line_118 | NAYY 4x150 SE | 108 | 110 | 0.03801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_3672-7_0_3_line_119 | NAYY 4x150 SE | 109 | 111 | 0.040139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_3672-7_0_3_line_120 | NAYY 4x150 SE | 112 | 113 | 0.012177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_3672-7_0_3_line_121 | NAYY 4x150 SE | 113 | 114 | 0.035713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_3672-7_0_3_line_122 | NAYY 4x150 SE | 115 | 117 | 0.099792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_3672-7_0_3_line_123 | NAYY 4x150 SE | 116 | 118 | 0.075425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_3672-7_0_3_line_124 | NAYY 4x150 SE | 117 | 119 | 0.023463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_3672-7_0_3_line_125 | NAYY 4x150 SE | 120 | 121 | 0.085752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_3672-7_0_3_line_126 | NAYY 4x150 SE | 121 | 122 | 0.42325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_3672-7_0_3_line_127 | NAYY 4x150 SE | 122 | 123 | 0.17691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_3672-7_0_3_line_128 | NAYY 4x150 SE | 122 | 124 | 0.10608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_3672-7_0_3_line_129 | NAYY 4x150 SE | 123 | 126 | 0.30313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_3672-7_0_3_line_130 | NAYY 4x150 SE | 124 | 125 | 0.15112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_3672-7_0_3_line_131 | NAYY 4x150 SE | 127 | 128 | 0.027537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_3672-7_0_3_line_132 | NAYY 4x150 SE | 127 | 129 | 0.042725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_3672-7_0_3_line_133 | NAYY 4x150 SE | 129 | 130 | 0.10532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_3672-7_0_3_line_134 | NAYY 4x150 SE | 130 | 131 | 0.019806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_3672-7_0_3_line_135 | NAYY 4x150 SE | 131 | 132 | 0.014957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_3672-7_0_3_line_136 | NAYY 4x150 SE | 132 | 133 | 0.016342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_3672-7_0_3_line_137 | NAYY 4x150 SE | 134 | 135 | 0.012313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_3672-7_0_3_line_138 | NAYY 4x150 SE | 136 | 137 | 0.0060313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_3672-7_0_3_line_139 | NAYY 4x150 SE | 137 | 138 | 0.025288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_3672-7_0_3_line_140 | NAYY 4x150 SE | 138 | 139 | 0.13701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_3672-7_0_3_line_141 | NAYY 4x150 SE | 139 | 142 | 0.057725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_3672-7_0_3_line_142 | NAYY 4x150 SE | 140 | 143 | 0.028858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_3672-7_0_3_line_143 | NAYY 4x150 SE | 141 | 144 | 0.00036013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_3672-7_0_3_line_144 | NAYY 4x150 SE | 142 | 145 | 0.0007918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_3672-7_0_3_line_145 | NAYY 4x150 SE | 144 | 147 | 0.021115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_3672-7_0_3_line_146 | NAYY 4x150 SE | 145 | 146 | 0.010478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3672-7_0_3_trafo_63 | 0.25 MVA 20/0.4 kV | 148 | 86 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2744830.0342 | 1182575.0527 | 2744830.356 | 1182580.8447 | 2744824.9406 | 1182593.4462 | 2744820.1594 | 1182603.5165 | 2744811.0358 | 1182616.8846 | 2744812.5407 | 1182630.7876 | 2744821.6904 | 1182645.7207 | 2744834.5624 | 1182664.9916 | 2744835.3238 | 1182678.5989
1 | 2744829.1765 | 1182694.385 | 2744835.6559 | 1182684.5337 | 2744835.3238 | 1182678.5989
2 | 2744829.1765 | 1182694.385 | 2744831.2935 | 1182697.5053 | 2744832.6858 | 1182702.5007
3 | 2744825.747 | 1182689.3092 | 2744829.1765 | 1182694.385
4 | 2744832.6858 | 1182702.5007 | 2744835.3845 | 1182712.1826 | 2744832.8865 | 1182717.7888
5 | 2744823.5575 | 1182738.7257 | 2744832.8865 | 1182717.7888
6 | 2744705.2646 | 1182875.1372 | 2744702.347 | 1182857.0968 | 2744702.4124 | 1182832.89 | 2744724.7442 | 1182805.574 | 2744808.8745 | 1182771.6787 | 2744823.5575 | 1182738.7257
7 | 2744665.5849 | 1182861.0459 | 2744671.3681 | 1182849.9543 | 2744674.5731 | 1182836.1762 | 2744676.9047 | 1182819.0299 | 2744680.0884 | 1182806.4522 | 2744682.4261 | 1182798.8581 | 2744688.9905 | 1182794.9578 | 2744695.2088 | 1182795.5862 | 2744700.3439 | 1182801.2036 | 2744700.3671 | 1182810.0446 | 2744696.9408 | 1182822.861 | 2744693.8337 | 1182832.5827 | 2744689.9554 | 1182844.1873 | 2744689.8477 | 1182858.763 | 2744692.5394 | 1182866.234 | 2744699.1175 | 1182871.8862 | 2744705.2646 | 1182875.1372
8 | 2744705.2646 | 1182875.1372 | 2744715.477 | 1182878.9646 | 2744724.0068 | 1182883.3469
9 | 2744665.5849 | 1182861.0459 | 2744660.1825 | 1182851.9415 | 2744664.1999 | 1182835.5253 | 2744661.8517 | 1182822.3692 | 2744660.8574 | 1182811.8605
10 | 2744665.5849 | 1182861.0459 | 2744661.3661 | 1182876.9457 | 2744654.1614 | 1182897.555 | 2744647.5973 | 1182911.252 | 2744643.2458 | 1182922.8452 | 2744643.1476 | 1182923.2551
11 | 2744727.2135 | 1182884.9944 | 2744724.0068 | 1182883.3469
12 | 2744724.3779 | 1182732.2174 | 2744728.0424 | 1182737.9994 | 2744736.6404 | 1182736.8839 | 2744749.7231 | 1182731.3176 | 2744754.5879 | 1182734.849 | 2744753.0456 | 1182743.3519 | 2744741.6393 | 1182750.6712 | 2744684.1232 | 1182775.0911 | 2744671.3353 | 1182784.2676 | 2744660.1782 | 1182804.6813 | 2744660.8574 | 1182811.8605
13 | 2744638.6942 | 1183022.1149 | 2744632.9741 | 1183010.9902 | 2744624.5953 | 1183000.5129 | 2744620.9819 | 1182991.3517 | 2744621.9303 | 1182981.8114 | 2744627.2437 | 1182970.2415 | 2744633.8192 | 1182956.0665 | 2744638.9809 | 1182940.6565 | 2744643.1476 | 1182923.2551
14 | 2744638.6942 | 1183022.1149 | 2744645.2651 | 1183032.4818
15 | 2744638.6942 | 1183022.1149 | 2744640.1183 | 1183032.4131
16 | 2745008.7062 | 1182961.8291 | 2744998.3868 | 1182950.4481 | 2744987.7056 | 1182938.5468 | 2744958.2149 | 1182899.9247 | 2744952.946 | 1182883.751 | 2744949.287 | 1182881.5385 | 2744943.386 | 1182884.2202
17 | 2745008.7062 | 1182961.8291 | 2745008.2333 | 1182933.0058
18 | 2745008.7062 | 1182961.8291 | 2745008.9711 | 1182968.0509
19 | 2745016.5164 | 1182851.0375 | 2745017.5518 | 1182853.3115 | 2745020.9108 | 1182863.8123 | 2745019.731 | 1182878.4622 | 2745016.5785 | 1182889.4059 | 2745010.2985 | 1182907.4239 | 2745008.2218 | 1182932.3048 | 2745008.2333 | 1182933.0058
20 | 2745080.6731 | 1183064.5532 | 2745073.1617 | 1183057.4101 | 2745056.7226 | 1183048.6051 | 2745045.6068 | 1183039.2063 | 2745027.6917 | 1183020.6913 | 2745019.6641 | 1183010.5667 | 2745012.3629 | 1182996.3119 | 2745009.4318 | 1182978.8715 | 2745008.9711 | 1182968.0509
21 | 2745016.5164 | 1182851.0375 | 2745008.4997 | 1182833.4321 | 2745007.404 | 1182819.3721 | 2745007.9847 | 1182804.5409 | 2745005.7523 | 1182788.2071 | 2745006.8095 | 1182776.7235 | 2745011.8426 | 1182764.1463 | 2745019.8887 | 1182749.2289 | 2745024.59 | 1182733.3188 | 2745027.4904 | 1182720.8012 | 2745033.9492 | 1182708.6588 | 2745045.4315 | 1182698.851 | 2745065.952 | 1182690.2629 | 2745083.4162 | 1182692.1093 | 2745088.0344 | 1182692.9707
22 | 2745080.6731 | 1183064.5532 | 2745090.2045 | 1183079.1289 | 2745105.9361 | 1183105.5321
23 | 2744935.0676 | 1183147.4526 | 2744937.0953 | 1183144.1545 | 2744938.3527 | 1183128.4946 | 2744943.101 | 1183122.6158 | 2744957.6888 | 1183118.9101 | 2744963.3024 | 1183113.5749 | 2744963.2741 | 1183113.1293
24 | 2744909.6109 | 1183313.3925 | 2744925.2136 | 1183313.4921 | 2744958.8917 | 1183295.7923 | 2744962.9081 | 1183283.5463 | 2744943.332 | 1183171.4606 | 2744935.0676 | 1183147.4526
25 | 2744929.6716 | 1183143.797 | 2744935.0676 | 1183147.4526
26 | 2744909.6109 | 1183313.3925 | 2744888.872 | 1183328.8925 | 2744880.1379 | 1183343.2484 | 2744876.9845 | 1183364.6672 | 2744875.5263 | 1183380.4224 | 2744882.7008 | 1183407.4842 | 2744890.3305 | 1183427.0955 | 2744898.0464 | 1183434.9328
27 | 2744816.9653 | 1183141.5598 | 2744829.2492 | 1183158.5703 | 2744841.8233 | 1183173.6863 | 2744858.4798 | 1183188.6564 | 2744869.8016 | 1183195.858 | 2744885.4151 | 1183204.3645 | 2744896.3097 | 1183219.4288 | 2744910.6552 | 1183240.5593 | 2744926.1932 | 1183261.9633 | 2744933.5573 | 1183274.5626 | 2744935.4675 | 1183284.6391 | 2744933.3491 | 1183292.9501 | 2744926.2406 | 1183299.4612 | 2744909.6109 | 1183313.3925
28 | 2744929.6716 | 1183143.797 | 2744929.4525 | 1183138.3317 | 2744918.9117 | 1183113.5937
29 | 2744929.6716 | 1183143.797 | 2744925.0716 | 1183143.8636 | 2744922.9425 | 1183143.9635
30 | 2744945.9295 | 1183454.8961 | 2744940.8595 | 1183448.1453 | 2744933.7571 | 1183444.6262 | 2744928.0608 | 1183442.3422 | 2744916.3605 | 1183440.3911 | 2744905.63 | 1183438.4523 | 2744898.0464 | 1183434.9328 | 2744898.0464 | 1183434.9328
31 | 2744816.9653 | 1183141.5598 | 2744814.6224 | 1183146.8408 | 2744824.1105 | 1183164.1728 | 2744831.8982 | 1183207.9072 | 2744842.3406 | 1183229.677 | 2744842.3406 | 1183229.677
32 | 2744816.9653 | 1183141.5598 | 2744808.2234 | 1183126.5365 | 2744795.6631 | 1183102.6569
33 | 2744876.9565 | 1183102.666 | 2744899.6802 | 1183140.4247 | 2744907.72 | 1183144.678 | 2744922.9425 | 1183143.9635
34 | 2745113.0648 | 1182699.633 | 2745097.0516 | 1182694.6525 | 2745088.0344 | 1182692.9707
35 | 2745122.8362 | 1183144.4047 | 2745121.1449 | 1183135.0785 | 2745117.774 | 1183125.4002 | 2745105.9361 | 1183105.5321
36 | 2745113.0648 | 1182699.633 | 2745135.0832 | 1182667.0622 | 2745140.3761 | 1182658.5947 | 2745142.1961 | 1182655.6808 | 2745161.3731 | 1182628.7792 | 2745177.249 | 1182614.2186 | 2745192.4243 | 1182605.557 | 2745211.6774 | 1182600.1079
37 | 2745113.0648 | 1182699.633 | 2745096.6292 | 1182733.5291 | 2745081.374 | 1182764.4291 | 2745076.7978 | 1182778.6408 | 2745076.0421 | 1182784.2937
38 | 2745077.4598 | 1182797.7792 | 2745076.5054 | 1182789.7649 | 2745076.0421 | 1182784.2937
39 | 2745122.8362 | 1183144.4047 | 2745130.0579 | 1183144.9022
40 | 2745122.8362 | 1183144.4047 | 2745121.739 | 1183153.1185 | 2745117.9521 | 1183162.8124 | 2745110.9694 | 1183173.2628 | 2745104.159 | 1183179.4362 | 2745091.0609 | 1183189.1269 | 2745089.7413 | 1183190.7839
41 | 2745130.0579 | 1183144.9022 | 2745129.7734 | 1183134.5759
42 | 2745130.0579 | 1183144.9022 | 2745127.2467 | 1183155.943 | 2745122.7985 | 1183169.6018 | 2745120.9243 | 1183178.5414 | 2745122.5857 | 1183189.1013 | 2745125.7427 | 1183197.5178 | 2745126.4204 | 1183198.8655
43 | 2745085.0557 | 1183199.59 | 2745085.0557 | 1183199.59 | 2745087.4291 | 1183193.6871 | 2745089.7413 | 1183190.7839
44 | 2745144.4894 | 1182876.8531 | 2745144.4587 | 1182874.0666 | 2745140.5533 | 1182865.3206 | 2745121.5887 | 1182846.6019 | 2745087.9264 | 1182817.4858 | 2745084.5825 | 1182812.9902 | 2745081.5918 | 1182808.1027 | 2745077.5718 | 1182798.7201 | 2745077.4598 | 1182797.7792
45 | 2745138.843 | 1182918.5553 | 2745143.438 | 1182893.4908 | 2745144.547 | 1182882.0863 | 2745144.4894 | 1182876.8531
46 | 2745138.843 | 1182918.5553 | 2745149.3235 | 1182919.1873
47 | 2745138.843 | 1182918.5553 | 2745138.1713 | 1182926.1006 | 2745138.7434 | 1182934.6436 | 2745139.4636 | 1182939.5378
48 | 2745149.3235 | 1182919.1873 | 2745158.7989 | 1182896.0359
49 | 2745149.3235 | 1182919.1873 | 2745149.5855 | 1182930.1247 | 2745152.8256 | 1182942.3686 | 2745159.5699 | 1182948.7036 | 2745172.3276 | 1182954.9448
50 | 2744786.9871 | 1184144.73 | 2744789.0118 | 1184137.1172 | 2744796.3753 | 1184124.7519 | 2744803.7002 | 1184120.7197
51 | 2744823.6616 | 1184113.4577 | 2744816.5272 | 1184116.977 | 2744803.8447 | 1184120.6402 | 2744803.7002 | 1184120.7197
52 | 2744788.7905 | 1184151.3233 | 2744786.9871 | 1184144.73 | 2744786.9871 | 1184144.73
53 | 2744823.6616 | 1184113.4577 | 2744829.2402 | 1184113.0524
54 | 2744823.6616 | 1184113.4577 | 2744828.9562 | 1184110.8502 | 2744836.4848 | 1184104.2936 | 2744838.6959 | 1184100.8877
55 | 2744788.7905 | 1184151.3233 | 2744783.372 | 1184158.1089 | 2744761.6347 | 1184176.071
56 | 2744829.2402 | 1184113.0524 | 2744860.3473 | 1184110.7923
57 | 2744838.6959 | 1184100.8877 | 2744845.0921 | 1184091.0354 | 2744853.0963 | 1184077.7627 | 2744854.8082 | 1184070.4537 | 2744853.1092 | 1184064.2855 | 2744846.1747 | 1184059.2249 | 2744846.1747 | 1184059.2249
58 | 2744945.9295 | 1183454.8961 | 2745030.4307 | 1183818.1429
59 | 2744945.9295 | 1183454.8961 | 2744946.8902 | 1183456.1753 | 2744953.1421 | 1183465.1671 | 2744957.8841 | 1183467.4281 | 2744963.1686 | 1183466.8443 | 2744968.0302 | 1183463.8484 | 2744969.8251 | 1183459.1213 | 2744970.1483 | 1183455.5485 | 2744966.705 | 1183449.4937 | 2744956.665 | 1183433.2267 | 2744953.3902 | 1183418.3132 | 2744952.326 | 1183386.2284 | 2744953.1737 | 1183374.8731 | 2744955.8892 | 1183367.4551 | 2744960.94 | 1183360.7496 | 2744967.7951 | 1183354.9218 | 2744990.5732 | 1183342.2738 | 2745026.7315 | 1183330.6615 | 2745027.6481 | 1183330.6244
60 | 2745030.4307 | 1183818.1429 | 2745033.4821 | 1183822.3979 | 2745035.1385 | 1183825.9075 | 2745035.0222 | 1183830.7086 | 2745034.6944 | 1183835.7269 | 2745032.0855 | 1183841.9021 | 2745030.42 | 1183844.481
61 | 2745085.1428 | 1183335.6681 | 2745064.7617 | 1183331.338 | 2745045.8079 | 1183329.8892 | 2745027.6481 | 1183330.6244
62 | 2744863.5976 | 1184110.5562 | 2744860.3473 | 1184110.7923
63 | 2744835.6775 | 1184056.1787 | 2744846.1747 | 1184059.2249
64 | 2744898.5488 | 1184134.472 | 2744887.8435 | 1184137.2171 | 2744885.6717 | 1184137.3553
65 | 2744898.5488 | 1184134.472 | 2744902.5449 | 1184133.4473 | 2744915.1309 | 1184129.1758
66 | 2744863.5976 | 1184110.5562 | 2744880.6139 | 1184109.3199 | 2744890.325 | 1184106.1376
67 | 2744835.6775 | 1184056.1787 | 2744825.4396 | 1184053.2078 | 2744816.606 | 1184050.2475 | 2744806.0588 | 1184041.7191 | 2744797.4694 | 1184028.6566 | 2744794.6006 | 1184020.3251 | 2744795.7314 | 1184011.7789 | 2744801.3293 | 1183996.0014 | 2744803.1003 | 1183986.2475 | 2744801.3623 | 1183969.3697 | 2744799.9149 | 1183953.1106 | 2744802.0208 | 1183942.1415 | 2744808.8477 | 1183926.3938 | 2744811.9662 | 1183911.7686 | 2744811.9124 | 1183901.3589 | 2744814.2643 | 1183892.8533 | 2744819.9683 | 1183885.6409 | 2744821.9412 | 1183880.1731 | 2744820.5032 | 1183876.1574
68 | 2744768.9225 | 1183284.3711 | 2744763.7259 | 1183284.0213 | 2744746.812 | 1183288.5498 | 2744736.3212 | 1183298.1708 | 2744716.4027 | 1183331.8947 | 2744694.5412 | 1183365.7496 | 2744665.2396 | 1183399.9474 | 2744650.5969 | 1183444.9738
69 | 2744782.2727 | 1183285.2698 | 2744768.9225 | 1183284.3711
70 | 2744768.9225 | 1183284.3711 | 2744675.6339 | 1183231.3391
71 | 2744950.861 | 1184144.1913 | 2744942.2883 | 1184157.4839
72 | 2744957.49 | 1184133.9126 | 2744950.861 | 1184144.1913
73 | 2744935.3706 | 1184120.0076 | 2744930.419 | 1184122.8017 | 2744916.583 | 1184128.6829 | 2744915.1309 | 1184129.1758
74 | 2744891.1636 | 1184105.8628 | 2744890.325 | 1184106.1376
75 | 2744891.1636 | 1184105.8628 | 2744895.6873 | 1184104.3804 | 2744904.0047 | 1184098.9207
76 | 2744820.5032 | 1183876.1574 | 2744820.5032 | 1183876.1574 | 2744815.3636 | 1183872.975 | 2744810.709 | 1183875.0086
77 | 2744904.0047 | 1184098.9207 | 2744913.3816 | 1184092.7655 | 2744915.8819 | 1184090.3628
78 | 2744924.5774 | 1184083.2309 | 2744920.6847 | 1184085.7476 | 2744915.8819 | 1184090.3628
79 | 2744935.585 | 1184119.8866 | 2744935.3706 | 1184120.0076
80 | 2744973.7048 | 1184090.1002 | 2744951.6591 | 1184108.8931 | 2744941.662 | 1184116.4574 | 2744935.585 | 1184119.8866
81 | 2744973.7048 | 1184090.1002 | 2744975.108 | 1184087.7207
82 | 2744973.7048 | 1184090.1002 | 2744970.5535 | 1184099.7694
83 | 2744924.5774 | 1184083.2309 | 2744930.7198 | 1184079.2597
84 | 2744930.7198 | 1184079.2597 | 2744943.8008 | 1184070.8025
85 | 2744943.8008 | 1184070.8025 | 2744946.9792 | 1184068.7477 | 2744954.851 | 1184058.1184 | 2744957.9027 | 1184055.827
86 | 2744975.108 | 1184087.7207 | 2744986.8938 | 1184067.7346 | 2744989.5744 | 1184065.0407
87 | 2744970.5535 | 1184099.7694 | 2744962.0371 | 1184125.9007
88 | 2744992.8039 | 1184061.7951 | 2744989.5744 | 1184065.0407
89 | 2744962.0371 | 1184125.9007 | 2744961.4037 | 1184127.8441 | 2744957.49 | 1184133.9126
90 | 2744992.8039 | 1184061.7951 | 2744995.124 | 1184059.5987
91 | 2744992.8039 | 1184061.7951 | 2744980.1926 | 1184056.3582
92 | 2744957.9027 | 1184055.827 | 2744960.4751 | 1184053.8955
93 | 2744975.3135 | 1184054.2547 | 2744960.4751 | 1184053.8955
94 | 2744975.3135 | 1184054.2547 | 2744974.1246 | 1184048.1544 | 2744979.2198 | 1184034.2331 | 2744989.6372 | 1184027.7036
95 | 2744975.3135 | 1184054.2547 | 2744980.1926 | 1184056.3582
96 | 2745003.1596 | 1184012.6172 | 2744996.4207 | 1184023.4517 | 2744989.6372 | 1184027.7036
97 | 2744995.124 | 1184059.5987 | 2745003.3098 | 1184051.8496
98 | 2745003.3098 | 1184051.8496 | 2745006.7662 | 1184048.5777
99 | 2745010.529 | 1184045.3337 | 2745008.1634 | 1184047.255 | 2745006.7662 | 1184048.5777
100 | 2745010.529 | 1184045.3337 | 2745016.8588 | 1184040.1926
101 | 2745016.8588 | 1184040.1926 | 2745020.4599 | 1184037.2678
102 | 2745020.4599 | 1184037.2678 | 2745023.2929 | 1184034.9668 | 2745030.1439 | 1184026.7593 | 2745030.4864 | 1184025.6927
103 | 2745030.4864 | 1184025.6927 | 2745032.2712 | 1184020.135
104 | 2745032.7062 | 1184018.7801 | 2745032.2712 | 1184020.135
105 | 2745032.7062 | 1184018.7801 | 2745034.1089 | 1184014.412 | 2745035.4981 | 1184008.4872
106 | 2745035.4981 | 1184008.4872 | 2745037.2433 | 1184001.0438 | 2745037.5836 | 1183992.3561 | 2745036.3373 | 1183987.1473
107 | 2745035.2741 | 1183982.7036 | 2745036.3373 | 1183987.1473
108 | 2745035.2741 | 1183982.7036 | 2745029.3131 | 1183969.6944
109 | 2745050.1217 | 1183935.714 | 2745053.9369 | 1183954.7773 | 2745040.3286 | 1183943.9837 | 2745047.1581 | 1183961.2628 | 2745037.9109 | 1183961.1834 | 2745046.4184 | 1183975.0894 | 2745035.2741 | 1183982.7036
110 | 2745022.5214 | 1183954.8726 | 2745029.3131 | 1183969.6944
111 | 2745050.1217 | 1183935.714 | 2745072.3272 | 1183965.5311 | 2745085.3502 | 1183977.4671 | 2745089.0137 | 1183983.5606 | 2745091.4166 | 1183991.2472 | 2745092.8457 | 1184000.0333 | 2745095.8753 | 1184001.3967 | 2745099.2209 | 1184001.0663 | 2745103.8422 | 1183993.1607 | 2745101.7957 | 1183969.1919 | 2745101.9126 | 1183966.7653
112 | 2745050.1217 | 1183935.714 | 2745043.5951 | 1183928.0776
113 | 2745022.5214 | 1183954.8726 | 2745017.0905 | 1183957.421 | 2745012.4372 | 1183954.9842
114 | 2745102.8256 | 1183947.8107 | 2745101.9126 | 1183966.7653
115 | 2745018.8904 | 1183878.5544 | 2745021.5288 | 1183888.9511 | 2745028.1518 | 1183907.1927 | 2745033.0493 | 1183916.263 | 2745038.3497 | 1183921.9402 | 2745043.5951 | 1183928.0776
116 | 2745012.4372 | 1183954.9842 | 2745005.8365 | 1183939.9235 | 2745004.1112 | 1183932.0564
117 | 2745102.8256 | 1183947.8107 | 2745097.6108 | 1183946.7948 | 2745094.7098 | 1183943.2773 | 2745094.534 | 1183936.4161
118 | 2745018.8904 | 1183878.5544 | 2745017.6871 | 1183873.8126 | 2745016.9715 | 1183869.6141 | 2745017.3708 | 1183865.7429 | 2745020.2699 | 1183860.1975 | 2745030.42 | 1183844.481
119 | 2745004.1112 | 1183932.0564 | 2744995.5132 | 1183892.8493
120 | 2745094.534 | 1183936.4161 | 2745094.2222 | 1183924.2431
121 | 2745097.2642 | 1183888.9176 | 2745097.4662 | 1183901.3881 | 2745094.0268 | 1183916.617 | 2745094.2222 | 1183924.2431
122 | 2744842.1786 | 1183253.139 | 2744842.13 | 1183260.1742 | 2744846.7998 | 1183279.3246 | 2744844.1014 | 1183288.2555 | 2744835.3424 | 1183292.2693 | 2744820.4603 | 1183293.3216 | 2744792.3385 | 1183285.9474 | 2744782.2727 | 1183285.2698
123 | 2744675.6339 | 1183231.3391 | 2744672.8896 | 1183223.346 | 2744668.3221 | 1183214.1617 | 2744660.571 | 1183207.7584 | 2744652.7832 | 1183202.5551 | 2744644.6142 | 1183193.5285 | 2744639.1043 | 1183183.8322 | 2744635.0447 | 1183173.2258 | 2744634.6844 | 1183170.6375
124 | 2744842.3406 | 1183229.677 | 2744842.1786 | 1183253.139
125 | 2744112.5462 | 1183360.453 | 2744149.279 | 1183334.2631 | 2744153.9323 | 1183324.6784 | 2744154.3166 | 1183301.4135 | 2744156.3117 | 1183295.0004
126 | 2744438.5099 | 1182979.5534 | 2744156.3117 | 1183295.0004
127 | 2744420.8564 | 1182873.7655 | 2744438.6476 | 1182851.2651 | 2744442.5664 | 1182847.779 | 2744447.3723 | 1182847.4167 | 2744448.9108 | 1182851.7239 | 2744446.0362 | 1182862.908 | 2744430.6369 | 1182895.5075 | 2744427.2747 | 1182905.6902 | 2744426.4308 | 1182920.7263 | 2744427.811 | 1182933.1807 | 2744430.2902 | 1182949.4757 | 2744433.5175 | 1182964.8435 | 2744438.5099 | 1182979.5534
128 | 2744438.5099 | 1182979.5534 | 2744445.0617 | 1182977.7432 | 2744447.8202 | 1182978.021 | 2744460.211 | 1182976.4072 | 2744480.9776 | 1182971.4705 | 2744496.3223 | 1182967.7374 | 2744507.8635 | 1182962.7116 | 2744518.5659 | 1182957.3097 | 2744527.2732 | 1182958.2983 | 2744531.3795 | 1182952.7373 | 2744536.9361 | 1182949.1239
129 | 2744420.8564 | 1182873.7655 | 2744358.8841 | 1182577.0352
130 | 2744640.1183 | 1183032.4131 | 2744626.4625 | 1183029.1587 | 2744602.7313 | 1183021.7914 | 2744569.7453 | 1183009.5414 | 2744558.996 | 1183005.1786 | 2744556.8006 | 1182998.9763 | 2744557.3262 | 1182989.2256 | 2744557.7329 | 1182975.2241 | 2744553.5947 | 1182964.3823 | 2744549.3011 | 1182957.1285 | 2744541.0977 | 1182950.1362 | 2744536.9361 | 1182949.1239
131 | 2744660.0185 | 1183055.7565 | 2744645.2651 | 1183032.4818
132 | 2744645.2651 | 1183032.4818 | 2744662.5985 | 1183040.3397 | 2744683.7389 | 1183051.0381
133 | 2744772.1399 | 1183057.2871 | 2744759.0349 | 1183070.1253 | 2744738.5922 | 1183072.7226 | 2744713.6857 | 1183077.9698 | 2744700.0811 | 1183060.9055 | 2744684.1737 | 1183051.2582 | 2744683.7389 | 1183051.0381
134 | 2744772.1399 | 1183057.2871 | 2744776.8434 | 1183066.5303 | 2744781.1951 | 1183074.9022
135 | 2744781.1951 | 1183074.9022 | 2744788.0936 | 1183088.1734
136 | 2744795.6631 | 1183102.6569 | 2744792.1862 | 1183096.0469 | 2744788.0936 | 1183088.1734
137 | 2744870.6077 | 1183092.1165 | 2744876.9565 | 1183102.666
138 | 2745085.0557 | 1183199.59 | 2745084.8146 | 1183205.6165
139 | 2745084.8146 | 1183205.6165 | 2745084.5908 | 1183211.2103 | 2745091.1561 | 1183223.0343 | 2745094.2572 | 1183228.363
140 | 2745085.1428 | 1183335.6681 | 2745100.9911 | 1183334.7733 | 2745107.3876 | 1183331.8035 | 2745113.6762 | 1183327.2966 | 2745116.9775 | 1183322.8174 | 2745120.1598 | 1183316.6339 | 2745121.7414 | 1183309.3664 | 2745121.6511 | 1183301.1131 | 2745120.671 | 1183293.9614 | 2745106.1707 | 1183252.1434 | 2745101.3565 | 1183240.562 | 2745094.2572 | 1183228.363
141 | 2745085.1428 | 1183335.6681 | 2745079.1855 | 1183343.8416 | 2745072.1651 | 1183352.701 | 2745061.1169 | 1183367.0229 | 2745054.8167 | 1183379.5805 | 2745053.8028 | 1183383.6255
142 | 2745132.9688 | 1183108.9438 | 2745126.263 | 1183115.8425 | 2745126.2081 | 1183122.2019 | 2745129.7734 | 1183134.5759
143 | 2745126.4204 | 1183198.8655 | 2745126.5822 | 1183199.1872
144 | 2745053.8028 | 1183383.6255 | 2745053.6102 | 1183384.3935
145 | 2745136.0688 | 1183218.051 | 2745126.5822 | 1183199.1872
146 | 2745051.0626 | 1183394.5572 | 2745053.6102 | 1183384.3935

## bus_geodata
| x | y | coords
0 | 2744830.0342 | 1182575.0527
1 | 2744835.3238 | 1182678.5989
2 | 2744829.1765 | 1182694.385
3 | 2744832.6858 | 1182702.5007
4 | 2744825.747 | 1182689.3092
5 | 2744832.8865 | 1182717.7888
6 | 2744823.5575 | 1182738.7257
7 | 2744705.2646 | 1182875.1372
8 | 2744665.5849 | 1182861.0459
9 | 2744724.0068 | 1182883.3469
10 | 2744660.8574 | 1182811.8605
11 | 2744643.1476 | 1182923.2551
12 | 2744727.2135 | 1182884.9944
13 | 2744724.3779 | 1182732.2174
14 | 2744638.6942 | 1183022.1149
15 | 2744943.386 | 1182884.2202
16 | 2745008.7062 | 1182961.8291
17 | 2745008.2333 | 1182933.0058
18 | 2745008.9711 | 1182968.0509
19 | 2745016.5164 | 1182851.0375
20 | 2745080.6731 | 1183064.5532
21 | 2744963.2741 | 1183113.1293
22 | 2744935.0676 | 1183147.4526
23 | 2744909.6109 | 1183313.3925
24 | 2744929.6716 | 1183143.797
25 | 2744898.0464 | 1183434.9328
26 | 2744816.9653 | 1183141.5598
27 | 2744918.9117 | 1183113.5937
28 | 2744922.9425 | 1183143.9635
29 | 2745088.0344 | 1182692.9707
30 | 2745105.9361 | 1183105.5321
31 | 2745113.0648 | 1182699.633
32 | 2745211.6774 | 1182600.1079
33 | 2745076.0421 | 1182784.2937
34 | 2745122.8362 | 1183144.4047
35 | 2745130.0579 | 1183144.9022
36 | 2745089.7413 | 1183190.7839
37 | 2745077.4598 | 1182797.7792
38 | 2745144.4894 | 1182876.8531
39 | 2745138.843 | 1182918.5553
40 | 2745149.3235 | 1182919.1873
41 | 2745139.4636 | 1182939.5378
42 | 2745158.7989 | 1182896.0359
43 | 2745172.3276 | 1182954.9448
44 | 2744803.7002 | 1184120.7197
45 | 2744786.9871 | 1184144.73
46 | 2744823.6616 | 1184113.4577
47 | 2744788.7905 | 1184151.3233
48 | 2744829.2402 | 1184113.0524
49 | 2744838.6959 | 1184100.8877
50 | 2744945.9295 | 1183454.8961
51 | 2745030.4308 | 1183818.1429
52 | 2745027.6481 | 1183330.6244
53 | 2744761.6347 | 1184176.071
54 | 2744860.3473 | 1184110.7923
55 | 2744846.1747 | 1184059.2249
56 | 2744885.6717 | 1184137.3553
57 | 2744898.5488 | 1184134.472
58 | 2744863.5976 | 1184110.5562
59 | 2744835.6775 | 1184056.1787
60 | 2744650.5969 | 1183444.9738
61 | 2744768.9225 | 1183284.3711
62 | 2744942.2883 | 1184157.4839
63 | 2744950.861 | 1184144.1913
64 | 2744915.1309 | 1184129.1758
65 | 2744890.325 | 1184106.1376
66 | 2744891.1636 | 1184105.8628
67 | 2744820.5032 | 1183876.1574
68 | 2744810.709 | 1183875.0087
69 | 2744904.0047 | 1184098.9207
70 | 2744915.8819 | 1184090.3628
71 | 2744935.3706 | 1184120.0076
72 | 2744935.585 | 1184119.8866
73 | 2744973.7048 | 1184090.1002
74 | 2744924.5774 | 1184083.2309
75 | 2744930.7198 | 1184079.2597
76 | 2744943.8008 | 1184070.8025
77 | 2744975.108 | 1184087.7207
78 | 2744970.5535 | 1184099.7694
79 | 2744989.5744 | 1184065.0407
80 | 2744962.0371 | 1184125.9007
81 | 2744992.8039 | 1184061.7951
82 | 2744957.49 | 1184133.9126
83 | 2744957.9027 | 1184055.827
84 | 2744960.4751 | 1184053.8955
85 | 2744975.3135 | 1184054.2547
86 | 2744989.6372 | 1184027.7036
87 | 2744980.1926 | 1184056.3582
88 | 2744995.124 | 1184059.5987
89 | 2745003.3098 | 1184051.8496
90 | 2745003.1596 | 1184012.6172
91 | 2745006.7662 | 1184048.5777
92 | 2745010.529 | 1184045.3337
93 | 2745016.8588 | 1184040.1926
94 | 2745020.4599 | 1184037.2678
95 | 2745030.4864 | 1184025.6927
96 | 2745032.2712 | 1184020.135
97 | 2745032.7062 | 1184018.7801
98 | 2745035.4981 | 1184008.4872
99 | 2745036.3373 | 1183987.1473
100 | 2745035.2741 | 1183982.7036
101 | 2745029.3131 | 1183969.6944
102 | 2745050.1217 | 1183935.714
103 | 2745022.5214 | 1183954.8726
104 | 2745101.9126 | 1183966.7653
105 | 2745043.5951 | 1183928.0776
106 | 2745012.4372 | 1183954.9842
107 | 2745102.8256 | 1183947.8107
108 | 2745018.8904 | 1183878.5544
109 | 2745004.1112 | 1183932.0564
110 | 2745030.42 | 1183844.481
111 | 2744995.5132 | 1183892.8493
112 | 2745094.534 | 1183936.4161
113 | 2745094.2222 | 1183924.2431
114 | 2745097.2642 | 1183888.9176
115 | 2744782.2727 | 1183285.2698
116 | 2744675.6339 | 1183231.3391
117 | 2744842.1786 | 1183253.139
118 | 2744634.6844 | 1183170.6375
119 | 2744842.3406 | 1183229.677
120 | 2744112.5462 | 1183360.453
121 | 2744156.3117 | 1183295.0004
122 | 2744438.5099 | 1182979.5534
123 | 2744420.8564 | 1182873.7655
124 | 2744536.9361 | 1182949.1239
125 | 2744640.1183 | 1183032.4131
126 | 2744358.8841 | 1182577.0352
127 | 2744645.2651 | 1183032.4818
128 | 2744660.0185 | 1183055.7565
129 | 2744683.7389 | 1183051.0381
130 | 2744772.1399 | 1183057.2871
131 | 2744781.1951 | 1183074.9022
132 | 2744788.0936 | 1183088.1734
133 | 2744795.6631 | 1183102.6569
134 | 2744876.9565 | 1183102.666
135 | 2744870.6077 | 1183092.1165
136 | 2745085.0557 | 1183199.59
137 | 2745084.8146 | 1183205.6165
138 | 2745094.2572 | 1183228.363
139 | 2745085.1428 | 1183335.6681
140 | 2745129.7734 | 1183134.5759
141 | 2745126.4204 | 1183198.8655
142 | 2745053.8028 | 1183383.6255
143 | 2745132.9688 | 1183108.9438
144 | 2745126.5822 | 1183199.1872
145 | 2745053.6102 | 1183384.3935
146 | 2745051.0626 | 1183394.5572
147 | 2745136.0688 | 1183218.051
148 | 2744989.6372 | 1184027.7036

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1