## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3732-23_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3732-23_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3732-23_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3732-23_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3732-23_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_3732-23_0_3_node_111 | 0.4 | n |  | TRUE
6 | bus_LV_3732-23_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3732-23_0_3_node_73 | 0.4 | n |  | TRUE
8 | bus_LV_3732-23_0_3_node_93 | 0.4 | n |  | TRUE
9 | bus_LV_3732-23_0_3_node_92 | 0.4 | n |  | TRUE
10 | bus_LV_3732-23_0_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_3732-23_0_3_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_3732-23_0_3_node_75 | 0.4 | n |  | TRUE
13 | bus_LV_3732-23_0_3_node_74 | 0.4 | n |  | TRUE
14 | bus_LV_3732-23_0_3_node_77 | 0.4 | n |  | TRUE
15 | bus_LV_3732-23_0_3_node_112 | 0.4 | n |  | TRUE
16 | bus_LV_3732-23_0_3_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_3732-23_0_3_node_113 | 0.4 | n |  | TRUE
18 | bus_LV_3732-23_0_3_node_87 | 0.4 | n |  | TRUE
19 | bus_LV_3732-23_0_3_node_88 | 0.4 | n |  | TRUE
20 | bus_LV_3732-23_0_3_node_89 | 0.4 | n |  | TRUE
21 | bus_LV_3732-23_0_3_node_90 | 0.4 | n |  | TRUE
22 | bus_LV_3732-23_0_3_node_97 | 0.4 | n |  | TRUE
23 | bus_MV_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3732-23_0_3_load_0 | 0 | 0.012156 | 0.0030465 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3732-23_0_3_load_111 | 5 | 0.0090039 | 0.0022566 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3732-23_0_3_load_73 | 7 | 0.00052721 | 0.00013213 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3732-23_0_3_load_93 | 8 | 0.00056318 | 0.00014114 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3732-23_0_3_load_92 | 9 | 0.0030744 | 0.00077053 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3732-23_0_3_load_75 | 12 | 0.0004698 | 0.00011774 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3732-23_0_3_load_74 | 13 | 0.00098796 | 0.00024761 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3732-23_0_3_load_77 | 14 | 0.00062564 | 0.0001568 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3732-23_0_3_load_112 | 15 | 0.00076023 | 0.00019053 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3732-23_0_3_load_113 | 17 | 0.0045022 | 0.0011284 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3732-23_0_3_load_89 | 20 | 0.001588 | 0.00039799 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3732-23_0_3_load_90 | 21 | 0.003226 | 0.00080851 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3732-23_0_3_load_97 | 22 | 0.00089122 | 0.00022336 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3732-23_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.32832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3732-23_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.69714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_3732-23_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.70618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3732-23_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.14383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_3732-23_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0068541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3732-23_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.72217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3732-23_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.10246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3732-23_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.031576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3732-23_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.17493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3732-23_0_3_line_9 | NAYY 4x150 SE | 7 | 11 | 0.075908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3732-23_0_3_line_10 | NAYY 4x150 SE | 8 | 22 | 0.0054133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3732-23_0_3_line_11 | NAYY 4x150 SE | 9 | 18 | 0.018125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3732-23_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.030498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3732-23_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.45096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3732-23_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.16563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3732-23_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.037515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3732-23_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.029163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3732-23_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.062061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3732-23_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.003016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3732-23_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.033247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3732-23_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.019992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3732-23_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.047253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3732-23_0_3_trafo_0 | 0.25 MVA 20/0.4 kV | 23 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61 | x62 | y62 | x63 | y63 | x64 | y64 | x65 | y65 | x66 | y66 | x67 | y67 | x68 | y68 | x69 | y69 | x70 | y70 | x71 | y71 | x72 | y72 | x73 | y73 | x74 | y74 | x75 | y75 | x76 | y76 | x77 | y77 | x78 | y78 | x79 | y79
0 | 2737726.8126 | 1192199.8482 | 2737726.0084 | 1192180.4588 | 2737725.1183 | 1192163.803 | 2737723.5213 | 1192134.1318 | 2737727.4381 | 1192096.5257 | 2737736.0059 | 1192080.8327 | 2737737.4229 | 1192067.655 | 2737740.2353 | 1192058.1344 | 2737745.987 | 1192051.7952 | 2737756.3518 | 1192048.1531 | 2737758.6163 | 1192039.5762 | 2737764.4207 | 1192016.3805 | 2737761.7188 | 1192005.5431 | 2737756.6711 | 1191994.5627 | 2737755.2945 | 1191986.7804 | 2737758.7237 | 1191975.317 | 2737760.6873 | 1191946.3617 | 2737766.0368 | 1191931.9957 | 2737771.1609 | 1191920.1265 | 2737785.2415 | 1191898.5559 | 2737786.5803 | 1191893.5743
1 | 2738227.4242 | 1191814.7195 | 2738212.2069 | 1191820.3836 | 2738202.7012 | 1191831.3728 | 2738201.2165 | 1191837.5322 | 2738204.0658 | 1191846.583 | 2738201.8382 | 1191855.5163 | 2738192.3002 | 1191870.2188 | 2738162.2862 | 1191880.5229 | 2738142.0946 | 1191884.282 | 2738131.1115 | 1191881.6486 | 2738118.3137 | 1191877.6723 | 2738104.5478 | 1191864.422 | 2738083.4784 | 1191851.6925 | 2738060.6777 | 1191837.9668 | 2738035.1595 | 1191825.3238 | 2738013.207 | 1191810.8617 | 2737999.8812 | 1191808.9307 | 2737969.3346 | 1191802.3212 | 2737935.8104 | 1191790.8839 | 2737902.5011 | 1191774.7481 | 2737863.0547 | 1191757.826 | 2737835.1368 | 1191748.9982 | 2737824.0697 | 1191749.3325 | 2737811.1644 | 1191755.2956 | 2737794.3764 | 1191759.9572 | 2737778.9687 | 1191772.2455 | 2737775.2175 | 1191777.1519 | 2737773.6506 | 1191782.2643 | 2737779.2452 | 1191788.0532 | 2737784.5152 | 1191791.3771 | 2737792.158 | 1191797.6469 | 2737803.2246 | 1191803.9511 | 2737816.4143 | 1191805.5004 | 2737820.727 | 1191810.6483 | 2737800.1709 | 1191827.5771 | 2737780.9998 | 1191845.3053 | 2737782.8815 | 1191864.9307 | 2737786.8073 | 1191884.2252 | 2737786.9433 | 1191892.2235 | 2737786.5803 | 1191893.5743
2 | 2737343.1933 | 1192325.8088 | 2737352.0388 | 1192314.236 | 2737357.7801 | 1192299.6897 | 2737366.5685 | 1192295.2546 | 2737379.6964 | 1192285.5038 | 2737391.1136 | 1192270.2206 | 2737406.5088 | 1192258.387 | 2737410.2469 | 1192238.0902 | 2737412.3654 | 1192216.9222 | 2737406.5257 | 1192204.545 | 2737400.7405 | 1192197.7624 | 2737399.698 | 1192195.6702 | 2737399.2222 | 1192192.1454 | 2737399.3561 | 1192189.6354 | 2737396.0904 | 1192185.3904 | 2737408.8334 | 1192179.7897 | 2737412.7679 | 1192175.51 | 2737415.1037 | 1192171.4382 | 2737415.9759 | 1192165.6759 | 2737415.6568 | 1192156.9951 | 2737408.9239 | 1192140.0049 | 2737405.5511 | 1192133.7782 | 2737404.985 | 1192127.5492 | 2737409.1158 | 1192120.0381 | 2737421.0432 | 1192120.0676 | 2737432.574 | 1192116.4517 | 2737446.0104 | 1192106.5747 | 2737456.8504 | 1192104.4776 | 2737467.4133 | 1192100.8285 | 2737480.9975 | 1192092.4895 | 2737495.8964 | 1192092.3205 | 2737510.7345 | 1192095.4528 | 2737523.5209 | 1192116.174 | 2737528.3676 | 1192130.9303 | 2737537.5828 | 1192144.7641 | 2737554.8517 | 1192153.2899 | 2737580.0882 | 1192154.9491 | 2737592.6908 | 1192168.0603 | 2737611.5045 | 1192217.8209 | 2737622.3589 | 1192231.6591 | 2737628.4728 | 1192239.3947 | 2737637.3924 | 1192242.8581 | 2737646.4269 | 1192236.0272 | 2737655.2324 | 1192221.9186 | 2737662.6373 | 1192219.2869 | 2737673.7139 | 1192225.7913 | 2737685.9751 | 1192237.4826 | 2737697.1424 | 1192244.6785 | 2737702.0846 | 1192244.67 | 2737706.4128 | 1192241.189 | 2737720.3843 | 1192211.0646 | 2737726.8126 | 1192199.8482
3 | 2738227.4242 | 1191814.7195 | 2738251.5582 | 1191806.3926 | 2738274.6839 | 1191797.1418 | 2738286.4741 | 1191796.8695 | 2738296.1143 | 1191790.2982 | 2738315.8723 | 1191788.4867 | 2738327.3461 | 1191790.3533 | 2738356.0226 | 1191764.707
4 | 2737343.1933 | 1192325.8088 | 2737339.2313 | 1192331.4017
5 | 2738229.3149 | 1191195.9867 | 2738230.8953 | 1191202.5283 | 2738235.0364 | 1191208.5064 | 2738242.8373 | 1191215.8702 | 2738250.3814 | 1191219.8253 | 2738255.2792 | 1191230.6803 | 2738257.6085 | 1191242.1098 | 2738261.2338 | 1191250.6002 | 2738262.7994 | 1191255.796 | 2738261.9712 | 1191261.9262 | 2738262.4942 | 1191269.9891 | 2738260.859 | 1191278.6915 | 2738259.4563 | 1191287.5661 | 2738257.1895 | 1191289.2706 | 2738250.3246 | 1191286.2986 | 2738242.8815 | 1191290.5189 | 2738239.7101 | 1191296.3836 | 2738236.6976 | 1191303.9533 | 2738233.2088 | 1191310.678 | 2738229.0242 | 1191323.7473 | 2738226.2165 | 1191335.9921 | 2738225.991 | 1191340.4682 | 2738229.0187 | 1191347.0877 | 2738229.3882 | 1191353.2122 | 2738228.8867 | 1191359.0719 | 2738226.2163 | 1191365.3708 | 2738226.9801 | 1191373.9062 | 2738227.3966 | 1191382.2891 | 2738229.9523 | 1191387.5523 | 2738231.6503 | 1191395.5978 | 2738233.7573 | 1191403.4416 | 2738237.6856 | 1191410.3711 | 2738240.3728 | 1191413.9026 | 2738241.9525 | 1191423.4355 | 2738237.5648 | 1191431.1069 | 2738233.6588 | 1191433.7743 | 2738229.3618 | 1191437.5225 | 2738231.6692 | 1191441.6457 | 2738228.3488 | 1191445.0495 | 2738230.8528 | 1191451.2233 | 2738235.1756 | 1191456.594 | 2738243.2086 | 1191463.1402 | 2738247.8388 | 1191465.7715 | 2738252.8636 | 1191472.1148 | 2738264.3785 | 1191483.7788 | 2738264.1984 | 1191491.5697 | 2738265.4446 | 1191500.3499 | 2738267.4516 | 1191507.235 | 2738271.7688 | 1191518.1211 | 2738271.186 | 1191522.5444 | 2738267.6556 | 1191529.4239 | 2738263.5722 | 1191534.4891 | 2738261.7462 | 1191540.5628 | 2738259.6339 | 1191548.7871 | 2738257.3886 | 1191557.4866 | 2738257.7027 | 1191564.6884 | 2738259.9488 | 1191571.4567 | 2738265.0622 | 1191579.2477 | 2738272.7673 | 1191589.4115 | 2738278.4007 | 1191610.9919 | 2738279.8941 | 1191619.9669 | 2738284.7374 | 1191631.1876 | 2738290.2726 | 1191646.1273 | 2738293.6778 | 1191666.0995 | 2738295.6218 | 1191675.7075 | 2738296.901 | 1191693.9404 | 2738297.4192 | 1191698.5782 | 2738303.4412 | 1191705.6563 | 2738303.5826 | 1191713.0654 | 2738310.4241 | 1191724.944 | 2738314.0857 | 1191733.8245 | 2738314.06 | 1191741.53 | 2738315.0093 | 1191760.8338 | 2738313.9829 | 1191764.98 | 2738310.6181 | 1191765.0356 | 2738309.312 | 1191768.7417 | 2738314.2352 | 1191779.4639 | 2738315.8723 | 1191788.4867 | 2738327.3461 | 1191790.3533 | 2738356.0226 | 1191764.707
6 | 2738356.0226 | 1191764.707 | 2738376.4883 | 1191742.2069 | 2738385.4965 | 1191733.2859 | 2738392.0294 | 1191724.8748 | 2738400.881 | 1191707.2322 | 2738417.6789 | 1191690.6409 | 2738422.1962 | 1191687.7399
7 | 2738229.3149 | 1191195.9867 | 2738210.9994 | 1191201.9684 | 2738200.9383 | 1191194.8777
8 | 2738229.3149 | 1191195.9867 | 2738240.3777 | 1191189.6149 | 2738244.7675 | 1191181.5322 | 2738244.8498 | 1191174.6731 | 2738244.1056 | 1191161.9904 | 2738238.2528 | 1191150.2015 | 2738224.948 | 1191135.7495 | 2738220.6239 | 1191127.7878 | 2738229.9221 | 1191119.218 | 2738276.664 | 1191101.8395 | 2738291.0258 | 1191088.7165 | 2738298.7075 | 1191083.0071
9 | 2738486.0677 | 1191646.7216 | 2738422.1962 | 1191687.7399
10 | 2738196.5135 | 1191191.7593 | 2738200.9383 | 1191194.8777
11 | 2738313.2546 | 1191072.1949 | 2738298.7075 | 1191083.0071
12 | 2738504.3363 | 1191623.615 | 2738499.9362 | 1191634.7775 | 2738497.3432 | 1191638.387 | 2738493.9415 | 1191641.6776 | 2738486.0677 | 1191646.7216
13 | 2738504.3363 | 1191623.615 | 2738504.2477 | 1191620.8552 | 2738505.5724 | 1191612.0678 | 2738507.4591 | 1191605.6953 | 2738510.3267 | 1191601.425 | 2738516.2266 | 1191598.2924 | 2738529.6557 | 1191594.7893 | 2738548.88 | 1191588.3959 | 2738556.4272 | 1191587.2475 | 2738563.5832 | 1191587.5133 | 2738571.1821 | 1191586.1104 | 2738585.1223 | 1191574.0458 | 2738603.4948 | 1191562.2842 | 2738608.6974 | 1191556.3333 | 2738610.8117 | 1191551.3339 | 2738611.7167 | 1191545.1945 | 2738609.6206 | 1191540.8536 | 2738595.5921 | 1191534.6683 | 2738583.2665 | 1191528.0666 | 2738575.3257 | 1191522.167 | 2738568.5694 | 1191515.8389 | 2738561.6851 | 1191506.1496 | 2738557.9022 | 1191497.2439 | 2738555.4046 | 1191483.5642 | 2738552.4411 | 1191476.8236 | 2738546.4553 | 1191470.1575 | 2738538.2881 | 1191462.8294 | 2738525.9218 | 1191453.369 | 2738519.5478 | 1191450.6193 | 2738511.9598 | 1191448.9091 | 2738487.9865 | 1191446.2633 | 2738482.2016 | 1191444.0944 | 2738478.5352 | 1191440.6958 | 2738477.1066 | 1191436.8375 | 2738477.9634 | 1191432.7764 | 2738482.2626 | 1191428.2834 | 2738487.512 | 1191424.5908 | 2738528.2175 | 1191398.7124 | 2738544.0888 | 1191386.9371 | 2738559.1854 | 1191377.657 | 2738566.9426 | 1191375.357 | 2738574.9614 | 1191374.6087 | 2738574.9614 | 1191374.6087
14 | 2738574.9614 | 1191374.6087 | 2738494.2122 | 1191230.001
15 | 2738610.7673 | 1191383.081 | 2738602.7311 | 1191383.6144 | 2738595.8359 | 1191382.9431 | 2738581.0555 | 1191376.2733 | 2738574.9614 | 1191374.6087
16 | 2738475.25 | 1191211.3056 | 2738479.0867 | 1191221.191 | 2738486.0278 | 1191228.7798 | 2738494.2122 | 1191230.001
17 | 2738313.7197 | 1191075.1746 | 2738314.4892 | 1191087.7468 | 2738306.5849 | 1191086.8301 | 2738295.7894 | 1191093.1745 | 2738302.3406 | 1191099.4975 | 2738291.8111 | 1191116.4454
18 | 2738313.2546 | 1191072.1949 | 2738313.7197 | 1191075.1746
19 | 2738313.2546 | 1191072.1949 | 2738313.2033 | 1191059.239 | 2738304.3499 | 1191040.9756
20 | 2738304.3499 | 1191040.9756 | 2738298.3276 | 1191037.1779 | 2738285.9174 | 1191040.5971
21 | 2738285.9174 | 1191040.5971 | 2738271.7038 | 1191044.5131 | 2738255.9816 | 1191042.8931 | 2738240.3331 | 1191037.0478

## bus_geodata
| x | y | coords
0 | 2737786.5803 | 1191893.5743
1 | 2737726.8126 | 1192199.8482
2 | 2738227.4242 | 1191814.7195
3 | 2737343.1933 | 1192325.8088
4 | 2738356.0226 | 1191764.707
5 | 2737339.2313 | 1192331.4017
6 | 2738229.3149 | 1191195.9867
7 | 2738422.1962 | 1191687.7399
8 | 2738200.9383 | 1191194.8777
9 | 2738298.7075 | 1191083.0071
10 | 2738504.3363 | 1191623.615
11 | 2738486.0676 | 1191646.7216
12 | 2738574.9614 | 1191374.6087
13 | 2738610.7673 | 1191383.081
14 | 2738494.2122 | 1191230.001
15 | 2738475.25 | 1191211.3056
16 | 2738313.7197 | 1191075.1746
17 | 2738291.8111 | 1191116.4454
18 | 2738313.2546 | 1191072.1949
19 | 2738304.3499 | 1191040.9756
20 | 2738285.9174 | 1191040.5971
21 | 2738240.3331 | 1191037.0478
22 | 2738196.5135 | 1191191.7593
23 | 2737786.5803 | 1191893.5743

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1