## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3764-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3764-9_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3764-9_0_3_node_42 | 0.4 | n |  | TRUE
3 | bus_LV_3764-9_0_3_node_23 | 0.4 | n |  | TRUE
4 | bus_LV_3764-9_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_3764-9_0_3_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_3764-9_0_3_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_3764-9_0_3_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_3764-9_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_3764-9_0_3_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_3764-9_0_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_3764-9_0_3_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_3764-9_0_3_node_3 | 0.4 | n |  | TRUE
13 | bus_LV_3764-9_0_3_node_4 | 0.4 | n |  | TRUE
14 | bus_LV_3764-9_0_3_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_3764-9_0_3_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_3764-9_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_3764-9_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_3764-9_0_3_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_3764-9_0_3_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_3764-9_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_3764-9_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_3764-9_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_3764-9_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_3764-9_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_3764-9_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_3764-9_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_3764-9_0_3_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_3764-9_0_3_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_3764-9_0_3_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_3764-9_0_3_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_3764-9_0_3_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_3764-9_0_3_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_3764-9_0_3_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_3764-9_0_3_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_3764-9_0_3_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_3764-9_0_3_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_3764-9_0_3_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_3764-9_0_3_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_3764-9_0_3_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_3764-9_0_3_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_3764-9_0_3_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_3764-9_0_3_node_21 | 0.4 | n |  | TRUE
43 | bus_MV_170_0_node_133 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3764-9_0_3_load_0 | 0 | 0.013272 | 0.0033262 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3764-9_0_3_load_23 | 3 | 0.0012456 | 0.00031218 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3764-9_0_3_load_2 | 6 | 0.0041306 | 0.0010352 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3764-9_0_3_load_31 | 7 | 0.0037045 | 0.00092844 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3764-9_0_3_load_12 | 8 | 0.0031375 | 0.00078634 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3764-9_0_3_load_41 | 9 | 0.0048082 | 0.001205 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3764-9_0_3_load_30 | 10 | 0.003414 | 0.00085564 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3764-9_0_3_load_13 | 11 | 0.0064197 | 0.0016089 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3764-9_0_3_load_3 | 12 | 0.025587 | 0.0064128 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3764-9_0_3_load_6 | 15 | 0.008972 | 0.0022486 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3764-9_0_3_load_9 | 17 | 0.0068453 | 0.0017156 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3764-9_0_3_load_24 | 18 | 0.0029882 | 0.00074891 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3764-9_0_3_load_40 | 19 | 0.017212 | 0.0043137 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3764-9_0_3_load_15 | 21 | 0.0065791 | 0.0016489 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3764-9_0_3_load_11 | 22 | 0.018151 | 0.0045491 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3764-9_0_3_load_25 | 24 | 0.005087 | 0.0012749 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3764-9_0_3_load_26 | 25 | 0.00454 | 0.0011378 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3764-9_0_3_load_27 | 26 | 0.0025612 | 0.0006419 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3764-9_0_3_load_28 | 27 | 0.0029309 | 0.00073455 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3764-9_0_3_load_32 | 29 | 0.0038443 | 0.00096346 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3764-9_0_3_load_33 | 30 | 0.0041511 | 0.0010404 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3764-9_0_3_load_34 | 31 | 0.0010545 | 0.00026428 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3764-9_0_3_load_36 | 33 | 0.00097498 | 0.00024435 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3764-9_0_3_load_37 | 34 | 0.00093949 | 0.00023546 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3764-9_0_3_load_38 | 35 | 0.00084508 | 0.0002118 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3764-9_0_3_load_16 | 37 | 0.0087556 | 0.0021944 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3764-9_0_3_load_17 | 38 | 0.0055731 | 0.0013967 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3764-9_0_3_load_18 | 39 | 0.00089529 | 0.00022438 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3764-9_0_3_load_19 | 40 | 0.0017785 | 0.00044575 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3764-9_0_3_load_20 | 41 | 0.001378 | 0.00034536 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3764-9_0_3_load_21 | 42 | 0.0026038 | 0.00065257 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3764-9_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3764-9_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.12912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3764-9_0_3_line_2 | NAYY 4x150 SE | 2 | 9 | 0.1028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3764-9_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.06612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3764-9_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.10337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3764-9_0_3_line_5 | NAYY 4x150 SE | 4 | 18 | 0.10093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3764-9_0_3_line_6 | NAYY 4x150 SE | 4 | 13 | 0.071903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3764-9_0_3_line_7 | NAYY 4x150 SE | 5 | 41 | 0.087927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3764-9_0_3_line_8 | NAYY 4x150 SE | 6 | 7 | 0.087195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_3764-9_0_3_line_9 | NAYY 4x150 SE | 6 | 8 | 0.1158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_3764-9_0_3_line_10 | NAYY 4x150 SE | 7 | 10 | 0.0035202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_3764-9_0_3_line_11 | NAYY 4x150 SE | 8 | 11 | 0.031649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_3764-9_0_3_line_12 | NAYY 4x150 SE | 9 | 30 | 0.09072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3764-9_0_3_line_13 | NAYY 4x150 SE | 10 | 27 | 0.0081294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_3764-9_0_3_line_14 | NAYY 4x150 SE | 11 | 23 | 0.025523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_3764-9_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.048658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3764-9_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.081028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3764-9_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.012101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3764-9_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.033934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3764-9_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.058536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3764-9_0_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.037156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3764-9_0_3_line_21 | NAYY 4x150 SE | 17 | 20 | 0.086214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3764-9_0_3_line_22 | NAYY 4x150 SE | 18 | 21 | 0.06997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_3764-9_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.075944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3764-9_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.031879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_3764-9_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.011332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_3764-9_0_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.016528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_3764-9_0_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.017901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_3764-9_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.022386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_3764-9_0_3_line_29 | NAYY 4x150 SE | 28 | 36 | 0.047248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_3764-9_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.045134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3764-9_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.012142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3764-9_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.021297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_3764-9_0_3_line_33 | NAYY 4x150 SE | 32 | 33 | 0.0068849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_3764-9_0_3_line_34 | NAYY 4x150 SE | 33 | 34 | 0.010869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_3764-9_0_3_line_35 | NAYY 4x150 SE | 34 | 35 | 0.017763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_3764-9_0_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.068717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_3764-9_0_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.0091038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3764-9_0_3_line_38 | NAYY 4x150 SE | 37 | 39 | 0.14917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3764-9_0_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.024992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3764-9_0_3_line_40 | NAYY 4x150 SE | 39 | 41 | 0.036849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3764-9_0_3_line_41 | NAYY 4x150 SE | 40 | 42 | 0.029053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3764-9_0_3_trafo_24 | 0.25 MVA 20/0.4 kV | 43 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2824078.0179 | 1191076.7671 | 2824071.3393 | 1191081.6119 | 2824067.1741 | 1191084.7822 | 2824057.9406 | 1191086.294 | 2824054.586 | 1191084.1326 | 2824051.3268 | 1191072.4964 | 2824048.1233 | 1191059.3717 | 2824040.0602 | 1191049.0811
1 | 2824078.0179 | 1191076.7671 | 2824064.0168 | 1191205.1216
2 | 2824150.1688 | 1191258.3776 | 2824130.5469 | 1191241.0998 | 2824114.2021 | 1191229.0623 | 2824100.3199 | 1191222.4124 | 2824071.7923 | 1191213.1779 | 2824064.0168 | 1191205.1216
3 | 2824192.4899 | 1190943.2227 | 2824164.7857 | 1190939.8925 | 2824138.7796 | 1190939.3295 | 2824126.5769 | 1190939.1327
4 | 2824038.981 | 1190899.6798 | 2824043.1281 | 1190908.6125 | 2824048.9832 | 1190916.7859 | 2824059.3697 | 1190925.8745 | 2824070.5305 | 1190931.8216 | 2824082.5603 | 1190936.3773 | 2824092.8612 | 1190937.7645 | 2824103.8713 | 1190938.7667 | 2824126.5769 | 1190939.1327
5 | 2824192.4899 | 1190943.2227 | 2824190.9939 | 1190952.3778 | 2824195.1725 | 1190957.4071 | 2824203.9258 | 1190960.3606 | 2824219.0804 | 1190962.2081 | 2824235.8777 | 1190962.3929 | 2824245.4384 | 1190965.399 | 2824266.4769 | 1190976.6784 | 2824275.3472 | 1190981.108
6 | 2824263.7934 | 1190953.9725 | 2824192.4899 | 1190943.2227
7 | 2824038.981 | 1190899.6798 | 2824042.2299 | 1190889.7893 | 2824041.2909 | 1190844.132 | 2824045.813 | 1190812.6051
8 | 2824262.3664 | 1191158.9799 | 2824246.2489 | 1191135.7925 | 2824228.1868 | 1191111.9314 | 2824204.2729 | 1191095.4741
9 | 2824302.0366 | 1191033.4125 | 2824204.2729 | 1191095.4741
10 | 2824262.3664 | 1191158.9799 | 2824265.3216 | 1191160.8928
11 | 2824302.0366 | 1191033.4125 | 2824330.7014 | 1191032.6413 | 2824333.612 | 1191033.2508
12 | 2824218.5215 | 1191198.7284 | 2824150.1688 | 1191258.3776
13 | 2824265.3216 | 1191160.8928 | 2824272.146 | 1191165.3102
14 | 2824358.5935 | 1191038.4823 | 2824333.612 | 1191033.2508
15 | 2824263.7934 | 1190953.9725 | 2824271.1005 | 1190939.7066 | 2824283.0546 | 1190931.2106 | 2824298.8267 | 1190929.4214 | 2824300.8456 | 1190928.8782
16 | 2824377.7518 | 1190903.6914 | 2824347.7044 | 1190915.6023 | 2824337.7869 | 1190918.4453 | 2824317.5146 | 1190924.3931 | 2824300.8456 | 1190928.8782
17 | 2824263.7934 | 1190953.9725 | 2824275.7743 | 1190955.673
18 | 2824346.9106 | 1190889.3406 | 2824377.7518 | 1190903.6914
19 | 2824275.7743 | 1190955.673 | 2824300.1175 | 1190959.1282 | 2824328.8919 | 1190960.9973 | 2824333.9698 | 1190960.3897
20 | 2824346.9106 | 1190889.3406 | 2824346.6353 | 1190885.2809 | 2824348.2057 | 1190880.8677 | 2824349.5999 | 1190877.2822 | 2824354.2559 | 1190872.8401 | 2824363.7528 | 1190866.3547 | 2824369.9606 | 1190864.0531
21 | 2824417.8123 | 1190941.1272 | 2824387.583 | 1190949.7493 | 2824357.2068 | 1190957.6095 | 2824333.9698 | 1190960.3897
22 | 2824335.2101 | 1191016.8144 | 2824332.8063 | 1191014.587 | 2824319.2562 | 1191004.3669 | 2824306.0027 | 1190996.4163 | 2824275.3472 | 1190981.108
23 | 2824353.6913 | 1190927.9862 | 2824369.8683 | 1190922.7303 | 2824386.6897 | 1190919.0228 | 2824399.7702 | 1190921.6161 | 2824412.6994 | 1190928.2421 | 2824416.5117 | 1190935.0933 | 2824417.8123 | 1190941.1272
24 | 2824358.5935 | 1191038.4823 | 2824335.2101 | 1191016.8144
25 | 2824297.5641 | 1191179.7284 | 2824287.6456 | 1191174.2487
26 | 2824297.5641 | 1191179.7284 | 2824307.7945 | 1191185.3804 | 2824311.5638 | 1191188.416
27 | 2824272.146 | 1191165.3102 | 2824276.1035 | 1191167.8719 | 2824287.6456 | 1191174.2487
28 | 2824327.9169 | 1191203.5563 | 2824322.9345 | 1191197.5735 | 2824311.5638 | 1191188.416
29 | 2824330.8731 | 1191240.7569 | 2824316.4484 | 1191226.1876 | 2824315.9474 | 1191218.782 | 2824327.9169 | 1191203.5563
30 | 2824192.715 | 1191161.9503 | 2824196.3331 | 1191168.3963 | 2824212.5723 | 1191193.0233 | 2824218.5215 | 1191198.7284
31 | 2824186.7719 | 1191151.3621 | 2824192.715 | 1191161.9503
32 | 2824233.8924 | 1191213.4688 | 2824218.5215 | 1191198.7284
33 | 2824233.8924 | 1191213.4688 | 2824239.9332 | 1191216.7721
34 | 2824249.4691 | 1191221.9866 | 2824239.9332 | 1191216.7721
35 | 2824249.4691 | 1191221.9866 | 2824255.8869 | 1191225.4961 | 2824265.0723 | 1191230.4763
36 | 2824330.8731 | 1191240.7569 | 2824320.7344 | 1191243.8141 | 2824292.2967 | 1191241.7574 | 2824277.4885 | 1191237.2083 | 2824265.0723 | 1191230.4763
37 | 2824140.2712 | 1190752.8472 | 2824131.4624 | 1190750.548 | 2824131.4624 | 1190750.548
38 | 2824054.4396 | 1190776.8963 | 2824059.0889 | 1190761.9757 | 2824079.8083 | 1190727.7983 | 2824093.3319 | 1190711.6514 | 2824110.3635 | 1190704.9918 | 2824118.8768 | 1190707.6359 | 2824123.5969 | 1190714.5209 | 2824124.8529 | 1190725.6259 | 2824131.4624 | 1190750.548
39 | 2824140.2712 | 1190752.8472 | 2824140.2712 | 1190752.8472 | 2824153.6751 | 1190741.3238 | 2824159.2501 | 1190736.5863
40 | 2824045.813 | 1190812.6051 | 2824047.9459 | 1190797.7356 | 2824054.4396 | 1190776.8963
41 | 2824177.616 | 1190714.5792 | 2824169.8498 | 1190727.5792 | 2824159.2501 | 1190736.5863

## bus_geodata
| x | y | coords
0 | 2824040.0602 | 1191049.0811
1 | 2824078.0179 | 1191076.7671
2 | 2824064.0168 | 1191205.1216
3 | 2824126.5769 | 1190939.1327
4 | 2824192.4899 | 1190943.2227
5 | 2824038.981 | 1190899.6798
6 | 2824204.2729 | 1191095.4741
7 | 2824262.3664 | 1191158.9799
8 | 2824302.0366 | 1191033.4125
9 | 2824150.1688 | 1191258.3776
10 | 2824265.3216 | 1191160.8928
11 | 2824333.612 | 1191033.2508
12 | 2824300.8456 | 1190928.8782
13 | 2824263.7934 | 1190953.9725
14 | 2824377.7518 | 1190903.6914
15 | 2824275.7743 | 1190955.673
16 | 2824346.9106 | 1190889.3406
17 | 2824333.9698 | 1190960.3897
18 | 2824275.3472 | 1190981.108
19 | 2824369.9606 | 1190864.0531
20 | 2824417.8123 | 1190941.1272
21 | 2824335.2101 | 1191016.8144
22 | 2824353.6913 | 1190927.9862
23 | 2824358.5935 | 1191038.4823
24 | 2824297.5641 | 1191179.7284
25 | 2824287.6456 | 1191174.2487
26 | 2824311.5638 | 1191188.416
27 | 2824272.146 | 1191165.3102
28 | 2824327.9169 | 1191203.5564
29 | 2824192.715 | 1191161.9503
30 | 2824218.5215 | 1191198.7284
31 | 2824186.7719 | 1191151.3621
32 | 2824233.8924 | 1191213.4688
33 | 2824239.9332 | 1191216.7721
34 | 2824249.4691 | 1191221.9866
35 | 2824265.0723 | 1191230.4763
36 | 2824330.8731 | 1191240.7569
37 | 2824131.4624 | 1190750.548
38 | 2824140.2712 | 1190752.8472
39 | 2824054.4396 | 1190776.8963
40 | 2824159.2501 | 1190736.5863
41 | 2824045.813 | 1190812.6051
42 | 2824177.616 | 1190714.5792
43 | 2824192.4899 | 1190943.2227

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1