## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3891-1_2_4_node_84 | 0.4 | n |  | TRUE
1 | bus_LV_3891-1_2_4_node_85 | 0.4 | n |  | TRUE
2 | bus_LV_3891-1_2_4_node_86 | 0.4 | n |  | TRUE
3 | bus_LV_3891-1_2_4_node_238 | 0.4 | n |  | TRUE
4 | bus_LV_3891-1_2_4_node_277 | 0.4 | n |  | TRUE
5 | bus_LV_3891-1_2_4_node_281 | 0.4 | n |  | TRUE
6 | bus_LV_3891-1_2_4_node_143 | 0.4 | n |  | TRUE
7 | bus_LV_3891-1_2_4_node_150 | 0.4 | n |  | TRUE
8 | bus_LV_3891-1_2_4_node_144 | 0.4 | n |  | TRUE
9 | bus_LV_3891-1_2_4_node_147 | 0.4 | n |  | TRUE
10 | bus_LV_3891-1_2_4_node_148 | 0.4 | n |  | TRUE
11 | bus_LV_3891-1_2_4_node_212 | 0.4 | n |  | TRUE
12 | bus_LV_3891-1_2_4_node_211 | 0.4 | n |  | TRUE
13 | bus_LV_3891-1_2_4_node_276 | 0.4 | n |  | TRUE
14 | bus_LV_3891-1_2_4_node_301 | 0.4 | n |  | TRUE
15 | bus_LV_3891-1_2_4_node_227 | 0.4 | n |  | TRUE
16 | bus_LV_3891-1_2_4_node_218 | 0.4 | n |  | TRUE
17 | bus_LV_3891-1_2_4_node_278 | 0.4 | n |  | TRUE
18 | bus_LV_3891-1_2_4_node_219 | 0.4 | n |  | TRUE
19 | bus_LV_3891-1_2_4_node_220 | 0.4 | n |  | TRUE
20 | bus_LV_3891-1_2_4_node_221 | 0.4 | n |  | TRUE
21 | bus_LV_3891-1_2_4_node_233 | 0.4 | n |  | TRUE
22 | bus_LV_3891-1_2_4_node_225 | 0.4 | n |  | TRUE
23 | bus_LV_3891-1_2_4_node_222 | 0.4 | n |  | TRUE
24 | bus_LV_3891-1_2_4_node_223 | 0.4 | n |  | TRUE
25 | bus_LV_3891-1_2_4_node_224 | 0.4 | n |  | TRUE
26 | bus_LV_3891-1_2_4_node_235 | 0.4 | n |  | TRUE
27 | bus_LV_3891-1_2_4_node_226 | 0.4 | n |  | TRUE
28 | bus_LV_3891-1_2_4_node_228 | 0.4 | n |  | TRUE
29 | bus_LV_3891-1_2_4_node_229 | 0.4 | n |  | TRUE
30 | bus_LV_3891-1_2_4_node_230 | 0.4 | n |  | TRUE
31 | bus_LV_3891-1_2_4_node_231 | 0.4 | n |  | TRUE
32 | bus_LV_3891-1_2_4_node_234 | 0.4 | n |  | TRUE
33 | bus_LV_3891-1_2_4_node_232 | 0.4 | n |  | TRUE
34 | bus_LV_3891-1_2_4_node_236 | 0.4 | n |  | TRUE
35 | bus_LV_3891-1_2_4_node_240 | 0.4 | n |  | TRUE
36 | bus_LV_3891-1_2_4_node_248 | 0.4 | n |  | TRUE
37 | bus_LV_3891-1_2_4_node_241 | 0.4 | n |  | TRUE
38 | bus_LV_3891-1_2_4_node_237 | 0.4 | n |  | TRUE
39 | bus_LV_3891-1_2_4_node_358 | 0.4 | n |  | TRUE
40 | bus_LV_3891-1_2_4_node_356 | 0.4 | n |  | TRUE
41 | bus_LV_3891-1_2_4_node_282 | 0.4 | n |  | TRUE
42 | bus_LV_3891-1_2_4_node_239 | 0.4 | n |  | TRUE
43 | bus_LV_3891-1_2_4_node_283 | 0.4 | n |  | TRUE
44 | bus_LV_3891-1_2_4_node_246 | 0.4 | n |  | TRUE
45 | bus_LV_3891-1_2_4_node_242 | 0.4 | n |  | TRUE
46 | bus_LV_3891-1_2_4_node_244 | 0.4 | n |  | TRUE
47 | bus_LV_3891-1_2_4_node_249 | 0.4 | n |  | TRUE
48 | bus_LV_3891-1_2_4_node_250 | 0.4 | n |  | TRUE
49 | bus_LV_3891-1_2_4_node_247 | 0.4 | n |  | TRUE
50 | bus_LV_3891-1_2_4_node_268 | 0.4 | n |  | TRUE
51 | bus_LV_3891-1_2_4_node_269 | 0.4 | n |  | TRUE
52 | bus_LV_3891-1_2_4_node_271 | 0.4 | n |  | TRUE
53 | bus_LV_3891-1_2_4_node_270 | 0.4 | n |  | TRUE
54 | bus_LV_3891-1_2_4_node_272 | 0.4 | n |  | TRUE
55 | bus_LV_3891-1_2_4_node_273 | 0.4 | n |  | TRUE
56 | bus_LV_3891-1_2_4_node_274 | 0.4 | n |  | TRUE
57 | bus_LV_3891-1_2_4_node_275 | 0.4 | n |  | TRUE
58 | bus_LV_3891-1_2_4_node_279 | 0.4 | n |  | TRUE
59 | bus_LV_3891-1_2_4_node_280 | 0.4 | n |  | TRUE
60 | bus_LV_3891-1_2_4_node_383 | 0.4 | n |  | TRUE
61 | bus_LV_3891-1_2_4_node_284 | 0.4 | n |  | TRUE
62 | bus_LV_3891-1_2_4_node_285 | 0.4 | n |  | TRUE
63 | bus_LV_3891-1_2_4_node_379 | 0.4 | n |  | TRUE
64 | bus_LV_3891-1_2_4_node_389 | 0.4 | n |  | TRUE
65 | bus_LV_3891-1_2_4_node_357 | 0.4 | n |  | TRUE
66 | bus_LV_3891-1_2_4_node_359 | 0.4 | n |  | TRUE
67 | bus_LV_3891-1_2_4_node_360 | 0.4 | n |  | TRUE
68 | bus_LV_3891-1_2_4_node_375 | 0.4 | n |  | TRUE
69 | bus_LV_3891-1_2_4_node_374 | 0.4 | n |  | TRUE
70 | bus_LV_3891-1_2_4_node_364 | 0.4 | n |  | TRUE
71 | bus_LV_3891-1_2_4_node_370 | 0.4 | n |  | TRUE
72 | bus_LV_3891-1_2_4_node_368 | 0.4 | n |  | TRUE
73 | bus_LV_3891-1_2_4_node_371 | 0.4 | n |  | TRUE
74 | bus_LV_3891-1_2_4_node_372 | 0.4 | n |  | TRUE
75 | bus_LV_3891-1_2_4_node_373 | 0.4 | n |  | TRUE
76 | bus_LV_3891-1_2_4_node_386 | 0.4 | n |  | TRUE
77 | bus_LV_3891-1_2_4_node_380 | 0.4 | n |  | TRUE
78 | bus_LV_3891-1_2_4_node_381 | 0.4 | n |  | TRUE
79 | bus_LV_3891-1_2_4_node_382 | 0.4 | n |  | TRUE
80 | bus_LV_3891-1_2_4_node_385 | 0.4 | n |  | TRUE
81 | bus_LV_3891-1_2_4_node_384 | 0.4 | n |  | TRUE
82 | bus_LV_3891-1_2_4_node_387 | 0.4 | n |  | TRUE
83 | bus_LV_3891-1_2_4_node_388 | 0.4 | n |  | TRUE
84 | bus_LV_3891-1_2_4_node_390 | 0.4 | n |  | TRUE
85 | bus_LV_3891-1_2_4_node_391 | 0.4 | n |  | TRUE
86 | bus_MV_0_node_236 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3891-1_2_4_load_85 | 1 | 0.00063228 | 0.00015846 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3891-1_2_4_load_277 | 4 | 0.00012634 | 3.1663e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3891-1_2_4_load_281 | 5 | 0.00019738 | 4.9468e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3891-1_2_4_load_150 | 7 | 0.00017857 | 4.4755e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3891-1_2_4_load_144 | 8 | 0.00020636 | 5.1719e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3891-1_2_4_load_147 | 9 | 0.00012773 | 3.2012e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3891-1_2_4_load_212 | 11 | 0.00013181 | 3.3035e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3891-1_2_4_load_211 | 12 | 0.00014535 | 3.6429e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3891-1_2_4_load_276 | 13 | 0.00080842 | 0.00020261 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3891-1_2_4_load_301 | 14 | 0.0017569 | 0.00044032 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3891-1_2_4_load_227 | 15 | 0.00016481 | 4.1306e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3891-1_2_4_load_218 | 16 | 0.00068355 | 0.00017131 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3891-1_2_4_load_278 | 17 | 0.00033381 | 8.366e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3891-1_2_4_load_219 | 18 | 0.00053078 | 0.00013303 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3891-1_2_4_load_220 | 19 | 0.00052337 | 0.00013117 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3891-1_2_4_load_233 | 21 | 0.0023604 | 0.00059158 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3891-1_2_4_load_225 | 22 | 7.7995e-05 | 1.9547e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3891-1_2_4_load_223 | 24 | 0.00096379 | 0.00024155 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3891-1_2_4_load_224 | 25 | 0.00010502 | 2.6322e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3891-1_2_4_load_235 | 26 | 0.00091621 | 0.00022962 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3891-1_2_4_load_226 | 27 | 7.2779e-05 | 1.824e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3891-1_2_4_load_228 | 28 | 0.0017866 | 0.00044775 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3891-1_2_4_load_229 | 29 | 0.00023622 | 5.9203e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3891-1_2_4_load_234 | 32 | 0.00043155 | 0.00010816 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3891-1_2_4_load_240 | 35 | 0.00060878 | 0.00015257 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3891-1_2_4_load_248 | 36 | 0.0027275 | 0.00068358 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3891-1_2_4_load_241 | 37 | 0.0016015 | 0.00040136 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3891-1_2_4_load_356 | 40 | 0.00098996 | 0.00024811 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3891-1_2_4_load_282 | 41 | 0.00030207 | 7.5707e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3891-1_2_4_load_246 | 44 | 0.00048197 | 0.00012079 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3891-1_2_4_load_242 | 45 | 0.0029666 | 0.00074351 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3891-1_2_4_load_249 | 47 | 0.001421 | 0.00035614 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3891-1_2_4_load_247 | 49 | 0.0012491 | 0.00031305 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3891-1_2_4_load_268 | 50 | 0.0018244 | 0.00045724 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3891-1_2_4_load_271 | 52 | 0.0021382 | 0.00053587 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3891-1_2_4_load_270 | 53 | 0.0041891 | 0.0010499 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3891-1_2_4_load_272 | 54 | 0.0023975 | 0.00060088 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3891-1_2_4_load_273 | 55 | 0.0012232 | 0.00030655 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3891-1_2_4_load_279 | 58 | 0.00042137 | 0.0001056 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3891-1_2_4_load_280 | 59 | 0.00046527 | 0.00011661 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3891-1_2_4_load_383 | 60 | 0.00073069 | 0.00018313 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3891-1_2_4_load_284 | 61 | 0.00027172 | 6.8099e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3891-1_2_4_load_285 | 62 | 0.00060698 | 0.00015212 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3891-1_2_4_load_379 | 63 | 0.00064936 | 0.00016274 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3891-1_2_4_load_389 | 64 | 0.00044702 | 0.00011203 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3891-1_2_4_load_357 | 65 | 0.0010839 | 0.00027165 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3891-1_2_4_load_359 | 66 | 0.00049791 | 0.00012479 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3891-1_2_4_load_374 | 69 | 0.00076848 | 0.0001926 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3891-1_2_4_load_364 | 70 | 0.0013943 | 0.00034945 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3891-1_2_4_load_368 | 72 | 0.00047883 | 0.00012001 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3891-1_2_4_load_372 | 74 | 0.00065515 | 0.0001642 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3891-1_2_4_load_373 | 75 | 0.0012019 | 0.00030121 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3891-1_2_4_load_386 | 76 | 0.00038967 | 9.766e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3891-1_2_4_load_380 | 77 | 0.00027822 | 6.9728e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3891-1_2_4_load_381 | 78 | 0.00051439 | 0.00012892 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3891-1_2_4_load_382 | 79 | 0.00060396 | 0.00015137 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3891-1_2_4_load_385 | 80 | 0.00036037 | 9.0318e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3891-1_2_4_load_384 | 81 | 0.00049379 | 0.00012375 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3891-1_2_4_load_387 | 82 | 0.00057647 | 0.00014448 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3891-1_2_4_load_388 | 83 | 0.00048092 | 0.00012053 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3891-1_2_4_load_390 | 84 | 0.00055948 | 0.00014022 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3891-1_2_4_load_391 | 85 | 0.00062096 | 0.00015563 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3891-1_2_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.1688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3891-1_2_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.067632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3891-1_2_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0099602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3891-1_2_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0044954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3891-1_2_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.13485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3891-1_2_4_line_5 | NAYY 4x150 SE | 3 | 41 | 0.0090777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3891-1_2_4_line_6 | NAYY 4x150 SE | 3 | 33 | 0.35555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3891-1_2_4_line_7 | NAYY 4x150 SE | 4 | 57 | 0.018068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3891-1_2_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.070325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3891-1_2_4_line_9 | NAYY 4x150 SE | 6 | 8 | 0.088058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3891-1_2_4_line_10 | NAYY 4x150 SE | 7 | 13 | 0.37591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3891-1_2_4_line_11 | NAYY 4x150 SE | 7 | 14 | 0.81642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3891-1_2_4_line_12 | NAYY 4x150 SE | 9 | 10 | 0.17588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3891-1_2_4_line_13 | NAYY 4x150 SE | 10 | 11 | 0.15751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3891-1_2_4_line_14 | NAYY 4x150 SE | 10 | 12 | 0.061654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3891-1_2_4_line_15 | NAYY 4x150 SE | 12 | 15 | 0.1788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3891-1_2_4_line_16 | NAYY 4x150 SE | 13 | 56 | 0.092277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3891-1_2_4_line_17 | NAYY 4x150 SE | 15 | 27 | 0.046471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3891-1_2_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.17523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3891-1_2_4_line_19 | NAYY 4x150 SE | 17 | 58 | 0.020848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3891-1_2_4_line_20 | NAYY 4x150 SE | 18 | 19 | 0.11427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3891-1_2_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.17706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_3891-1_2_4_line_22 | NAYY 4x150 SE | 18 | 21 | 0.16911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_3891-1_2_4_line_23 | NAYY 4x150 SE | 18 | 22 | 0.26446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3891-1_2_4_line_24 | NAYY 4x150 SE | 19 | 23 | 0.017032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3891-1_2_4_line_25 | NAYY 4x150 SE | 20 | 24 | 0.13018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_3891-1_2_4_line_26 | NAYY 4x150 SE | 21 | 30 | 0.071616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_3891-1_2_4_line_27 | NAYY 4x150 SE | 22 | 27 | 0.0086699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3891-1_2_4_line_28 | NAYY 4x150 SE | 23 | 25 | 0.03481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3891-1_2_4_line_29 | NAYY 4x150 SE | 24 | 26 | 0.21523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_3891-1_2_4_line_30 | NAYY 4x150 SE | 26 | 36 | 0.091759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3891-1_2_4_line_31 | NAYY 4x150 SE | 26 | 33 | 0.21928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_3891-1_2_4_line_32 | NAYY 4x150 SE | 28 | 29 | 0.12971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_3891-1_2_4_line_33 | NAYY 4x150 SE | 28 | 30 | 0.016363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_3891-1_2_4_line_34 | NAYY 4x150 SE | 29 | 31 | 0.063086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_3891-1_2_4_line_35 | NAYY 4x150 SE | 31 | 32 | 0.14183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_3891-1_2_4_line_36 | NAYY 4x150 SE | 32 | 35 | 0.02295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_3891-1_2_4_line_37 | NAYY 4x150 SE | 33 | 34 | 0.30151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_3891-1_2_4_line_38 | NAYY 4x150 SE | 34 | 37 | 0.13813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3891-1_2_4_line_39 | NAYY 4x150 SE | 35 | 44 | 0.091197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3891-1_2_4_line_40 | NAYY 4x150 SE | 37 | 45 | 0.096049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3891-1_2_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.053054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3891-1_2_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.033945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3891-1_2_4_line_43 | NAYY 4x150 SE | 39 | 66 | 0.017624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3891-1_2_4_line_44 | NAYY 4x150 SE | 39 | 67 | 0.004825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3891-1_2_4_line_45 | NAYY 4x150 SE | 40 | 65 | 0.0068458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3891-1_2_4_line_46 | NAYY 4x150 SE | 41 | 42 | 0.09051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3891-1_2_4_line_47 | NAYY 4x150 SE | 42 | 43 | 0.020297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3891-1_2_4_line_48 | NAYY 4x150 SE | 43 | 61 | 0.0085119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3891-1_2_4_line_49 | NAYY 4x150 SE | 43 | 62 | 0.0073215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_3891-1_2_4_line_50 | NAYY 4x150 SE | 44 | 49 | 0.016136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_3891-1_2_4_line_51 | NAYY 4x150 SE | 46 | 47 | 0.039857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_3891-1_2_4_line_52 | NAYY 4x150 SE | 46 | 48 | 0.009417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_3891-1_2_4_line_53 | NAYY 4x150 SE | 48 | 51 | 0.10714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_3891-1_2_4_line_54 | NAYY 4x150 SE | 48 | 50 | 0.03542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_3891-1_2_4_line_55 | NAYY 4x150 SE | 49 | 50 | 0.038958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_3891-1_2_4_line_56 | NAYY 4x150 SE | 51 | 52 | 0.0089747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_3891-1_2_4_line_57 | NAYY 4x150 SE | 52 | 53 | 0.0029608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_3891-1_2_4_line_58 | NAYY 4x150 SE | 53 | 54 | 0.022944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_3891-1_2_4_line_59 | NAYY 4x150 SE | 55 | 56 | 0.046585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_3891-1_2_4_line_60 | NAYY 4x150 SE | 56 | 57 | 0.041715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_3891-1_2_4_line_61 | NAYY 4x150 SE | 58 | 59 | 0.017279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_3891-1_2_4_line_62 | NAYY 4x150 SE | 59 | 60 | 0.022431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_3891-1_2_4_line_63 | NAYY 4x150 SE | 60 | 81 | 0.044028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_3891-1_2_4_line_64 | NAYY 4x150 SE | 61 | 63 | 0.020865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_3891-1_2_4_line_65 | NAYY 4x150 SE | 62 | 64 | 0.0040339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_3891-1_2_4_line_66 | NAYY 4x150 SE | 63 | 77 | 0.0081245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_3891-1_2_4_line_67 | NAYY 4x150 SE | 64 | 68 | 0.029077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_3891-1_2_4_line_68 | NAYY 4x150 SE | 67 | 68 | 0.088313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_3891-1_2_4_line_69 | NAYY 4x150 SE | 67 | 69 | 0.01809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_3891-1_2_4_line_70 | NAYY 4x150 SE | 68 | 76 | 0.041823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_3891-1_2_4_line_71 | NAYY 4x150 SE | 69 | 75 | 0.030817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_3891-1_2_4_line_72 | NAYY 4x150 SE | 70 | 71 | 0.0061521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_3891-1_2_4_line_73 | NAYY 4x150 SE | 71 | 73 | 0.01825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_3891-1_2_4_line_74 | NAYY 4x150 SE | 71 | 72 | 0.046407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_3891-1_2_4_line_75 | NAYY 4x150 SE | 73 | 74 | 0.042782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_3891-1_2_4_line_76 | NAYY 4x150 SE | 73 | 75 | 0.0037887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_3891-1_2_4_line_77 | NAYY 4x150 SE | 76 | 82 | 0.029558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_3891-1_2_4_line_78 | NAYY 4x150 SE | 77 | 78 | 0.019033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_3891-1_2_4_line_79 | NAYY 4x150 SE | 78 | 79 | 0.023343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_3891-1_2_4_line_80 | NAYY 4x150 SE | 79 | 80 | 0.023574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_3891-1_2_4_line_81 | NAYY 4x150 SE | 80 | 81 | 0.0018372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_3891-1_2_4_line_82 | NAYY 4x150 SE | 82 | 83 | 0.023816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_3891-1_2_4_line_83 | NAYY 4x150 SE | 83 | 84 | 0.019884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_3891-1_2_4_line_84 | NAYY 4x150 SE | 84 | 85 | 0.018228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3891-1_2_4_trafo_236 | 0.25 MVA 20/0.4 kV | 86 | 34 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46
0 | 2777947.5065 | 1200813.0148 | 2777934.9245 | 1200798.0701 | 2777919.2641 | 1200778.7961 | 2777921.3631 | 1200749.5189 | 2777917.703 | 1200721.5048 | 2777902.3118 | 1200668.8953 | 2777901.2274 | 1200656.9334
1 | 2777898.1364 | 1200775.5418 | 2777899.481 | 1200774.6476 | 2777900.443 | 1200773.553 | 2777901.0662 | 1200772.0701 | 2777908.2246 | 1200783.6723 | 2777911.2659 | 1200787.1996 | 2777915.022 | 1200790.2588 | 2777920.0562 | 1200793.1226 | 2777922.8493 | 1200795.0076 | 2777924.9388 | 1200796.727 | 2777931.5211 | 1200802.3507 | 2777935.8976 | 1200805.8066 | 2777939.1047 | 1200808.3712 | 2777942.0507 | 1200810.2385 | 2777947.5065 | 1200813.0148
2 | 2777900.7397 | 1200646.9938 | 2777900.7751 | 1200651.9441 | 2777901.2274 | 1200656.9334
3 | 2777898.1364 | 1200775.5418 | 2777896.4112 | 1200776.1689 | 2777895.1407 | 1200776.3646 | 2777893.7708 | 1200776.4748
4 | 2777898.1364 | 1200775.5418 | 2777898.6268 | 1200778.7707 | 2777899.0146 | 1200784.9327 | 2777893.406 | 1200791.8837 | 2777892.3896 | 1200805.2887 | 2777895.2259 | 1200820.0431 | 2777900.0757 | 1200826.2824 | 2777908.3514 | 1200829.7878 | 2777933.5292 | 1200837.4781 | 2777954.6768 | 1200845.4266 | 2777972.629 | 1200851.4448 | 2777975.4696 | 1200853.0571
5 | 2777900.7397 | 1200646.9938 | 2777900.1529 | 1200637.9351
6 | 2777588.7648 | 1200645.8594 | 2777598.026 | 1200637.2484 | 2777618.8053 | 1200630.7262 | 2777640.358 | 1200625.862 | 2777660.7386 | 1200620.963 | 2777675.5422 | 1200617.8667 | 2777682.4583 | 1200617.1494 | 2777688.7102 | 1200616.7348 | 2777692.2269 | 1200616.0721 | 2777694.7937 | 1200614.8138 | 2777697.0146 | 1200612.6333 | 2777697.9419 | 1200609.8915 | 2777698.004 | 1200606.5234 | 2777697.21 | 1200603.508 | 2777705.9941 | 1200605.3042 | 2777712.4119 | 1200606.9967 | 2777715.625 | 1200607.5705 | 2777718.3987 | 1200607.553 | 2777722.3165 | 1200606.98 | 2777725.5333 | 1200605.8969 | 2777732.4643 | 1200603.6563 | 2777735.8095 | 1200603.122 | 2777740.9538 | 1200602.2963 | 2777744.7799 | 1200601.476 | 2777759.5229 | 1200596.5763 | 2777762.9979 | 1200595.7789 | 2777766.6112 | 1200595.4527 | 2777773.2613 | 1200595.7397 | 2777777.1416 | 1200595.1434 | 2777780.884 | 1200594.0648 | 2777789.4503 | 1200590.1269 | 2777793.1092 | 1200589.0346 | 2777797.6532 | 1200588.4136 | 2777802.0184 | 1200588.4213 | 2777808.7026 | 1200588.8428 | 2777815.4149 | 1200589.3429 | 2777819.4393 | 1200590.308 | 2777822.0399 | 1200591.7535 | 2777828.0714 | 1200595.9259 | 2777833.4302 | 1200600.4342 | 2777835.8458 | 1200602.9752 | 2777855.8797 | 1200623.0242 | 2777881.6319 | 1200648.0372 | 2777884.5124 | 1200649.5467 | 2777887.8209 | 1200650.2458 | 2777891.1588 | 1200649.7002 | 2777900.7397 | 1200646.9938
7 | 2777875.7162 | 1200775.7748 | 2777893.7279 | 1200776.4782 | 2777893.7708 | 1200776.4748
8 | 2777968.8663 | 1201257.0181 | 2777941.9905 | 1201243.2265 | 2777902.7588 | 1201234.8447
9 | 2777968.8663 | 1201257.0181 | 2777927.9635 | 1201334.9995
10 | 2777902.7588 | 1201234.8447 | 2777838.8854 | 1200864.3986
11 | 2777902.7588 | 1201234.8447 | 2778047.6974 | 1200431.3947
12 | 2777349.2981 | 1201390.4633 | 2777352.5514 | 1201388.647 | 2777362.9342 | 1201388.3882 | 2777380.432 | 1201390.9434 | 2777394.9652 | 1201389.9515 | 2777416.6229 | 1201383.2546 | 2777429.0196 | 1201378.5403 | 2777446.5176 | 1201374.1667 | 2777459.0959 | 1201377.1875 | 2777472.7845 | 1201384.1119 | 2777484.4862 | 1201388.9419 | 2777494.0107 | 1201391.6719 | 2777507.2853 | 1201390.2314 | 2777518.6008 | 1201389.3444
13 | 2777349.2981 | 1201390.4633 | 2777348.6472 | 1201394.1698 | 2777351.1945 | 1201398.4274 | 2777365.3376 | 1201402.1062 | 2777373.5341 | 1201408.2555 | 2777382.1028 | 1201417.2631 | 2777391.6995 | 1201429.3597 | 2777397.4984 | 1201442.3667 | 2777404.0039 | 1201457.2299 | 2777411.7469 | 1201471.7183 | 2777426.2748 | 1201489.8674 | 2777442.0304 | 1201504.3827 | 2777446.0939 | 1201506.2767
14 | 2777349.2981 | 1201390.4633 | 2777328.658 | 1201386.7583 | 2777310.3521 | 1201383.968 | 2777296.4578 | 1201383.9669 | 2777288.2974 | 1201385.321
15 | 2777288.2974 | 1201385.321 | 2777228.6353 | 1201216.7701
16 | 2777850.5607 | 1200801.5958 | 2777876.91 | 1200836.2026 | 2777873.3901 | 1200844.6506 | 2777838.8854 | 1200864.3986
17 | 2777228.6353 | 1201216.7701 | 2777216.4722 | 1201213.3505 | 2777195.7501 | 1201211.1005 | 2777182.884 | 1201209.2951
18 | 2778155.727 | 1200779.9411 | 2778136.3752 | 1200743.7178 | 2778109.1639 | 1200687.474 | 2778090.3915 | 1200652.4916 | 2778069.2475 | 1200631.3743 | 2778067.8039 | 1200629.86
19 | 2778053.4181 | 1200614.7706 | 2778067.8039 | 1200629.86
20 | 2777241.4403 | 1200950.1569 | 2777160.6922 | 1200927.4406 | 2777148.255 | 1200922.7118 | 2777133.1354 | 1200914.7553
21 | 2777412.7292 | 1200977.4657 | 2777358.1655 | 1200980.9051 | 2777343.109 | 1200981.5256 | 2777329.9761 | 1200980.7351 | 2777320.4486 | 1200979.1064 | 2777301.7436 | 1200975.3478 | 2777284.9694 | 1200969.678 | 2777241.4403 | 1200950.1569
22 | 2777324.8993 | 1200803.0782 | 2777241.4403 | 1200950.1569
23 | 2777174.8298 | 1201206.0862 | 2777241.4403 | 1200950.1569
24 | 2777118.0633 | 1200906.8238 | 2777133.1354 | 1200914.7553
25 | 2777535.3544 | 1201004.4667 | 2777511.337 | 1201008.2347 | 2777490.0287 | 1201010.0481 | 2777471.7214 | 1201007.2684 | 2777452.4671 | 1200995.0848 | 2777429.1089 | 1200983.5912 | 2777412.7292 | 1200977.4657
26 | 2777324.8993 | 1200803.0782 | 2777318.6439 | 1200795.1515 | 2777316.4226 | 1200787.3447 | 2777308.0453 | 1200752.8737 | 2777305.7965 | 1200744.4543 | 2777298.237 | 1200739.136
27 | 2777174.8298 | 1201206.0862 | 2777182.884 | 1201209.2951 | 2777182.884 | 1201209.2951
28 | 2777118.0633 | 1200906.8238 | 2777115.7685 | 1200899.9491 | 2777112.2419 | 1200892.7375 | 2777110.9073 | 1200889.7061 | 2777108.3398 | 1200886.6271 | 2777104.5063 | 1200883.5994 | 2777097.7646 | 1200880.7249
29 | 2777570.505 | 1200792.1241 | 2777535.3544 | 1201004.4667
30 | 2777482.8724 | 1200790.2547 | 2777498.3693 | 1200796.6211 | 2777516.9594 | 1200803.491 | 2777531.3376 | 1200802.8953 | 2777553.716 | 1200797.655 | 2777567.1513 | 1200794.1841 | 2777570.505 | 1200792.1241
31 | 2777588.7648 | 1200645.8594 | 2777589.1819 | 1200663.6002 | 2777574.5266 | 1200678.3681 | 2777533.4985 | 1200693.3194 | 2777528.1766 | 1200699.8677 | 2777527.6128 | 1200714.9879 | 2777530.0753 | 1200728.5075 | 2777542.3594 | 1200746.59 | 2777557.05 | 1200755.9912 | 2777573.813 | 1200760.7716 | 2777584.0367 | 1200769.2281 | 2777585.1361 | 1200778.6255 | 2777579.1716 | 1200786.8007 | 2777570.505 | 1200792.1241
32 | 2777282.2975 | 1200735.4374 | 2777279.1096 | 1200734.6977 | 2777269.7941 | 1200733.6092 | 2777263.0215 | 1200727.7026 | 2777259.4553 | 1200717.2088 | 2777246.803 | 1200702.7751 | 2777243.0445 | 1200699.5271 | 2777237.31 | 1200696.632 | 2777193.188 | 1200677.761 | 2777176.6324 | 1200670.3408 | 2777176.3947 | 1200670.2159
33 | 2777298.237 | 1200739.136 | 2777282.2975 | 1200735.4374
34 | 2777129.678 | 1200630.5993 | 2777133.0396 | 1200638.2397 | 2777137.4202 | 1200644.9204 | 2777140.7747 | 1200648.1786 | 2777147.0295 | 1200653.825 | 2777158.0736 | 1200660.5923 | 2777176.3947 | 1200670.2159
35 | 2777129.678 | 1200630.5993 | 2777140.8812 | 1200628.1512 | 2777209.6809 | 1200617.4691 | 2777215.9136 | 1200616.9312 | 2777229.8727 | 1200617.6346 | 2777247.4094 | 1200619.4676 | 2777259.8235 | 1200619.0909 | 2777270.227 | 1200618.0922
36 | 2777270.227 | 1200618.0922 | 2777293.0718 | 1200615.8993
37 | 2777525.0402 | 1200576.2763 | 2777531.8141 | 1200577.0116 | 2777536.8598 | 1200578.2182 | 2777542.4315 | 1200579.9298 | 2777550.4555 | 1200582.693 | 2777555.4807 | 1200584.077 | 2777560.3592 | 1200585.0117 | 2777566.4143 | 1200585.5811 | 2777571.3237 | 1200586.2498 | 2777575.8431 | 1200587.2183 | 2777605.4177 | 1200594.671 | 2777625.8864 | 1200599.1058 | 2777633.4404 | 1200600.2537 | 2777639.3442 | 1200600.7852 | 2777646.6224 | 1200600.9572 | 2777654.4728 | 1200600.846 | 2777662.6115 | 1200600.2651 | 2777670.7323 | 1200599.2611 | 2777680.0373 | 1200598.4036 | 2777684.3571 | 1200598.3986 | 2777688.3477 | 1200598.7065 | 2777691.4954 | 1200599.4341 | 2777694.4759 | 1200600.6572 | 2777696.1142 | 1200601.9294 | 2777697.21 | 1200603.508 | 2777698.004 | 1200606.5234 | 2777697.9419 | 1200609.8915 | 2777697.0146 | 1200612.6333 | 2777694.7937 | 1200614.8138 | 2777692.2269 | 1200616.0721 | 2777688.7102 | 1200616.7348 | 2777682.4583 | 1200617.1494 | 2777675.5422 | 1200617.8667 | 2777660.7386 | 1200620.963 | 2777640.358 | 1200625.862 | 2777618.8053 | 1200630.7262 | 2777598.026 | 1200637.2484 | 2777588.7648 | 1200645.8594
38 | 2777525.0402 | 1200576.2763 | 2777510.8435 | 1200576.8997 | 2777505.541 | 1200576.3862 | 2777500.43 | 1200575.3222 | 2777496.2487 | 1200573.9968 | 2777488.2117 | 1200570.1321 | 2777486.0711 | 1200569.3567 | 2777483.3976 | 1200568.5654 | 2777466.8516 | 1200565.4377 | 2777460.0184 | 1200564.1336 | 2777453.2036 | 1200561.9513 | 2777449.1166 | 1200560.2728 | 2777445.4664 | 1200558.5072 | 2777441.9291 | 1200556.2778 | 2777422.9616 | 1200541.3112 | 2777419.9762 | 1200538.709 | 2777417.6938 | 1200536.2944 | 2777416.1392 | 1200534.0016 | 2777415.0905 | 1200531.6015 | 2777414.4288 | 1200529.0015 | 2777414.1234 | 1200525.6892 | 2777414.2363 | 1200517.1361
39 | 2777322.5889 | 1200595.2736 | 2777345.9479 | 1200606.8783 | 2777348.0529 | 1200613.4694 | 2777342.009 | 1200619.1957 | 2777329.906 | 1200620.3822 | 2777308.3165 | 1200614.4359 | 2777293.0718 | 1200615.8993
40 | 2777414.2363 | 1200517.1361 | 2777414.6168 | 1200488.3119 | 2777414.549 | 1200483.9279 | 2777414.1492 | 1200479.4338 | 2777413.3433 | 1200474.7609 | 2777411.5928 | 1200468.8032 | 2777409.2836 | 1200462.4173 | 2777406.4627 | 1200456.0718 | 2777403.1239 | 1200449.4663 | 2777400.1191 | 1200444.4389 | 2777388.0168 | 1200428.0401
41 | 2777769.8173 | 1200475.2197 | 2777771.8362 | 1200479.5729 | 2777774.5203 | 1200483.0783 | 2777778.1423 | 1200486.5561 | 2777789.7563 | 1200494.6428 | 2777796.1798 | 1200499.2161 | 2777799.774 | 1200502.6041 | 2777807.8477 | 1200511.3751
42 | 2777807.8477 | 1200511.3751 | 2777804.4799 | 1200512.9208 | 2777799.0735 | 1200514.6172 | 2777793.7574 | 1200515.5822 | 2777789.0115 | 1200516.0749 | 2777784.4973 | 1200515.9516 | 2777774.8374 | 1200513.8637
43 | 2777769.8173 | 1200475.2197 | 2777766.3622 | 1200475.6062 | 2777762.2974 | 1200475.4852 | 2777752.3058 | 1200473.8086
44 | 2777769.8173 | 1200475.2197 | 2777770.3296 | 1200474.3897 | 2777771.9735 | 1200472.4033 | 2777772.78 | 1200471.4152
45 | 2777768.1461 | 1200512.4174 | 2777774.8374 | 1200513.8637
46 | 2777883.1169 | 1200549.3406 | 2777884.2279 | 1200562.4309 | 2777892.2174 | 1200589.3617 | 2777899.4612 | 1200627.2587 | 2777900.1529 | 1200637.9351
47 | 2777883.1169 | 1200549.3406 | 2777882.6497 | 1200542.0085 | 2777886.5752 | 1200529.6688
48 | 2777886.5752 | 1200529.6688 | 2777894.4517 | 1200532.8958
49 | 2777886.5752 | 1200529.6688 | 2777879.6621 | 1200527.2576
50 | 2777322.5889 | 1200595.2736 | 2777308.1384 | 1200588.0945
51 | 2777297.568 | 1200548.4528 | 2777288.2534 | 1200545.5292 | 2777284.7883 | 1200538.2972 | 2777285.0665 | 1200528.9297 | 2777283.0324 | 1200521.7401 | 2777278.2205 | 1200519.5842
52 | 2777278.2205 | 1200519.5842 | 2777274.5574 | 1200528.2617
53 | 2777206.427 | 1200551.008 | 2777209.1799 | 1200539.1114 | 2777205.9973 | 1200525.1812 | 2777207.2266 | 1200514.3071 | 2777215.9772 | 1200512.8763 | 2777237.167 | 1200517.9317 | 2777254.1925 | 1200521.0841 | 2777261.0773 | 1200524.7585 | 2777274.5574 | 1200528.2617
54 | 2777274.5574 | 1200528.2617 | 2777273.5046 | 1200545.7587 | 2777280.5069 | 1200562.2231
55 | 2777280.5069 | 1200562.2231 | 2777280.6474 | 1200562.5535 | 2777294.1367 | 1200581.1384 | 2777308.1384 | 1200588.0945
56 | 2777206.427 | 1200551.008 | 2777214.075 | 1200552.0691 | 2777215.3177 | 1200552.2331
57 | 2777218.253 | 1200552.6204 | 2777215.3177 | 1200552.2331
58 | 2777218.253 | 1200552.6204 | 2777229.951 | 1200554.1641 | 2777239.8155 | 1200559.3506
59 | 2777850.5607 | 1200801.5958 | 2777836.9029 | 1200792.8364 | 2777813.4033 | 1200785.8304 | 2777810.7005 | 1200780.656
60 | 2777850.5607 | 1200801.5958 | 2777849.2469 | 1200790.9686 | 2777855.0963 | 1200784.6253 | 2777875.7162 | 1200775.7748
61 | 2778041.471 | 1200602.2936 | 2778041.6035 | 1200602.378 | 2778053.4181 | 1200614.7706
62 | 2778041.471 | 1200602.2936 | 2778022.5559 | 1200590.2369
63 | 2778022.5559 | 1200590.2369 | 2778000.6919 | 1200576.3007 | 2777983.681 | 1200570.115
64 | 2777913.7592 | 1200540.806 | 2777894.4517 | 1200532.8958
65 | 2777879.6621 | 1200527.2576 | 2777875.8533 | 1200525.9291
66 | 2777913.7592 | 1200540.806 | 2777920.2426 | 1200543.4622 | 2777921.2419 | 1200543.9636
67 | 2777848.3985 | 1200516.3531 | 2777875.8533 | 1200525.9291
68 | 2777848.3985 | 1200516.3531 | 2777796.1645 | 1200489.7509 | 2777786.7286 | 1200483.9979 | 2777780.8339 | 1200479.5738 | 2777772.78 | 1200471.4152
69 | 2777772.78 | 1200471.4152 | 2777766.219 | 1200464.0351 | 2777761.6607 | 1200458.2272 | 2777761.1825 | 1200457.5466
70 | 2777848.3985 | 1200516.3531 | 2777862.7394 | 1200512.1757 | 2777881.348 | 1200504.8891 | 2777888.1743 | 1200503.869
71 | 2777744.7351 | 1200431.4978 | 2777748.7812 | 1200437.8799 | 2777757.5822 | 1200452.4225 | 2777761.1825 | 1200457.5466
72 | 2777729.2943 | 1200415.8011 | 2777726.2831 | 1200410.4362
73 | 2777729.2943 | 1200415.8011 | 2777732.2948 | 1200418.404 | 2777735.5985 | 1200421.572 | 2777742.4557 | 1200428.4715
74 | 2777729.2943 | 1200415.8011 | 2777722.7918 | 1200411.3145 | 2777716.7517 | 1200407.9316 | 2777708.1202 | 1200404.0712 | 2777687.4293 | 1200396.224
75 | 2777742.4557 | 1200428.4715 | 2777739.3971 | 1200430.3824 | 2777735.6722 | 1200431.8953 | 2777734.7608 | 1200435.1269 | 2777734.4643 | 1200438.1766 | 2777732.9277 | 1200441.423 | 2777721.8772 | 1200449.2131 | 2777711.8768 | 1200455.255
76 | 2777742.4557 | 1200428.4715 | 2777744.7351 | 1200431.4978
77 | 2777888.1743 | 1200503.869 | 2777894.9367 | 1200503.9704 | 2777903.7225 | 1200504.9439 | 2777911.3874 | 1200506.4624 | 2777917.1913 | 1200508.4711
78 | 2777921.2419 | 1200543.9636 | 2777938.2535 | 1200552.5004
79 | 2777959.7993 | 1200561.431 | 2777953.9478 | 1200559.3033 | 2777942.7918 | 1200554.7778 | 2777938.2535 | 1200552.5004
80 | 2777959.7993 | 1200561.431 | 2777981.9544 | 1200569.4872
81 | 2777981.9544 | 1200569.4872 | 2777983.681 | 1200570.115
82 | 2777917.1913 | 1200508.4711 | 2777939.6978 | 1200516.2605
83 | 2777939.6978 | 1200516.2605 | 2777958.4882 | 1200522.7638
84 | 2777958.4882 | 1200522.7638 | 2777975.7137 | 1200528.7255

## bus_geodata
| x | y | coords
0 | 2777947.5065 | 1200813.0148
1 | 2777901.2274 | 1200656.9334
2 | 2777898.1364 | 1200775.5418
3 | 2777900.7397 | 1200646.9938
4 | 2777893.7708 | 1200776.4748
5 | 2777975.4696 | 1200853.0571
6 | 2777968.8663 | 1201257.0181
7 | 2777902.7588 | 1201234.8447
8 | 2777927.9635 | 1201334.9995
9 | 2777518.6008 | 1201389.3444
10 | 2777349.2981 | 1201390.4633
11 | 2777446.0939 | 1201506.2767
12 | 2777288.2974 | 1201385.321
13 | 2777838.8854 | 1200864.3986
14 | 2778047.6973 | 1200431.3947
15 | 2777228.6353 | 1201216.7701
16 | 2778155.727 | 1200779.9411
17 | 2778067.8039 | 1200629.86
18 | 2777241.4403 | 1200950.1569
19 | 2777133.1354 | 1200914.7553
20 | 2777412.7292 | 1200977.4657
21 | 2777324.8993 | 1200803.0782
22 | 2777174.8298 | 1201206.0862
23 | 2777118.0633 | 1200906.8238
24 | 2777535.3544 | 1201004.4667
25 | 2777097.7646 | 1200880.7249
26 | 2777570.505 | 1200792.1241
27 | 2777182.884 | 1201209.2951
28 | 2777282.2975 | 1200735.4374
29 | 2777176.3947 | 1200670.2159
30 | 2777298.237 | 1200739.136
31 | 2777129.678 | 1200630.5993
32 | 2777270.227 | 1200618.0922
33 | 2777588.7648 | 1200645.8594
34 | 2777525.0402 | 1200576.2763
35 | 2777293.0718 | 1200615.8993
36 | 2777482.8724 | 1200790.2547
37 | 2777414.2363 | 1200517.1361
38 | 2777807.8477 | 1200511.3751
39 | 2777769.8173 | 1200475.2197
40 | 2777774.8374 | 1200513.8637
41 | 2777900.1529 | 1200637.9351
42 | 2777883.1169 | 1200549.3406
43 | 2777886.5752 | 1200529.6688
44 | 2777322.589 | 1200595.2736
45 | 2777388.0168 | 1200428.0401
46 | 2777278.2205 | 1200519.5842
47 | 2777297.568 | 1200548.4528
48 | 2777274.5574 | 1200528.2617
49 | 2777308.1384 | 1200588.0945
50 | 2777280.5069 | 1200562.2231
51 | 2777206.427 | 1200551.008
52 | 2777215.3177 | 1200552.2331
53 | 2777218.253 | 1200552.6204
54 | 2777239.8155 | 1200559.3506
55 | 2777810.7005 | 1200780.656
56 | 2777850.5607 | 1200801.5958
57 | 2777875.7162 | 1200775.7748
58 | 2778053.4181 | 1200614.7706
59 | 2778041.471 | 1200602.2936
60 | 2778022.5559 | 1200590.2369
61 | 2777894.4517 | 1200532.8958
62 | 2777879.6621 | 1200527.2576
63 | 2777913.7592 | 1200540.806
64 | 2777875.8533 | 1200525.9291
65 | 2777768.1461 | 1200512.4174
66 | 2777752.3058 | 1200473.8086
67 | 2777772.78 | 1200471.4152
68 | 2777848.3985 | 1200516.3531
69 | 2777761.1825 | 1200457.5466
70 | 2777726.2831 | 1200410.4362
71 | 2777729.2943 | 1200415.8011
72 | 2777687.4293 | 1200396.224
73 | 2777742.4557 | 1200428.4715
74 | 2777711.8768 | 1200455.255
75 | 2777744.7351 | 1200431.4978
76 | 2777888.1743 | 1200503.869
77 | 2777921.2419 | 1200543.9636
78 | 2777938.2535 | 1200552.5004
79 | 2777959.7993 | 1200561.431
80 | 2777981.9544 | 1200569.4872
81 | 2777983.681 | 1200570.115
82 | 2777917.1913 | 1200508.4711
83 | 2777939.6978 | 1200516.2605
84 | 2777958.4882 | 1200522.7638
85 | 2777975.7137 | 1200528.7254
86 | 2777525.0402 | 1200576.2763

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1