## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3961-14_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3961-14_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3961-14_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3961-14_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3961-14_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_3961-14_0_2_node_17 | 0.4 | n |  | TRUE
6 | bus_LV_3961-14_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_3961-14_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_3961-14_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_3961-14_0_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_3961-14_0_2_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_3961-14_0_2_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_3961-14_0_2_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_3961-14_0_2_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_3961-14_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_3961-14_0_2_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_3961-14_0_2_node_103 | 0.4 | n |  | TRUE
17 | bus_LV_3961-14_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_3961-14_0_2_node_113 | 0.4 | n |  | TRUE
19 | bus_LV_3961-14_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_3961-14_0_2_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_3961-14_0_2_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_3961-14_0_2_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_3961-14_0_2_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_3961-14_0_2_node_110 | 0.4 | n |  | TRUE
25 | bus_LV_3961-14_0_2_node_108 | 0.4 | n |  | TRUE
26 | bus_LV_3961-14_0_2_node_114 | 0.4 | n |  | TRUE
27 | bus_LV_3961-14_0_2_node_98 | 0.4 | n |  | TRUE
28 | bus_LV_3961-14_0_2_node_99 | 0.4 | n |  | TRUE
29 | bus_LV_3961-14_0_2_node_100 | 0.4 | n |  | TRUE
30 | bus_LV_3961-14_0_2_node_101 | 0.4 | n |  | TRUE
31 | bus_LV_3961-14_0_2_node_102 | 0.4 | n |  | TRUE
32 | bus_LV_3961-14_0_2_node_104 | 0.4 | n |  | TRUE
33 | bus_LV_3961-14_0_2_node_105 | 0.4 | n |  | TRUE
34 | bus_LV_3961-14_0_2_node_106 | 0.4 | n |  | TRUE
35 | bus_LV_3961-14_0_2_node_107 | 0.4 | n |  | TRUE
36 | bus_LV_3961-14_0_2_node_111 | 0.4 | n |  | TRUE
37 | bus_LV_3961-14_0_2_node_112 | 0.4 | n |  | TRUE
38 | bus_MV_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3961-14_0_2_load_0 | 0 | 0.0018635 | 0.00046704 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3961-14_0_2_load_1 | 1 | 0.0015939 | 0.00039947 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3961-14_0_2_load_2 | 2 | 0.0067184 | 0.0016838 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3961-14_0_2_load_3 | 3 | 0.00063171 | 0.00015832 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3961-14_0_2_load_17 | 5 | 0.00022136 | 5.5478e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3961-14_0_2_load_4 | 6 | 0.010785 | 0.002703 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3961-14_0_2_load_5 | 7 | 0.00066719 | 0.00016721 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3961-14_0_2_load_7 | 8 | 0.0023932 | 0.00059978 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3961-14_0_2_load_8 | 9 | 0.00091354 | 0.00022896 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3961-14_0_2_load_9 | 10 | 0.0015383 | 0.00038552 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3961-14_0_2_load_12 | 11 | 0.0015755 | 0.00039485 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3961-14_0_2_load_11 | 12 | 0.001334 | 0.00033433 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3961-14_0_2_load_13 | 13 | 0.001615 | 0.00040475 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3961-14_0_2_load_15 | 15 | 0.00071318 | 0.00017874 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3961-14_0_2_load_103 | 16 | 0.0028497 | 0.00071419 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3961-14_0_2_load_16 | 17 | 0.00098243 | 0.00024622 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3961-14_0_2_load_113 | 18 | 0.00088779 | 0.0002225 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3961-14_0_2_load_18 | 19 | 0.00037876 | 9.4926e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3961-14_0_2_load_19 | 20 | 0.00090239 | 0.00022616 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3961-14_0_2_load_23 | 22 | 0.00044665 | 0.00011194 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3961-14_0_2_load_108 | 25 | 0.0004101 | 0.00010278 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3961-14_0_2_load_114 | 26 | 0.00071969 | 0.00018037 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3961-14_0_2_load_98 | 27 | 0.00030099 | 7.5435e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3961-14_0_2_load_101 | 30 | 0.0014682 | 0.00036797 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3961-14_0_2_load_104 | 32 | 0.00070569 | 0.00017686 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3961-14_0_2_load_105 | 33 | 0.00066504 | 0.00016667 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3961-14_0_2_load_106 | 34 | 0.00065317 | 0.0001637 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3961-14_0_2_load_107 | 35 | 0.00048329 | 0.00012112 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3961-14_0_2_load_111 | 36 | 0.00030232 | 7.5768e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3961-14_0_2_load_112 | 37 | 0.00046913 | 0.00011757 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3961-14_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.17059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3961-14_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.040791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3961-14_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.041415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3961-14_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.16359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3961-14_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.10725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3961-14_0_2_line_5 | NAYY 4x150 SE | 4 | 9 | 0.18601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3961-14_0_2_line_6 | NAYY 4x150 SE | 4 | 10 | 0.061752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3961-14_0_2_line_7 | NAYY 4x150 SE | 4 | 6 | 0.12495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3961-14_0_2_line_8 | NAYY 4x150 SE | 5 | 19 | 0.040899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3961-14_0_2_line_9 | NAYY 4x150 SE | 6 | 7 | 0.18539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3961-14_0_2_line_10 | NAYY 4x150 SE | 7 | 8 | 0.029386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3961-14_0_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.099057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3961-14_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.010786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3961-14_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.13767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3961-14_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.23479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3961-14_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.02583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3961-14_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.12122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3961-14_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.073865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3961-14_0_2_line_18 | NAYY 4x150 SE | 16 | 31 | 0.029705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3961-14_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.22699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3961-14_0_2_line_20 | NAYY 4x150 SE | 18 | 26 | 0.042875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3961-14_0_2_line_21 | NAYY 4x150 SE | 18 | 37 | 0.22124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3961-14_0_2_line_22 | NAYY 4x150 SE | 19 | 20 | 0.03367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3961-14_0_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.010456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3961-14_0_2_line_24 | NAYY 4x150 SE | 21 | 23 | 0.1149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3961-14_0_2_line_25 | NAYY 4x150 SE | 22 | 26 | 0.018996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3961-14_0_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.2797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3961-14_0_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.35823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3961-14_0_2_line_28 | NAYY 4x150 SE | 24 | 36 | 0.088338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3961-14_0_2_line_29 | NAYY 4x150 SE | 25 | 35 | 0.15582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3961-14_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.11622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3961-14_0_2_line_31 | NAYY 4x150 SE | 27 | 29 | 0.044707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3961-14_0_2_line_32 | NAYY 4x150 SE | 28 | 30 | 0.012431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3961-14_0_2_line_33 | NAYY 4x150 SE | 29 | 31 | 0.015794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3961-14_0_2_line_34 | NAYY 4x150 SE | 31 | 32 | 0.02494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3961-14_0_2_line_35 | NAYY 4x150 SE | 32 | 33 | 0.023275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3961-14_0_2_line_36 | NAYY 4x150 SE | 33 | 34 | 0.0070616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3961-14_0_2_trafo_8 | 0.25 MVA 20/0.4 kV | 38 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2767127.2031 | 1204753.2206 | 2767120.3007 | 1204754.5563 | 2767106.7498 | 1204750.7736 | 2767089.7315 | 1204735.1607 | 2767075.4411 | 1204730.6011 | 2767025.4738 | 1204739.801 | 2767011.479 | 1204738.2749 | 2766967.4254 | 1204723.3648
1 | 2766967.4254 | 1204723.3648 | 2766935.9322 | 1204712.7057 | 2766928.3892 | 1204712.7252
2 | 2766928.3892 | 1204712.7252 | 2766886.9739 | 1204712.8321
3 | 2766983.1196 | 1204558.5591 | 2766928.3892 | 1204712.7252
4 | 2766780.8715 | 1204725.2715 | 2766824.0508 | 1204715.9716 | 2766854.023 | 1204712.9171 | 2766886.9739 | 1204712.8321
5 | 2766983.1196 | 1204558.5591 | 2766918.4272 | 1204565.068 | 2766839.3564 | 1204543.1939 | 2766813.6299 | 1204513.3476
6 | 2766983.1196 | 1204558.5591 | 2767003.2498 | 1204517.1389 | 2767009.0404 | 1204502.5466
7 | 2766983.1196 | 1204558.5591 | 2767006.5082 | 1204563.373 | 2767032.699 | 1204576.5955 | 2767060.1477 | 1204572.0701 | 2767078.5102 | 1204553.2885 | 2767094.9435 | 1204546.8597
8 | 2766740.6095 | 1204732.2586 | 2766760.1549 | 1204729.7334 | 2766780.8715 | 1204725.2715
9 | 2767094.9435 | 1204546.8597 | 2767111.8848 | 1204540.2322 | 2767136.6581 | 1204536.3774 | 2767163.7364 | 1204545.0877 | 2767195.1316 | 1204548.6142 | 2767251.407 | 1204530.8955 | 2767273.9724 | 1204525.9841
10 | 2767302.7216 | 1204519.9567 | 2767300.6578 | 1204520.1759 | 2767273.9724 | 1204525.9841
11 | 2766813.6299 | 1204513.3476 | 2766827.2703 | 1204415.2346
12 | 2767013.0187 | 1204492.521 | 2767009.0404 | 1204502.5466
13 | 2766827.2703 | 1204415.2346 | 2766804.4808 | 1204417.7031 | 2766742.3148 | 1204408.4032 | 2766711.0377 | 1204391.6256 | 2766695.4812 | 1204386.4468
14 | 2766468.2727 | 1204330.6425 | 2766479.2053 | 1204334.9957 | 2766546.7148 | 1204357.4541 | 2766666.9123 | 1204376.9361 | 2766695.4812 | 1204386.4468
15 | 2766468.2727 | 1204330.6425 | 2766457.3046 | 1204354.0283
16 | 2766523.1785 | 1204222.5727 | 2766468.2727 | 1204330.6425
17 | 2766460.2245 | 1204423.7491 | 2766447.2911 | 1204389.6014 | 2766450.3193 | 1204368.9222 | 2766457.3046 | 1204354.0283
18 | 2766508.7427 | 1204197.7917 | 2766509.0485 | 1204204.8401 | 2766523.1785 | 1204222.5727
19 | 2766460.2245 | 1204423.7491 | 2766256.5653 | 1204523.9872
20 | 2766256.5653 | 1204523.9872 | 2766249.0154 | 1204517.1198 | 2766233.9065 | 1204506.9232 | 2766221.0046 | 1204500.4348
21 | 2766373.4177 | 1204707.8831 | 2766369.131 | 1204701.6357 | 2766365.2541 | 1204690.5174 | 2766360.3288 | 1204675.4996 | 2766356.9117 | 1204664.8167 | 2766329.5131 | 1204633.4467 | 2766312.4082 | 1204611.5723 | 2766303.0503 | 1204600.9908 | 2766299.0189 | 1204595.6848 | 2766295.948 | 1204590.3276 | 2766293.1618 | 1204582.1313 | 2766288.6147 | 1204568.5588 | 2766280.6318 | 1204552.0657 | 2766271.3325 | 1204538.2829 | 2766261.9565 | 1204528.891 | 2766256.5653 | 1204523.9872
22 | 2766707.2168 | 1204736.573 | 2766740.6095 | 1204732.2586
23 | 2766197.2829 | 1204483.916 | 2766204.0338 | 1204491.9001
24 | 2766197.2829 | 1204483.916 | 2766187.5982 | 1204477.6741 | 2766179.3825 | 1204469.5268 | 2766167.8083 | 1204455.1359 | 2766158.0427 | 1204438.6712 | 2766144.5678 | 1204415.1635 | 2766140.9897 | 1204409.9702 | 2766137.3079 | 1204406.5869 | 2766133.8165 | 1204405.3887 | 2766130.3924 | 1204405.6047 | 2766126.7493 | 1204407.9389 | 2766124.7913 | 1204411.8214
25 | 2766221.0046 | 1204500.4348 | 2766204.0338 | 1204491.9001 | 2766204.0338 | 1204491.9001
26 | 2765922.8888 | 1204425.5776 | 2765928.432 | 1204431.8373 | 2765935.1184 | 1204462.963 | 2765945.7641 | 1204462.0357 | 2765954.8686 | 1204450.2778 | 2765965.2277 | 1204444.8717 | 2765972.9906 | 1204444.6761 | 2765980.7174 | 1204453.4434 | 2765988.8155 | 1204448.5862 | 2765990.5696 | 1204451.4821 | 2765995.2274 | 1204445.506 | 2766002.0688 | 1204449.155 | 2765998.5791 | 1204457.1988 | 2766002.4697 | 1204464.0244 | 2766017.2212 | 1204455.0706 | 2766053.2232 | 1204423.2975 | 2766091.4629 | 1204413.9854 | 2766124.7913 | 1204411.8214
27 | 2766124.7913 | 1204411.8214 | 2766124.1545 | 1204416.3746 | 2766128.258 | 1204434.9615 | 2766149.3146 | 1204491.0325 | 2766153.361 | 1204504.5576 | 2766153.9062 | 1204510.6784 | 2766153.1996 | 1204516.6421 | 2766149.0904 | 1204527.7937 | 2766147.4673 | 1204533.0423 | 2766146.3863 | 1204538.7842 | 2766146.6053 | 1204545.6856 | 2766147.6692 | 1204552.5882 | 2766149.9902 | 1204559.7261 | 2766153.4024 | 1204567.595 | 2766164.1879 | 1204583.5098 | 2766178.4294 | 1204603.8026 | 2766200.1064 | 1204639.7391 | 2766211.1835 | 1204649.2784 | 2766220.688 | 1204660.064 | 2766223.1383 | 1204673.4891 | 2766217.5942 | 1204688.8713 | 2766209.9435 | 1204693.7963 | 2766191.5923 | 1204702.9942 | 2766173.5166 | 1204712.9671
28 | 2765958.6161 | 1204359.5979 | 2765946.3157 | 1204368.8314 | 2765945.948 | 1204389.1734 | 2765925.4912 | 1204397.9687 | 2765918.9551 | 1204405.5164 | 2765922.8888 | 1204425.5776
29 | 2766093.7176 | 1204669.4388 | 2766107.7523 | 1204690.2723 | 2766125.8979 | 1204723.4522 | 2766136.3021 | 1204749.4991 | 2766144.6553 | 1204756.2488 | 2766150.9721 | 1204751.1086 | 2766152.785 | 1204745.0535 | 2766159.0577 | 1204725.6433 | 2766173.5166 | 1204712.9671
30 | 2766625.1818 | 1204099.5141 | 2766626.5387 | 1204123.174 | 2766585.548 | 1204163.0232 | 2766560.2011 | 1204187.6614
31 | 2766517.1639 | 1204185.2037 | 2766537.161 | 1204191.3002 | 2766548.7401 | 1204191.868 | 2766560.2011 | 1204187.6614
32 | 2766637.061 | 1204098.3333 | 2766630.7977 | 1204097.1575 | 2766625.1818 | 1204099.5141
33 | 2766517.1639 | 1204185.2037 | 2766515.2027 | 1204192.1888 | 2766508.7427 | 1204197.7917
34 | 2766508.7427 | 1204197.7917 | 2766499.417 | 1204197.7762 | 2766485.2258 | 1204191.2644
35 | 2766485.2258 | 1204191.2644 | 2766475.5206 | 1204186.811 | 2766462.9339 | 1204186.296
36 | 2766455.8782 | 1204186.0073 | 2766462.9339 | 1204186.296

## bus_geodata
| x | y | coords
0 | 2767127.2031 | 1204753.2206
1 | 2766967.4254 | 1204723.3648
2 | 2766928.3892 | 1204712.7252
3 | 2766886.9739 | 1204712.8321
4 | 2766983.1196 | 1204558.5591
5 | 2766780.8715 | 1204725.2715
6 | 2767094.9435 | 1204546.8597
7 | 2767273.9724 | 1204525.9841
8 | 2767302.7216 | 1204519.9567
9 | 2766813.6299 | 1204513.3476
10 | 2767009.0404 | 1204502.5466
11 | 2766827.2703 | 1204415.2346
12 | 2767013.0187 | 1204492.521
13 | 2766695.4812 | 1204386.4468
14 | 2766468.2727 | 1204330.6425
15 | 2766457.3046 | 1204354.0283
16 | 2766523.1785 | 1204222.5727
17 | 2766460.2245 | 1204423.7491
18 | 2766256.5653 | 1204523.9872
19 | 2766740.6095 | 1204732.2586
20 | 2766707.2168 | 1204736.573
21 | 2766197.2829 | 1204483.916
22 | 2766204.0338 | 1204491.9001
23 | 2766124.7913 | 1204411.8214
24 | 2765922.8888 | 1204425.5776
25 | 2766173.5166 | 1204712.9671
26 | 2766221.0046 | 1204500.4348
27 | 2766560.2011 | 1204187.6614
28 | 2766625.1818 | 1204099.5141
29 | 2766517.1639 | 1204185.2037
30 | 2766637.061 | 1204098.3333
31 | 2766508.7427 | 1204197.7917
32 | 2766485.2258 | 1204191.2644
33 | 2766462.9339 | 1204186.296
34 | 2766455.8782 | 1204186.0073
35 | 2766093.7176 | 1204669.4388
36 | 2765958.6161 | 1204359.5979
37 | 2766373.4177 | 1204707.8831
38 | 2766813.6299 | 1204513.3476

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1