## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3986-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3986-13_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3986-13_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3986-13_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3986-13_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3986-13_0_3_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_3986-13_0_3_node_50 | 0.4 | n |  | TRUE
7 | bus_LV_3986-13_0_3_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_3986-13_0_3_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_3986-13_0_3_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_3986-13_0_3_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_3986-13_0_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_3986-13_0_3_node_53 | 0.4 | n |  | TRUE
13 | bus_LV_3986-13_0_3_node_54 | 0.4 | n |  | TRUE
14 | bus_LV_3986-13_0_3_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_3986-13_0_3_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_3986-13_0_3_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_3986-13_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_3986-13_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_3986-13_0_3_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_3986-13_0_3_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_3986-13_0_3_node_45 | 0.4 | n |  | TRUE
22 | bus_LV_3986-13_0_3_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_3986-13_0_3_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_3986-13_0_3_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_3986-13_0_3_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_3986-13_0_3_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_3986-13_0_3_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_3986-13_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_3986-13_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_3986-13_0_3_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_3986-13_0_3_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_3986-13_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_3986-13_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_3986-13_0_3_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_3986-13_0_3_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_3986-13_0_3_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_3986-13_0_3_node_42 | 0.4 | n |  | TRUE
38 | bus_LV_3986-13_0_3_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_3986-13_0_3_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_3986-13_0_3_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_3986-13_0_3_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_3986-13_0_3_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_3986-13_0_3_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_3986-13_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_3986-13_0_3_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_3986-13_0_3_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_3986-13_0_3_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_3986-13_0_3_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_3986-13_0_3_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_3986-13_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_MV_180_0_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3986-13_0_3_load_0 | 0 | 0.0022066 | 0.00055302 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3986-13_0_3_load_1 | 1 | 0.001949 | 0.00048846 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3986-13_0_3_load_2 | 2 | 0.0023582 | 0.00059103 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3986-13_0_3_load_3 | 3 | 0.0040292 | 0.0010098 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3986-13_0_3_load_40 | 5 | 0.0015515 | 0.00038884 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3986-13_0_3_load_50 | 6 | 0.0028582 | 0.00071634 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3986-13_0_3_load_28 | 7 | 0.0061657 | 0.0015453 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3986-13_0_3_load_36 | 9 | 0.0025621 | 0.00064212 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3986-13_0_3_load_37 | 10 | 0.0023127 | 0.00057963 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3986-13_0_3_load_33 | 11 | 0.0017084 | 0.00042817 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3986-13_0_3_load_54 | 13 | 0.0013209 | 0.00033105 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3986-13_0_3_load_5 | 14 | 0.0018262 | 0.00045769 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3986-13_0_3_load_6 | 15 | 0.0018509 | 0.00046387 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3986-13_0_3_load_7 | 16 | 0.002015 | 0.000505 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3986-13_0_3_load_8 | 17 | 0.0021214 | 0.00053168 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3986-13_0_3_load_34 | 18 | 0.0017921 | 0.00044915 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3986-13_0_3_load_38 | 19 | 0.0014761 | 0.00036994 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3986-13_0_3_load_46 | 20 | 0.0035614 | 0.00089256 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3986-13_0_3_load_45 | 21 | 0.0018562 | 0.0004652 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3986-13_0_3_load_39 | 22 | 0.0034077 | 0.00085404 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3986-13_0_3_load_9 | 23 | 0.0035164 | 0.00088129 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3986-13_0_3_load_10 | 24 | 0.0028491 | 0.00071406 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3986-13_0_3_load_11 | 25 | 0.0027718 | 0.00069467 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3986-13_0_3_load_29 | 27 | 0.0027868 | 0.00069844 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3986-13_0_3_load_25 | 28 | 0.0025865 | 0.00064825 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3986-13_0_3_load_26 | 29 | 0.0021833 | 0.00054719 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3986-13_0_3_load_13 | 30 | 0.0032623 | 0.00081762 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3986-13_0_3_load_17 | 32 | 0.0045477 | 0.0011398 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3986-13_0_3_load_18 | 33 | 0.0037014 | 0.00092765 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3986-13_0_3_load_43 | 34 | 0.0028085 | 0.00070387 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3986-13_0_3_load_41 | 35 | 0.0017304 | 0.00043369 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3986-13_0_3_load_23 | 36 | 0.0027682 | 0.00069377 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3986-13_0_3_load_42 | 37 | 0.0027243 | 0.00068279 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3986-13_0_3_load_19 | 38 | 0.0029759 | 0.00074584 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3986-13_0_3_load_20 | 39 | 0.002105 | 0.00052755 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3986-13_0_3_load_22 | 41 | 0.0023347 | 0.00058513 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3986-13_0_3_load_30 | 43 | 0.0027947 | 0.00070041 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3986-13_0_3_load_44 | 44 | 0.0035099 | 0.00087966 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3986-13_0_3_load_52 | 45 | 0.0013508 | 0.00033853 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3986-13_0_3_load_27 | 46 | 0.0018468 | 0.00046286 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3986-13_0_3_load_32 | 47 | 0.0043563 | 0.0010918 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3986-13_0_3_load_51 | 49 | 0.0048572 | 0.0012173 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3986-13_0_3_load_48 | 50 | 0.0016384 | 0.00041062 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3986-13_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.005821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3986-13_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.010404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3986-13_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0015536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3986-13_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0044092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3986-13_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.014135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3986-13_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.025909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3986-13_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.018594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3986-13_0_3_line_7 | NAYY 4x150 SE | 7 | 26 | 0.0078622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3986-13_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.019243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3986-13_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.038407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3986-13_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.048406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3986-13_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.084091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3986-13_0_3_line_12 | NAYY 4x150 SE | 11 | 18 | 0.016807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3986-13_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.044577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3986-13_0_3_line_14 | NAYY 4x150 SE | 14 | 15 | 0.0092115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3986-13_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.002276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3986-13_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.0058021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3986-13_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.054791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3986-13_0_3_line_18 | NAYY 4x150 SE | 17 | 19 | 0.0094256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3986-13_0_3_line_19 | NAYY 4x150 SE | 19 | 22 | 0.00058335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3986-13_0_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.020649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3986-13_0_3_line_21 | NAYY 4x150 SE | 21 | 47 | 0.047849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3986-13_0_3_line_22 | NAYY 4x150 SE | 22 | 27 | 0.01082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3986-13_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.0046561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3986-13_0_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.0029431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3986-13_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.020009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_3986-13_0_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.025283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3986-13_0_3_line_27 | NAYY 4x150 SE | 26 | 28 | 0.018612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3986-13_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.0027007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3986-13_0_3_line_29 | NAYY 4x150 SE | 29 | 46 | 0.023117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3986-13_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.020683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3986-13_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.027673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3986-13_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.0035939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3986-13_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.0049291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3986-13_0_3_line_34 | NAYY 4x150 SE | 34 | 37 | 0.0070331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3986-13_0_3_line_35 | NAYY 4x150 SE | 35 | 36 | 0.007372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3986-13_0_3_line_36 | NAYY 4x150 SE | 36 | 40 | 0.021185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3986-13_0_3_line_37 | NAYY 4x150 SE | 37 | 42 | 0.029699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3986-13_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.016322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3986-13_0_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.0082973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3986-13_0_3_line_40 | NAYY 4x150 SE | 39 | 41 | 0.012485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3986-13_0_3_line_41 | NAYY 4x150 SE | 40 | 42 | 0.00416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3986-13_0_3_line_42 | NAYY 4x150 SE | 41 | 43 | 0.01633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3986-13_0_3_line_43 | NAYY 4x150 SE | 42 | 44 | 0.01538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3986-13_0_3_line_44 | NAYY 4x150 SE | 44 | 45 | 0.040357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_3986-13_0_3_line_45 | NAYY 4x150 SE | 45 | 49 | 0.036194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_3986-13_0_3_line_46 | NAYY 4x150 SE | 46 | 47 | 0.022498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_3986-13_0_3_line_47 | NAYY 4x150 SE | 47 | 48 | 0.035771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_3986-13_0_3_line_48 | NAYY 4x150 SE | 48 | 49 | 0.013111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_3986-13_0_3_line_49 | NAYY 4x150 SE | 48 | 50 | 0.060585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3986-13_0_3_trafo_10 | 0.25 MVA 20/0.4 kV | 51 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2703162.4158 | 1170931.5639 | 2703156.8454 | 1170929.8744
1 | 2703162.4158 | 1170931.5639 | 2703172.3716 | 1170934.5835
2 | 2703156.8454 | 1170929.8744 | 2703155.3587 | 1170929.4235
3 | 2703176.591 | 1170935.8633 | 2703172.3716 | 1170934.5835
4 | 2703155.3587 | 1170929.4235 | 2703141.832 | 1170925.3207
5 | 2703163.194 | 1170958.0364 | 2703167.8004 | 1170949.5767 | 2703172.5448 | 1170942.4425 | 2703176.591 | 1170935.8633
6 | 2703141.832 | 1170925.3207 | 2703124.0388 | 1170919.924
7 | 2703116.5151 | 1170917.642 | 2703124.0388 | 1170919.924
8 | 2703215.2761 | 1170874.1881 | 2703212.213 | 1170879.6612 | 2703211.1851 | 1170882.034 | 2703210.8373 | 1170884.0182 | 2703210.5221 | 1170886.7701 | 2703210.5464 | 1170888.4716 | 2703210.9272 | 1170890.3572 | 2703211.4684 | 1170892.2566
9 | 2703215.2761 | 1170874.1881 | 2703226.6609 | 1170880.499 | 2703232.2584 | 1170883.3859 | 2703236.7499 | 1170885.6201 | 2703240.6144 | 1170887.3877 | 2703247.2425 | 1170889.97 | 2703249.8281 | 1170890.7896
10 | 2703215.2761 | 1170874.1881 | 2703175.9687 | 1170852.3208 | 2703172.9571 | 1170850.6882
11 | 2703332.7306 | 1170891.2967 | 2703319.7685 | 1170893.942 | 2703310.3029 | 1170895.7248 | 2703304.9183 | 1170896.4771 | 2703299.2116 | 1170896.8236 | 2703292.9325 | 1170897.0825 | 2703287.2609 | 1170897.1739 | 2703280.388 | 1170896.811 | 2703275.5513 | 1170896.4053 | 2703268.3215 | 1170895.4359 | 2703258.3176 | 1170893.3737 | 2703252.509 | 1170891.6394 | 2703249.8281 | 1170890.7896
12 | 2703172.9571 | 1170850.6882 | 2703158.1817 | 1170842.6786
13 | 2703295.1497 | 1170874.9618 | 2703299.0738 | 1170877.2641 | 2703304.2745 | 1170879.1993 | 2703308.7993 | 1170880.389 | 2703312.1692 | 1170880.6583 | 2703315.2421 | 1170880.3998 | 2703320.9783 | 1170880.1206 | 2703323.5656 | 1170880.5098 | 2703325.9318 | 1170881.2954 | 2703327.9127 | 1170882.2412 | 2703329.6188 | 1170884.0384 | 2703330.7953 | 1170886.3713 | 2703332.7306 | 1170891.2967
14 | 2703105.2541 | 1170857.5906 | 2703106.7871 | 1170866.6737
15 | 2703104.8753 | 1170855.3463 | 2703105.2541 | 1170857.5906
16 | 2703106.7871 | 1170866.6737 | 2703107.7527 | 1170872.3949
17 | 2703104.8753 | 1170855.3463 | 2703158.1817 | 1170842.6786
18 | 2703109.3214 | 1170881.689 | 2703107.7527 | 1170872.3949
19 | 2703109.3214 | 1170881.689 | 2703109.4185 | 1170882.2642
20 | 2703032.7349 | 1170867.0175 | 2703035.3032 | 1170863.3686 | 2703040.15 | 1170856.9476 | 2703044.5138 | 1170851.9193 | 2703045.5298 | 1170850.8379
21 | 2703051.6987 | 1170910.9481 | 2703032.7349 | 1170867.0175
22 | 2703109.4185 | 1170882.2642 | 2703111.2192 | 1170892.9334
23 | 2703121.2014 | 1170941.3454 | 2703120.2611 | 1170936.7852
24 | 2703121.5211 | 1170944.2674 | 2703121.331 | 1170941.9737 | 2703121.2014 | 1170941.3454
25 | 2703116.5151 | 1170917.642 | 2703115.5263 | 1170921.3052 | 2703116.6822 | 1170925.7279 | 2703119.7205 | 1170934.1633 | 2703120.2611 | 1170936.7852
26 | 2703116.5151 | 1170917.642 | 2703112.7024 | 1170901.7218 | 2703111.2192 | 1170892.9334
27 | 2703116.5151 | 1170917.642 | 2703098.7452 | 1170912.1072
28 | 2703098.7452 | 1170912.1072 | 2703096.1667 | 1170911.304
29 | 2703073.7426 | 1170906.6449 | 2703075.7316 | 1170906.4235 | 2703079.5167 | 1170906.5775 | 2703083.2312 | 1170907.275 | 2703096.1667 | 1170911.304
30 | 2703050.0423 | 1170982.2873 | 2703045.5751 | 1170992.4506 | 2703044.1045 | 1171001.9186
31 | 2703050.0423 | 1170982.2873 | 2703053.9099 | 1170981.6421 | 2703059.9307 | 1170981.7122 | 2703069.1017 | 1170983.7042 | 2703077.2064 | 1170985.6961
32 | 2703050.0423 | 1170982.2873 | 2703046.484 | 1170981.782
33 | 2703081.9931 | 1170986.8726 | 2703077.2064 | 1170985.6961
34 | 2703088.8903 | 1170988.2256 | 2703084.4706 | 1170987.4815 | 2703081.9931 | 1170986.8726
35 | 2703102.3728 | 1171011.6672 | 2703102.7768 | 1171009.5767 | 2703106.424 | 1171005.8103
36 | 2703121.1614 | 1170990.5912 | 2703106.424 | 1171005.8103
37 | 2703117.4602 | 1170988.6708 | 2703115.0478 | 1170990.5751 | 2703112.3762 | 1170991.5298 | 2703109.771 | 1170991.7408 | 2703088.8903 | 1170988.2256
38 | 2703145.4591 | 1170994.0666 | 2703138.2305 | 1170993.8308 | 2703131.4214 | 1170992.8799 | 2703129.2596 | 1170992.3977
39 | 2703121.1614 | 1170990.5912 | 2703129.2596 | 1170992.3977
40 | 2703145.4591 | 1170994.0666 | 2703157.9372 | 1170994.4736
41 | 2703121.1614 | 1170990.5912 | 2703117.4602 | 1170988.6708
42 | 2703174.2582 | 1170995.006 | 2703157.9372 | 1170994.4736
43 | 2703117.4602 | 1170988.6708 | 2703104.7216 | 1170980.0529
44 | 2703069.8089 | 1170959.8875 | 2703080.8604 | 1170965.5609 | 2703094.0167 | 1170972.9804 | 2703103.5653 | 1170979.2706 | 2703104.7216 | 1170980.0529
45 | 2703040.5305 | 1170938.7557 | 2703057.639 | 1170952.5206 | 2703067.1695 | 1170958.5325 | 2703069.8089 | 1170959.8875
46 | 2703073.7426 | 1170906.6449 | 2703069.7593 | 1170907.0881 | 2703061.5579 | 1170908.7818 | 2703054.6706 | 1170910.5981 | 2703051.6987 | 1170910.9481
47 | 2703031.3054 | 1170929.5428 | 2703030.3338 | 1170927.7472 | 2703029.7625 | 1170925.814 | 2703029.4342 | 1170922.6507 | 2703029.947 | 1170919.5242 | 2703031.3471 | 1170916.4128 | 2703033.4704 | 1170913.9699 | 2703035.6503 | 1170912.6843 | 2703040.1127 | 1170911.7157 | 2703047.8312 | 1170911.4035 | 2703051.6987 | 1170910.9481
48 | 2703031.3054 | 1170929.5428 | 2703033.57 | 1170932.6837 | 2703039.0567 | 1170937.5699 | 2703040.5305 | 1170938.7557
49 | 2703031.3054 | 1170929.5428 | 2702984.0873 | 1170967.5026

## bus_geodata
| x | y | coords
0 | 2703162.4158 | 1170931.5639
1 | 2703156.8454 | 1170929.8744
2 | 2703172.3716 | 1170934.5835
3 | 2703155.3587 | 1170929.4235
4 | 2703176.591 | 1170935.8633
5 | 2703141.832 | 1170925.3207
6 | 2703163.194 | 1170958.0364
7 | 2703124.0388 | 1170919.924
8 | 2703215.2761 | 1170874.1881
9 | 2703211.4684 | 1170892.2566
10 | 2703249.8281 | 1170890.7896
11 | 2703172.9571 | 1170850.6882
12 | 2703332.7306 | 1170891.2967
13 | 2703295.1497 | 1170874.9618
14 | 2703105.2541 | 1170857.5906
15 | 2703106.7871 | 1170866.6737
16 | 2703104.8753 | 1170855.3463
17 | 2703107.7527 | 1170872.3949
18 | 2703158.1817 | 1170842.6786
19 | 2703109.3214 | 1170881.689
20 | 2703045.5298 | 1170850.8379
21 | 2703032.7349 | 1170867.0175
22 | 2703109.4185 | 1170882.2642
23 | 2703121.2014 | 1170941.3454
24 | 2703120.2611 | 1170936.7852
25 | 2703121.5211 | 1170944.2674
26 | 2703116.5151 | 1170917.642
27 | 2703111.2192 | 1170892.9334
28 | 2703098.7452 | 1170912.1072
29 | 2703096.1667 | 1170911.304
30 | 2703044.1045 | 1171001.9186
31 | 2703050.0423 | 1170982.2873
32 | 2703077.2064 | 1170985.6961
33 | 2703046.484 | 1170981.782
34 | 2703081.9931 | 1170986.8726
35 | 2703102.3727 | 1171011.6672
36 | 2703106.424 | 1171005.8103
37 | 2703088.8903 | 1170988.2256
38 | 2703129.2596 | 1170992.3977
39 | 2703145.459 | 1170994.0666
40 | 2703121.1614 | 1170990.5912
41 | 2703157.9372 | 1170994.4736
42 | 2703117.4602 | 1170988.6708
43 | 2703174.2582 | 1170995.006
44 | 2703104.7216 | 1170980.0529
45 | 2703069.8089 | 1170959.8875
46 | 2703073.7426 | 1170906.6449
47 | 2703051.6987 | 1170910.9481
48 | 2703031.3054 | 1170929.5428
49 | 2703040.5305 | 1170938.7557
50 | 2702984.0873 | 1170967.5026
51 | 2703121.5211 | 1170944.2674

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1