## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3988-3_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3988-3_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3988-3_0_2_node_127 | 0.4 | n |  | TRUE
3 | bus_LV_3988-3_0_2_node_83 | 0.4 | n |  | TRUE
4 | bus_LV_3988-3_0_2_node_128 | 0.4 | n |  | TRUE
5 | bus_LV_3988-3_0_2_node_125 | 0.4 | n |  | TRUE
6 | bus_LV_3988-3_0_2_node_129 | 0.4 | n |  | TRUE
7 | bus_LV_3988-3_0_2_node_111 | 0.4 | n |  | TRUE
8 | bus_LV_3988-3_0_2_node_86 | 0.4 | n |  | TRUE
9 | bus_LV_3988-3_0_2_node_87 | 0.4 | n |  | TRUE
10 | bus_LV_3988-3_0_2_node_88 | 0.4 | n |  | TRUE
11 | bus_LV_3988-3_0_2_node_89 | 0.4 | n |  | TRUE
12 | bus_LV_3988-3_0_2_node_90 | 0.4 | n |  | TRUE
13 | bus_LV_3988-3_0_2_node_122 | 0.4 | n |  | TRUE
14 | bus_LV_3988-3_0_2_node_92 | 0.4 | n |  | TRUE
15 | bus_LV_3988-3_0_2_node_93 | 0.4 | n |  | TRUE
16 | bus_LV_3988-3_0_2_node_94 | 0.4 | n |  | TRUE
17 | bus_LV_3988-3_0_2_node_95 | 0.4 | n |  | TRUE
18 | bus_LV_3988-3_0_2_node_96 | 0.4 | n |  | TRUE
19 | bus_LV_3988-3_0_2_node_99 | 0.4 | n |  | TRUE
20 | bus_LV_3988-3_0_2_node_97 | 0.4 | n |  | TRUE
21 | bus_LV_3988-3_0_2_node_98 | 0.4 | n |  | TRUE
22 | bus_LV_3988-3_0_2_node_101 | 0.4 | n |  | TRUE
23 | bus_LV_3988-3_0_2_node_100 | 0.4 | n |  | TRUE
24 | bus_LV_3988-3_0_2_node_103 | 0.4 | n |  | TRUE
25 | bus_LV_3988-3_0_2_node_106 | 0.4 | n |  | TRUE
26 | bus_LV_3988-3_0_2_node_102 | 0.4 | n |  | TRUE
27 | bus_LV_3988-3_0_2_node_104 | 0.4 | n |  | TRUE
28 | bus_LV_3988-3_0_2_node_105 | 0.4 | n |  | TRUE
29 | bus_LV_3988-3_0_2_node_107 | 0.4 | n |  | TRUE
30 | bus_LV_3988-3_0_2_node_108 | 0.4 | n |  | TRUE
31 | bus_LV_3988-3_0_2_node_109 | 0.4 | n |  | TRUE
32 | bus_LV_3988-3_0_2_node_110 | 0.4 | n |  | TRUE
33 | bus_LV_3988-3_0_2_node_113 | 0.4 | n |  | TRUE
34 | bus_LV_3988-3_0_2_node_112 | 0.4 | n |  | TRUE
35 | bus_LV_3988-3_0_2_node_121 | 0.4 | n |  | TRUE
36 | bus_LV_3988-3_0_2_node_119 | 0.4 | n |  | TRUE
37 | bus_LV_3988-3_0_2_node_114 | 0.4 | n |  | TRUE
38 | bus_LV_3988-3_0_2_node_115 | 0.4 | n |  | TRUE
39 | bus_LV_3988-3_0_2_node_116 | 0.4 | n |  | TRUE
40 | bus_LV_3988-3_0_2_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_3988-3_0_2_node_123 | 0.4 | n |  | TRUE
42 | bus_LV_3988-3_0_2_node_120 | 0.4 | n |  | TRUE
43 | bus_LV_3988-3_0_2_node_118 | 0.4 | n |  | TRUE
44 | bus_LV_3988-3_0_2_node_124 | 0.4 | n |  | TRUE
45 | bus_LV_3988-3_0_2_node_126 | 0.4 | n |  | TRUE
46 | bus_MV_179_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3988-3_0_2_load_0 | 0 | 0.013976 | 0.0035027 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3988-3_0_2_load_83 | 3 | 0.0034216 | 0.00085753 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3988-3_0_2_load_128 | 4 | 0.0035318 | 0.00088514 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3988-3_0_2_load_125 | 5 | 0.0042956 | 0.0010766 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3988-3_0_2_load_129 | 6 | 0.0058687 | 0.0014708 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3988-3_0_2_load_86 | 8 | 0.0084833 | 0.0021261 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3988-3_0_2_load_89 | 11 | 0.0027774 | 0.00069608 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3988-3_0_2_load_90 | 12 | 0.0021725 | 0.00054447 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3988-3_0_2_load_122 | 13 | 0.0058362 | 0.0014627 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3988-3_0_2_load_92 | 14 | 0.0097667 | 0.0024478 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3988-3_0_2_load_93 | 15 | 0.0059247 | 0.0014849 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3988-3_0_2_load_96 | 18 | 0.0047325 | 0.0011861 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3988-3_0_2_load_97 | 20 | 0.0072488 | 0.0018167 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3988-3_0_2_load_98 | 21 | 0.0073201 | 0.0018346 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3988-3_0_2_load_100 | 23 | 0.0053994 | 0.0013532 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3988-3_0_2_load_106 | 25 | 0.002544 | 0.00063758 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3988-3_0_2_load_102 | 26 | 0.0037519 | 0.00094031 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3988-3_0_2_load_104 | 27 | 0.0085499 | 0.0021428 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3988-3_0_2_load_105 | 28 | 0.0081293 | 0.0020374 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3988-3_0_2_load_107 | 29 | 0.002758 | 0.00069122 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3988-3_0_2_load_108 | 30 | 0.0044453 | 0.0011141 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3988-3_0_2_load_121 | 35 | 0.0013837 | 0.0003468 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3988-3_0_2_load_119 | 36 | 0.0041865 | 0.0010492 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3988-3_0_2_load_114 | 37 | 0.0081831 | 0.0020509 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3988-3_0_2_load_115 | 38 | 0.003231 | 0.00080976 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3988-3_0_2_load_116 | 39 | 0.0028768 | 0.000721 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3988-3_0_2_load_123 | 41 | 0.0071985 | 0.0018041 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3988-3_0_2_load_120 | 42 | 0.0041799 | 0.0010476 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3988-3_0_2_load_118 | 43 | 0.0040517 | 0.0010154 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3988-3_0_2_load_124 | 44 | 0.0032582 | 0.00081658 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3988-3_0_2_load_126 | 45 | 0.0026095 | 0.00065401 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3988-3_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.038983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_3988-3_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.15501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_3988-3_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.26398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_3988-3_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_3988-3_0_2_line_4 | NAYY 4x150 SE | 2 | 45 | 0.03666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_3988-3_0_2_line_5 | NAYY 4x150 SE | 4 | 5 | 0.016102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_3988-3_0_2_line_6 | NAYY 4x150 SE | 5 | 44 | 0.0014441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_3988-3_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.036865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_3988-3_0_2_line_8 | NAYY 4x150 SE | 7 | 31 | 0.096592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_3988-3_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.037526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_3988-3_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.030737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_3988-3_0_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.030869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_3988-3_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.038257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_3988-3_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.01348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_3988-3_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.018966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_3988-3_0_2_line_15 | NAYY 4x150 SE | 13 | 35 | 0.013129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_3988-3_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.0060947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_3988-3_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.018955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_3988-3_0_2_line_18 | NAYY 4x150 SE | 16 | 17 | 0.01505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_3988-3_0_2_line_19 | NAYY 4x150 SE | 16 | 18 | 0.020022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_3988-3_0_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.003969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_3988-3_0_2_line_21 | NAYY 4x150 SE | 17 | 20 | 0.027276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_3988-3_0_2_line_22 | NAYY 4x150 SE | 19 | 22 | 0.018939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_3988-3_0_2_line_23 | NAYY 4x150 SE | 19 | 23 | 0.01948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_3988-3_0_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.015758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_3988-3_0_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.00471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_3988-3_0_2_line_26 | NAYY 4x150 SE | 22 | 25 | 0.013735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_3988-3_0_2_line_27 | NAYY 4x150 SE | 24 | 28 | 0.026284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_3988-3_0_2_line_28 | NAYY 4x150 SE | 24 | 26 | 0.012329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_3988-3_0_2_line_29 | NAYY 4x150 SE | 25 | 29 | 0.04152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_3988-3_0_2_line_30 | NAYY 4x150 SE | 26 | 27 | 0.020373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_3988-3_0_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.040446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_3988-3_0_2_line_32 | NAYY 4x150 SE | 30 | 32 | 0.014663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_3988-3_0_2_line_33 | NAYY 4x150 SE | 32 | 33 | 0.010678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_3988-3_0_2_line_34 | NAYY 4x150 SE | 33 | 36 | 0.01341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_3988-3_0_2_line_35 | NAYY 4x150 SE | 33 | 34 | 0.009481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_3988-3_0_2_line_36 | NAYY 4x150 SE | 34 | 35 | 0.014257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_3988-3_0_2_line_37 | NAYY 4x150 SE | 36 | 43 | 0.0078322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_3988-3_0_2_line_38 | NAYY 4x150 SE | 37 | 38 | 0.020626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_3988-3_0_2_line_39 | NAYY 4x150 SE | 37 | 39 | 0.011754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_3988-3_0_2_line_40 | NAYY 4x150 SE | 39 | 40 | 0.020472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_3988-3_0_2_line_41 | NAYY 4x150 SE | 40 | 41 | 0.0082505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_3988-3_0_2_line_42 | NAYY 4x150 SE | 40 | 42 | 0.014747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_3988-3_0_2_line_43 | NAYY 4x150 SE | 41 | 44 | 0.0072808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_3988-3_0_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.0016112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3988-3_0_2_trafo_121 | 0.25 MVA 20/0.4 kV | 46 | 35 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2728567.7109 | 1179146.6088 | 2728546.3418 | 1179156.2356 | 2728531.4373 | 1179151.8187
1 | 2728376.9107 | 1179164.1012 | 2728531.4373 | 1179151.8187
2 | 2728573.7355 | 1178882.6992 | 2728567.7109 | 1179146.6088
3 | 2728376.9107 | 1179164.1012 | 2728367.0839 | 1179171.5185
4 | 2728376.9107 | 1179164.1012 | 2728372.2385 | 1179153.5156 | 2728351.5644 | 1179139.3012
5 | 2728367.0839 | 1179171.5185 | 2728367.0839 | 1179171.5185 | 2728358.681 | 1179185.2538
6 | 2728357.9274 | 1179186.4856 | 2728358.681 | 1179185.2538
7 | 2728199.4969 | 1179248.635 | 2728222.5927 | 1179259.3478 | 2728232.0996 | 1179265.8002
8 | 2728276.4439 | 1179211.4196 | 2728267.9892 | 1179210.0823 | 2728258.1653 | 1179209.5162 | 2728249.0161 | 1179210.6325 | 2728241.4748 | 1179212.328 | 2728235.5854 | 1179214.3258 | 2728228.1584 | 1179218.1809 | 2728223.1523 | 1179219.6194 | 2728213.5026 | 1179220.5582 | 2728210.0929 | 1179230.9708 | 2728207.0083 | 1179238.6883 | 2728203.8643 | 1179243.469 | 2728199.4969 | 1179248.635
9 | 2728393.9596 | 1179284.0544 | 2728395.2096 | 1179289.9188 | 2728397.084 | 1179295.1739 | 2728406.2144 | 1179316.3294 | 2728406.8305 | 1179319.1718
10 | 2728403.3673 | 1179348.9814 | 2728406.6182 | 1179341.0007 | 2728408.0919 | 1179334.2828 | 2728408.2995 | 1179328.1605 | 2728407.6332 | 1179322.8757 | 2728406.8305 | 1179319.1718
11 | 2728393.9596 | 1179284.0544 | 2728374.2465 | 1179268.8546 | 2728369.2834 | 1179265.525
12 | 2728403.3673 | 1179348.9814 | 2728368.7728 | 1179332.646
13 | 2728358.0888 | 1179258.015 | 2728369.2834 | 1179265.525
14 | 2728368.7728 | 1179332.646 | 2728351.6226 | 1179324.5478
15 | 2728347.1861 | 1179250.7009 | 2728358.0888 | 1179258.015
16 | 2728351.6226 | 1179324.5478 | 2728346.1114 | 1179321.9454
17 | 2728328.9715 | 1179313.8521 | 2728346.1114 | 1179321.9454
18 | 2728315.33 | 1179307.411 | 2728328.9715 | 1179313.8521
19 | 2728318.0047 | 1179330.6186 | 2728328.9715 | 1179313.8521
20 | 2728311.7284 | 1179305.7216 | 2728315.33 | 1179307.411
21 | 2728315.33 | 1179307.411 | 2728327.2413 | 1179282.873
22 | 2728294.6091 | 1179297.516 | 2728311.7284 | 1179305.7216
23 | 2728311.7284 | 1179305.7216 | 2728303.5084 | 1179320.5566 | 2728302.2727 | 1179322.7529
24 | 2728327.2413 | 1179282.873 | 2728328.4821 | 1179280.3169 | 2728328.2535 | 1179278.1437 | 2728327.0872 | 1179276.5732 | 2728319.3276 | 1179272.4741
25 | 2728294.6091 | 1179297.516 | 2728290.2698 | 1179295.6551
26 | 2728294.6091 | 1179297.516 | 2728298.6875 | 1179284.4005
27 | 2728266.4202 | 1179284.459 | 2728290.2698 | 1179295.6551
28 | 2728290.2698 | 1179295.6551 | 2728283.8099 | 1179306.1563
29 | 2728282.936 | 1179255.5243 | 2728300.1066 | 1179264.1979 | 2728302.0689 | 1179265.3519 | 2728303.1242 | 1179266.7533 | 2728303.1009 | 1179268.5541 | 2728299.6239 | 1179281.3892 | 2728298.6875 | 1179284.4005
30 | 2728273.1352 | 1179323.5091 | 2728283.8099 | 1179306.1563
31 | 2728276.4439 | 1179211.4196 | 2728283.7033 | 1179213.6098 | 2728299.3973 | 1179219.8613 | 2728310.5028 | 1179226.248 | 2728313.1665 | 1179227.947
32 | 2728325.5293 | 1179235.8321 | 2728313.1665 | 1179227.947
33 | 2728335.9316 | 1179233.2973 | 2728325.5293 | 1179235.8321
34 | 2728335.9316 | 1179233.2973 | 2728343.6013 | 1179222.2972
35 | 2728335.9316 | 1179233.2973 | 2728335.3469 | 1179242.7584
36 | 2728335.3469 | 1179242.7584 | 2728347.1861 | 1179250.7009
37 | 2728346.849 | 1179215.3895 | 2728346.4578 | 1179218.2003 | 2728343.6013 | 1179222.2972
38 | 2728318.7084 | 1179196.8981 | 2728315.2097 | 1179195.5928 | 2728301.322 | 1179191.0034 | 2728299.086 | 1179190.6404
39 | 2728318.7084 | 1179196.8981 | 2728329.7207 | 1179201.0068
40 | 2728349.1042 | 1179199.1874 | 2728345.349 | 1179201.4531 | 2728342.245 | 1179202.5764 | 2728339.4723 | 1179202.8618 | 2728336.5534 | 1179202.8326 | 2728330.8288 | 1179201.4202 | 2728329.7207 | 1179201.0068
41 | 2728349.1042 | 1179199.1874 | 2728351.8167 | 1179196.3656 | 2728354.1202 | 1179192.6915
42 | 2728349.1042 | 1179199.1874 | 2728347.0711 | 1179213.7937
43 | 2728354.1202 | 1179192.6915 | 2728354.5545 | 1179191.9987 | 2728357.9274 | 1179186.4856
44 | 2728346.849 | 1179215.3895 | 2728347.0711 | 1179213.7937

## bus_geodata
| x | y | coords
0 | 2728531.4373 | 1179151.8187
1 | 2728567.7109 | 1179146.6088
2 | 2728376.9107 | 1179164.1012
3 | 2728573.7355 | 1178882.6992
4 | 2728367.0839 | 1179171.5185
5 | 2728358.681 | 1179185.2538
6 | 2728232.0996 | 1179265.8002
7 | 2728199.4969 | 1179248.635
8 | 2728406.8305 | 1179319.1718
9 | 2728393.9596 | 1179284.0544
10 | 2728403.3673 | 1179348.9814
11 | 2728369.2834 | 1179265.525
12 | 2728368.7728 | 1179332.646
13 | 2728358.0888 | 1179258.015
14 | 2728351.6226 | 1179324.5478
15 | 2728346.1114 | 1179321.9454
16 | 2728328.9715 | 1179313.8521
17 | 2728315.33 | 1179307.411
18 | 2728318.0047 | 1179330.6186
19 | 2728311.7284 | 1179305.7216
20 | 2728327.2413 | 1179282.873
21 | 2728319.3276 | 1179272.4741
22 | 2728294.6091 | 1179297.516
23 | 2728302.2727 | 1179322.7529
24 | 2728290.2698 | 1179295.6551
25 | 2728298.6875 | 1179284.4005
26 | 2728283.8099 | 1179306.1563
27 | 2728273.1352 | 1179323.5091
28 | 2728266.4202 | 1179284.459
29 | 2728282.936 | 1179255.5243
30 | 2728313.1665 | 1179227.947
31 | 2728276.4439 | 1179211.4196
32 | 2728325.5293 | 1179235.8321
33 | 2728335.9316 | 1179233.2973
34 | 2728335.3469 | 1179242.7584
35 | 2728347.1861 | 1179250.7009
36 | 2728343.6013 | 1179222.2972
37 | 2728318.7084 | 1179196.8981
38 | 2728299.086 | 1179190.6404
39 | 2728329.7207 | 1179201.0068
40 | 2728349.1042 | 1179199.1874
41 | 2728354.1202 | 1179192.6915
42 | 2728347.0711 | 1179213.7937
43 | 2728346.849 | 1179215.3895
44 | 2728357.9274 | 1179186.4856
45 | 2728351.5644 | 1179139.3012
46 | 2728335.3469 | 1179242.7584

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1